## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-103_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-103_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-103_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-103_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_261-103_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_261-103_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_261-103_0_4_node_62 | 0.4 | n |  | TRUE
7 | bus_LV_261-103_0_4_node_54 | 0.4 | n |  | TRUE
8 | bus_LV_261-103_0_4_node_142 | 0.4 | n |  | TRUE
9 | bus_LV_261-103_0_4_node_41 | 0.4 | n |  | TRUE
10 | bus_LV_261-103_0_4_node_40 | 0.4 | n |  | TRUE
11 | bus_LV_261-103_0_4_node_53 | 0.4 | n |  | TRUE
12 | bus_LV_261-103_0_4_node_109 | 0.4 | n |  | TRUE
13 | bus_LV_261-103_0_4_node_36 | 0.4 | n |  | TRUE
14 | bus_LV_261-103_0_4_node_56 | 0.4 | n |  | TRUE
15 | bus_LV_261-103_0_4_node_123 | 0.4 | n |  | TRUE
16 | bus_LV_261-103_0_4_node_108 | 0.4 | n |  | TRUE
17 | bus_LV_261-103_0_4_node_39 | 0.4 | n |  | TRUE
18 | bus_LV_261-103_0_4_node_35 | 0.4 | n |  | TRUE
19 | bus_LV_261-103_0_4_node_37 | 0.4 | n |  | TRUE
20 | bus_LV_261-103_0_4_node_38 | 0.4 | n |  | TRUE
21 | bus_LV_261-103_0_4_node_33 | 0.4 | n |  | TRUE
22 | bus_LV_261-103_0_4_node_74 | 0.4 | n |  | TRUE
23 | bus_LV_261-103_0_4_node_101 | 0.4 | n |  | TRUE
24 | bus_LV_261-103_0_4_node_42 | 0.4 | n |  | TRUE
25 | bus_LV_261-103_0_4_node_97 | 0.4 | n |  | TRUE
26 | bus_LV_261-103_0_4_node_48 | 0.4 | n |  | TRUE
27 | bus_LV_261-103_0_4_node_95 | 0.4 | n |  | TRUE
28 | bus_LV_261-103_0_4_node_45 | 0.4 | n |  | TRUE
29 | bus_LV_261-103_0_4_node_51 | 0.4 | n |  | TRUE
30 | bus_LV_261-103_0_4_node_80 | 0.4 | n |  | TRUE
31 | bus_LV_261-103_0_4_node_83 | 0.4 | n |  | TRUE
32 | bus_LV_261-103_0_4_node_46 | 0.4 | n |  | TRUE
33 | bus_LV_261-103_0_4_node_47 | 0.4 | n |  | TRUE
34 | bus_LV_261-103_0_4_node_85 | 0.4 | n |  | TRUE
35 | bus_LV_261-103_0_4_node_120 | 0.4 | n |  | TRUE
36 | bus_LV_261-103_0_4_node_50 | 0.4 | n |  | TRUE
37 | bus_LV_261-103_0_4_node_75 | 0.4 | n |  | TRUE
38 | bus_LV_261-103_0_4_node_94 | 0.4 | n |  | TRUE
39 | bus_LV_261-103_0_4_node_82 | 0.4 | n |  | TRUE
40 | bus_LV_261-103_0_4_node_52 | 0.4 | n |  | TRUE
41 | bus_LV_261-103_0_4_node_96 | 0.4 | n |  | TRUE
42 | bus_LV_261-103_0_4_node_116 | 0.4 | n |  | TRUE
43 | bus_LV_261-103_0_4_node_55 | 0.4 | n |  | TRUE
44 | bus_LV_261-103_0_4_node_16 | 0.4 | n |  | TRUE
45 | bus_LV_261-103_0_4_node_7 | 0.4 | n |  | TRUE
46 | bus_LV_261-103_0_4_node_8 | 0.4 | n |  | TRUE
47 | bus_LV_261-103_0_4_node_9 | 0.4 | n |  | TRUE
48 | bus_LV_261-103_0_4_node_10 | 0.4 | n |  | TRUE
49 | bus_LV_261-103_0_4_node_12 | 0.4 | n |  | TRUE
50 | bus_LV_261-103_0_4_node_115 | 0.4 | n |  | TRUE
51 | bus_LV_261-103_0_4_node_11 | 0.4 | n |  | TRUE
52 | bus_LV_261-103_0_4_node_103 | 0.4 | n |  | TRUE
53 | bus_LV_261-103_0_4_node_113 | 0.4 | n |  | TRUE
54 | bus_LV_261-103_0_4_node_143 | 0.4 | n |  | TRUE
55 | bus_LV_261-103_0_4_node_100 | 0.4 | n |  | TRUE
56 | bus_LV_261-103_0_4_node_111 | 0.4 | n |  | TRUE
57 | bus_LV_261-103_0_4_node_13 | 0.4 | n |  | TRUE
58 | bus_LV_261-103_0_4_node_14 | 0.4 | n |  | TRUE
59 | bus_LV_261-103_0_4_node_15 | 0.4 | n |  | TRUE
60 | bus_LV_261-103_0_4_node_18 | 0.4 | n |  | TRUE
61 | bus_LV_261-103_0_4_node_17 | 0.4 | n |  | TRUE
62 | bus_LV_261-103_0_4_node_19 | 0.4 | n |  | TRUE
63 | bus_LV_261-103_0_4_node_22 | 0.4 | n |  | TRUE
64 | bus_LV_261-103_0_4_node_20 | 0.4 | n |  | TRUE
65 | bus_LV_261-103_0_4_node_23 | 0.4 | n |  | TRUE
66 | bus_LV_261-103_0_4_node_21 | 0.4 | n |  | TRUE
67 | bus_LV_261-103_0_4_node_68 | 0.4 | n |  | TRUE
68 | bus_LV_261-103_0_4_node_27 | 0.4 | n |  | TRUE
69 | bus_LV_261-103_0_4_node_24 | 0.4 | n |  | TRUE
70 | bus_LV_261-103_0_4_node_63 | 0.4 | n |  | TRUE
71 | bus_LV_261-103_0_4_node_66 | 0.4 | n |  | TRUE
72 | bus_LV_261-103_0_4_node_25 | 0.4 | n |  | TRUE
73 | bus_LV_261-103_0_4_node_26 | 0.4 | n |  | TRUE
74 | bus_LV_261-103_0_4_node_121 | 0.4 | n |  | TRUE
75 | bus_LV_261-103_0_4_node_144 | 0.4 | n |  | TRUE
76 | bus_LV_261-103_0_4_node_31 | 0.4 | n |  | TRUE
77 | bus_LV_261-103_0_4_node_28 | 0.4 | n |  | TRUE
78 | bus_LV_261-103_0_4_node_29 | 0.4 | n |  | TRUE
79 | bus_LV_261-103_0_4_node_30 | 0.4 | n |  | TRUE
80 | bus_LV_261-103_0_4_node_67 | 0.4 | n |  | TRUE
81 | bus_LV_261-103_0_4_node_32 | 0.4 | n |  | TRUE
82 | bus_LV_261-103_0_4_node_72 | 0.4 | n |  | TRUE
83 | bus_LV_261-103_0_4_node_65 | 0.4 | n |  | TRUE
84 | bus_LV_261-103_0_4_node_70 | 0.4 | n |  | TRUE
85 | bus_LV_261-103_0_4_node_34 | 0.4 | n |  | TRUE
86 | bus_LV_261-103_0_4_node_122 | 0.4 | n |  | TRUE
87 | bus_LV_261-103_0_4_node_99 | 0.4 | n |  | TRUE
88 | bus_LV_261-103_0_4_node_102 | 0.4 | n |  | TRUE
89 | bus_LV_261-103_0_4_node_134 | 0.4 | n |  | TRUE
90 | bus_LV_261-103_0_4_node_98 | 0.4 | n |  | TRUE
91 | bus_LV_261-103_0_4_node_106 | 0.4 | n |  | TRUE
92 | bus_LV_261-103_0_4_node_76 | 0.4 | n |  | TRUE
93 | bus_LV_261-103_0_4_node_77 | 0.4 | n |  | TRUE
94 | bus_LV_261-103_0_4_node_78 | 0.4 | n |  | TRUE
95 | bus_LV_261-103_0_4_node_81 | 0.4 | n |  | TRUE
96 | bus_LV_261-103_0_4_node_79 | 0.4 | n |  | TRUE
97 | bus_LV_261-103_0_4_node_87 | 0.4 | n |  | TRUE
98 | bus_LV_261-103_0_4_node_84 | 0.4 | n |  | TRUE
99 | bus_LV_261-103_0_4_node_93 | 0.4 | n |  | TRUE
100 | bus_LV_261-103_0_4_node_141 | 0.4 | n |  | TRUE
101 | bus_LV_261-103_0_4_node_57 | 0.4 | n |  | TRUE
102 | bus_LV_261-103_0_4_node_58 | 0.4 | n |  | TRUE
103 | bus_LV_261-103_0_4_node_59 | 0.4 | n |  | TRUE
104 | bus_LV_261-103_0_4_node_60 | 0.4 | n |  | TRUE
105 | bus_LV_261-103_0_4_node_61 | 0.4 | n |  | TRUE
106 | bus_LV_261-103_0_4_node_69 | 0.4 | n |  | TRUE
107 | bus_LV_261-103_0_4_node_73 | 0.4 | n |  | TRUE
108 | bus_LV_261-103_0_4_node_64 | 0.4 | n |  | TRUE
109 | bus_LV_261-103_0_4_node_71 | 0.4 | n |  | TRUE
110 | bus_LV_261-103_0_4_node_86 | 0.4 | n |  | TRUE
111 | bus_LV_261-103_0_4_node_88 | 0.4 | n |  | TRUE
112 | bus_LV_261-103_0_4_node_89 | 0.4 | n |  | TRUE
113 | bus_LV_261-103_0_4_node_90 | 0.4 | n |  | TRUE
114 | bus_LV_261-103_0_4_node_119 | 0.4 | n |  | TRUE
115 | bus_LV_261-103_0_4_node_91 | 0.4 | n |  | TRUE
116 | bus_LV_261-103_0_4_node_92 | 0.4 | n |  | TRUE
117 | bus_LV_261-103_0_4_node_133 | 0.4 | n |  | TRUE
118 | bus_LV_261-103_0_4_node_104 | 0.4 | n |  | TRUE
119 | bus_LV_261-103_0_4_node_112 | 0.4 | n |  | TRUE
120 | bus_LV_261-103_0_4_node_114 | 0.4 | n |  | TRUE
121 | bus_LV_261-103_0_4_node_110 | 0.4 | n |  | TRUE
122 | bus_LV_261-103_0_4_node_105 | 0.4 | n |  | TRUE
123 | bus_LV_261-103_0_4_node_107 | 0.4 | n |  | TRUE
124 | bus_LV_261-103_0_4_node_131 | 0.4 | n |  | TRUE
125 | bus_LV_261-103_0_4_node_135 | 0.4 | n |  | TRUE
126 | bus_LV_261-103_0_4_node_130 | 0.4 | n |  | TRUE
127 | bus_LV_261-103_0_4_node_140 | 0.4 | n |  | TRUE
128 | bus_LV_261-103_0_4_node_138 | 0.4 | n |  | TRUE
129 | bus_LV_261-103_0_4_node_137 | 0.4 | n |  | TRUE
130 | bus_LV_261-103_0_4_node_139 | 0.4 | n |  | TRUE
131 | bus_LV_261-103_0_4_node_124 | 0.4 | n |  | TRUE
132 | bus_LV_261-103_0_4_node_125 | 0.4 | n |  | TRUE
133 | bus_LV_261-103_0_4_node_127 | 0.4 | n |  | TRUE
134 | bus_LV_261-103_0_4_node_128 | 0.4 | n |  | TRUE
135 | bus_LV_261-103_0_4_node_132 | 0.4 | n |  | TRUE
136 | bus_LV_261-103_0_4_node_136 | 0.4 | n |  | TRUE
137 | bus_MV_524_0_node_20 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-103_0_4_load_0 | 0 | 0.0086278 | 0.0021623 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-103_0_4_load_5 | 4 | 0.0087476 | 0.0021924 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-103_0_4_load_6 | 5 | 0.017232 | 0.0043188 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-103_0_4_load_62 | 6 | 0.0043138 | 0.0010811 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-103_0_4_load_142 | 8 | 0.013823 | 0.0034645 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-103_0_4_load_109 | 12 | 0.0043785 | 0.0010973 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-103_0_4_load_36 | 13 | 0.0084524 | 0.0021184 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-103_0_4_load_123 | 15 | 0.0064447 | 0.0016152 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-103_0_4_load_108 | 16 | 0.0047141 | 0.0011815 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-103_0_4_load_38 | 20 | 0.0050091 | 0.0012554 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-103_0_4_load_33 | 21 | 0.0037517 | 0.00094028 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-103_0_4_load_74 | 22 | 0.0045711 | 0.0011456 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-103_0_4_load_97 | 25 | 0.0059308 | 0.0014864 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-103_0_4_load_95 | 27 | 0.0039922 | 0.0010005 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-103_0_4_load_83 | 31 | 0.0032778 | 0.0008215 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-103_0_4_load_120 | 35 | 0.0039399 | 0.00098744 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-103_0_4_load_75 | 37 | 0.011681 | 0.0029275 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-103_0_4_load_94 | 38 | 0.0032137 | 0.00080542 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-103_0_4_load_82 | 39 | 0.0036703 | 0.00091986 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-103_0_4_load_96 | 41 | 0.0047567 | 0.0011921 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-103_0_4_load_116 | 42 | 0.0037528 | 0.00094053 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-103_0_4_load_16 | 44 | 0.00414 | 0.0010376 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-103_0_4_load_7 | 45 | 0.0047628 | 0.0011937 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-103_0_4_load_8 | 46 | 0.0047515 | 0.0011908 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-103_0_4_load_10 | 48 | 0.0047459 | 0.0011894 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-103_0_4_load_12 | 49 | 0.004365 | 0.001094 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-103_0_4_load_115 | 50 | 0.0047326 | 0.0011861 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-103_0_4_load_103 | 52 | 0.0044046 | 0.0011039 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-103_0_4_load_143 | 54 | 0.0044146 | 0.0011064 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-103_0_4_load_111 | 56 | 0.0042758 | 0.0010716 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-103_0_4_load_13 | 57 | 0.0038176 | 0.00095678 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-103_0_4_load_14 | 58 | 0.0038692 | 0.00096971 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-103_0_4_load_18 | 60 | 0.004701 | 0.0011782 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-103_0_4_load_17 | 61 | 0.0041904 | 0.0010502 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-103_0_4_load_19 | 62 | 0.0038251 | 0.00095866 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-103_0_4_load_22 | 63 | 0.0044846 | 0.0011239 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-103_0_4_load_20 | 64 | 0.0039924 | 0.0010006 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-103_0_4_load_23 | 65 | 0.0035576 | 0.00089162 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-103_0_4_load_21 | 66 | 0.0038263 | 0.00095897 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-103_0_4_load_24 | 69 | 0.003779 | 0.00094711 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-103_0_4_load_63 | 70 | 0.00458 | 0.0011479 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-103_0_4_load_66 | 71 | 0.0029319 | 0.00073481 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-103_0_4_load_25 | 72 | 0.0073547 | 0.0018433 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-103_0_4_load_26 | 73 | 0.0027205 | 0.00068182 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-103_0_4_load_144 | 75 | 0.0031833 | 0.00079782 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-103_0_4_load_28 | 77 | 0.0036853 | 0.00092363 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-103_0_4_load_29 | 78 | 0.0042262 | 0.0010592 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-103_0_4_load_30 | 79 | 0.0035284 | 0.0008843 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-103_0_4_load_67 | 80 | 0.0030163 | 0.00075597 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-103_0_4_load_32 | 81 | 0.003565 | 0.00089347 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-103_0_4_load_70 | 84 | 0.0042766 | 0.0010718 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-103_0_4_load_34 | 85 | 0.0024977 | 0.00062599 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-103_0_4_load_122 | 86 | 0.0054904 | 0.001376 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-103_0_4_load_99 | 87 | 0.0043294 | 0.0010851 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-103_0_4_load_102 | 88 | 0.0043165 | 0.0010818 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-103_0_4_load_98 | 90 | 0.0043301 | 0.0010852 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-103_0_4_load_76 | 92 | 0.0052674 | 0.0013201 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-103_0_4_load_78 | 94 | 0.0036906 | 0.00092496 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-103_0_4_load_81 | 95 | 0.0030866 | 0.00077358 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-103_0_4_load_79 | 96 | 0.004612 | 0.0011559 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-103_0_4_load_87 | 97 | 0.0018305 | 0.00045876 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-103_0_4_load_84 | 98 | 0.0033247 | 0.00083325 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-103_0_4_load_93 | 99 | 0.014225 | 0.0035652 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-103_0_4_load_141 | 100 | 0.0062827 | 0.0015746 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-103_0_4_load_57 | 101 | 0.003517 | 0.00088145 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-103_0_4_load_58 | 102 | 0.0029231 | 0.0007326 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-103_0_4_load_59 | 103 | 0.0026304 | 0.00065923 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-103_0_4_load_60 | 104 | 0.0036446 | 0.00091343 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-103_0_4_load_61 | 105 | 0.0025293 | 0.00063391 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-103_0_4_load_69 | 106 | 0.0026271 | 0.00065841 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-103_0_4_load_73 | 107 | 0.0033773 | 0.00084643 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-103_0_4_load_64 | 108 | 0.0026824 | 0.00067226 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-103_0_4_load_71 | 109 | 0.004442 | 0.0011133 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-103_0_4_load_88 | 111 | 0.002619 | 0.00065638 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-103_0_4_load_89 | 112 | 0.0024314 | 0.00060936 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-103_0_4_load_90 | 113 | 0.001512 | 0.00037895 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-103_0_4_load_119 | 114 | 0.0012494 | 0.00031312 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-103_0_4_load_91 | 115 | 0.0018131 | 0.00045441 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-103_0_4_load_92 | 116 | 0.0016657 | 0.00041746 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-103_0_4_load_133 | 117 | 0.0056786 | 0.0014232 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-103_0_4_load_104 | 118 | 0.0064573 | 0.0016183 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-103_0_4_load_110 | 121 | 0.0055954 | 0.0014023 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_261-103_0_4_load_105 | 122 | 0.0056788 | 0.0014232 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_261-103_0_4_load_107 | 123 | 0.0055288 | 0.0013857 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_261-103_0_4_load_131 | 124 | 0.0047337 | 0.0011864 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_261-103_0_4_load_130 | 126 | 0.0048607 | 0.0012182 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_261-103_0_4_load_140 | 127 | 0.0054472 | 0.0013652 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_261-103_0_4_load_138 | 128 | 0.0055971 | 0.0014028 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_261-103_0_4_load_137 | 129 | 0.005448 | 0.0013654 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_261-103_0_4_load_139 | 130 | 0.0063662 | 0.0015955 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_261-103_0_4_load_124 | 131 | 0.0048617 | 0.0012185 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_261-103_0_4_load_128 | 134 | 0.0047337 | 0.0011864 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_261-103_0_4_load_132 | 135 | 0.0055299 | 0.0013859 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_261-103_0_4_load_136 | 136 | 0.0055963 | 0.0014026 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 81 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-103_0_4_line_0 |  | 0 | 1 | 0.030402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-103_0_4_line_1 |  | 0 | 2 | 0.02642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-103_0_4_line_2 |  | 1 | 3 | 0.002658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-103_0_4_line_3 |  | 2 | 4 | 0.028251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-103_0_4_line_4 |  | 2 | 5 | 0.036989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-103_0_4_line_5 |  | 3 | 6 | 0.074463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-103_0_4_line_6 |  | 6 | 43 | 0.054893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-103_0_4_line_7 |  | 7 | 8 | 0.015206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-103_0_4_line_8 |  | 7 | 9 | 0.036147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-103_0_4_line_9 |  | 9 | 13 | 0.021632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-103_0_4_line_10 |  | 9 | 10 | 0.019865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-103_0_4_line_11 |  | 10 | 11 | 0.079328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-103_0_4_line_12 |  | 10 | 12 | 0.033942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-103_0_4_line_13 |  | 11 | 42 | 0.082876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-103_0_4_line_14 |  | 12 | 88 | 0.016014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-103_0_4_line_15 |  | 13 | 85 | 0.0346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-103_0_4_line_16 |  | 14 | 15 | 0.015868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-103_0_4_line_17 |  | 14 | 16 | 0.016302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_261-103_0_4_line_18 |  | 14 | 17 | 0.038904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_261-103_0_4_line_19 |  | 15 | 100 | 0.018205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-103_0_4_line_20 |  | 16 | 91 | 0.024571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_261-103_0_4_line_21 |  | 17 | 23 | 0.011355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-103_0_4_line_22 |  | 17 | 18 | 0.011638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_261-103_0_4_line_23 |  | 18 | 19 | 0.013167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-103_0_4_line_24 |  | 18 | 20 | 0.021554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_261-103_0_4_line_25 |  | 18 | 21 | 0.043567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-103_0_4_line_26 |  | 19 | 22 | 0.0079625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-103_0_4_line_27 |  | 20 | 82 | 0.015493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_261-103_0_4_line_28 |  | 23 | 86 | 0.023591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-103_0_4_line_29 |  | 24 | 25 | 0.018786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-103_0_4_line_30 |  | 24 | 26 | 0.017869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-103_0_4_line_31 |  | 24 | 27 | 0.0172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-103_0_4_line_32 |  | 25 | 89 | 0.015802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_261-103_0_4_line_33 |  | 26 | 36 | 0.04585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-103_0_4_line_34 |  | 26 | 37 | 0.040282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-103_0_4_line_35 |  | 27 | 40 | 0.025791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-103_0_4_line_36 |  | 28 | 29 | 0.019773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-103_0_4_line_37 |  | 28 | 30 | 0.035822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-103_0_4_line_38 |  | 28 | 31 | 0.013798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-103_0_4_line_39 |  | 29 | 39 | 0.0011003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-103_0_4_line_40 |  | 30 | 95 | 0.013293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-103_0_4_line_41 |  | 30 | 96 | 0.020958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-103_0_4_line_42 |  | 31 | 33 | 0.013598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-103_0_4_line_43 |  | 32 | 33 | 0.024943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-103_0_4_line_44 |  | 32 | 34 | 0.038218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-103_0_4_line_45 |  | 32 | 35 | 0.023134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-103_0_4_line_46 |  | 34 | 97 | 0.0033269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-103_0_4_line_47 |  | 34 | 98 | 0.011951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-103_0_4_line_48 |  | 36 | 38 | 0.037262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-103_0_4_line_49 |  | 38 | 99 | 0.0056122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-103_0_4_line_50 |  | 40 | 41 | 0.029664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-103_0_4_line_51 |  | 43 | 44 | 0.043603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-103_0_4_line_52 |  | 44 | 58 | 0.0044727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-103_0_4_line_53 |  | 45 | 46 | 0.010651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-103_0_4_line_54 |  | 45 | 47 | 0.010271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-103_0_4_line_55 |  | 46 | 48 | 0.020978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-103_0_4_line_56 |  | 47 | 49 | 0.010057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-103_0_4_line_57 |  | 48 | 50 | 0.011671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-103_0_4_line_58 |  | 49 | 53 | 0.011258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-103_0_4_line_59 |  | 51 | 52 | 0.013604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-103_0_4_line_60 |  | 51 | 53 | 0.019054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-103_0_4_line_61 |  | 52 | 54 | 0.019273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-103_0_4_line_62 |  | 52 | 55 | 0.00998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-103_0_4_line_63 |  | 53 | 56 | 0.01439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-103_0_4_line_64 |  | 55 | 88 | 0.036659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-103_0_4_line_65 |  | 55 | 87 | 0.028252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-103_0_4_line_66 |  | 56 | 121 | 0.014982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-103_0_4_line_67 |  | 57 | 58 | 9.3251e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-103_0_4_line_68 |  | 57 | 59 | 0.014514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-103_0_4_line_69 |  | 59 | 60 | 0.014448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-103_0_4_line_70 |  | 60 | 63 | 0.018518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-103_0_4_line_71 |  | 61 | 62 | 0.014391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-103_0_4_line_72 |  | 62 | 64 | 0.026836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-103_0_4_line_73 |  | 63 | 65 | 0.0061657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-103_0_4_line_74 |  | 64 | 66 | 0.015915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-103_0_4_line_75 |  | 65 | 69 | 0.00076949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-103_0_4_line_76 |  | 66 | 67 | 0.023258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-103_0_4_line_77 |  | 67 | 68 | 0.001931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-103_0_4_line_78 |  | 68 | 74 | 0.008242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-103_0_4_line_79 |  | 68 | 73 | 0.0048417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-103_0_4_line_80 |  | 69 | 70 | 0.012548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_261-103_0_4_line_81 |  | 70 | 71 | 0.014875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-103_0_4_line_82 |  | 71 | 108 | 0.014672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_261-103_0_4_line_83 |  | 72 | 73 | 0.01336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_261-103_0_4_line_84 |  | 74 | 75 | 0.007596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_261-103_0_4_line_85 |  | 74 | 76 | 0.025554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_261-103_0_4_line_86 |  | 76 | 80 | 0.008984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_261-103_0_4_line_87 |  | 76 | 78 | 0.024417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_261-103_0_4_line_88 |  | 77 | 78 | 0.016989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_261-103_0_4_line_89 |  | 77 | 79 | 0.016143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_261-103_0_4_line_90 |  | 80 | 83 | 0.016115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_261-103_0_4_line_91 |  | 81 | 82 | 0.019955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_261-103_0_4_line_92 |  | 82 | 84 | 0.010377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_261-103_0_4_line_93 |  | 83 | 108 | 0.019333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_261-103_0_4_line_94 |  | 83 | 105 | 0.0056335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_261-103_0_4_line_95 |  | 84 | 109 | 0.00066178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_261-103_0_4_line_96 |  | 89 | 117 | 0.0023036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_261-103_0_4_line_97 |  | 90 | 91 | 0.018286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_261-103_0_4_line_98 |  | 91 | 118 | 0.0181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_261-103_0_4_line_99 |  | 92 | 93 | 0.014712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_261-103_0_4_line_100 |  | 93 | 94 | 0.020548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_261-103_0_4_line_101 |  | 94 | 96 | 0.03628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_261-103_0_4_line_102 |  | 97 | 113 | 0.005287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_261-103_0_4_line_103 |  | 98 | 110 | 0.0057285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_261-103_0_4_line_104 |  | 99 | 116 | 0.0065416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_261-103_0_4_line_105 |  | 100 | 130 | 0.0098238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_261-103_0_4_line_106 |  | 101 | 102 | 0.0022249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_261-103_0_4_line_107 |  | 101 | 103 | 0.024444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_261-103_0_4_line_108 |  | 102 | 104 | 0.014621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_261-103_0_4_line_109 |  | 103 | 105 | 0.00055898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-103_0_4_line_110 |  | 104 | 106 | 0.00021435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_261-103_0_4_line_111 |  | 106 | 107 | 0.016657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_261-103_0_4_line_112 |  | 107 | 109 | 0.008905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
113 | LV_261-103_0_4_line_113 |  | 110 | 111 | 0.020688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_261-103_0_4_line_114 |  | 110 | 112 | 0.014989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_261-103_0_4_line_115 |  | 111 | 114 | 0.00039394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_261-103_0_4_line_116 |  | 113 | 115 | 0.029622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_261-103_0_4_line_117 |  | 115 | 116 | 0.018344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_261-103_0_4_line_118 |  | 117 | 135 | 0.015928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
119 | LV_261-103_0_4_line_119 |  | 118 | 122 | 0.016507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_261-103_0_4_line_120 |  | 119 | 120 | 0.004003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_261-103_0_4_line_121 |  | 119 | 121 | 0.024612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_261-103_0_4_line_122 |  | 120 | 127 | 0.023815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_261-103_0_4_line_123 |  | 120 | 128 | 0.010657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_261-103_0_4_line_124 |  | 122 | 123 | 0.018023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
125 | LV_261-103_0_4_line_125 |  | 123 | 124 | 0.014634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
126 | LV_261-103_0_4_line_126 |  | 124 | 125 | 0.019301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
127 | LV_261-103_0_4_line_127 |  | 124 | 126 | 0.020186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
128 | LV_261-103_0_4_line_128 |  | 125 | 136 | 0.005618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_261-103_0_4_line_129 |  | 126 | 134 | 0.025182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
130 | LV_261-103_0_4_line_130 |  | 128 | 129 | 0.025816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_261-103_0_4_line_131 |  | 129 | 136 | 0.014213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_261-103_0_4_line_132 |  | 131 | 132 | 0.01386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_261-103_0_4_line_133 |  | 132 | 133 | 0.011837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
134 | LV_261-103_0_4_line_134 |  | 132 | 134 | 0.0023282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
135 | LV_261-103_0_4_line_135 |  | 133 | 135 | 0.0025464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-103_0_4_trafo_32 | 0.63 MVA 20/0.4 kV | 137 | 81 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2681008.7843 | 1251873.534 | 2681031.8195 | 1251873.0486 | 2681038.4952 | 1251869.9464
1 | 2681062.4548 | 1251858.8125 | 2681038.4952 | 1251869.9464
2 | 2681008.7843 | 1251873.534 | 2681007.762 | 1251875.9885
3 | 2681062.4548 | 1251858.8125 | 2681039.5628 | 1251842.2567
4 | 2681096.0831 | 1251843.1943 | 2681062.4548 | 1251858.8125
5 | 2681007.762 | 1251875.9885 | 2681009.1552 | 1251919.8068 | 2681008.9839 | 1251949.9825 | 2681008.9157 | 1251950.4233
6 | 2681001.8043 | 1252004.7362 | 2681001.4824 | 1251998.4716 | 2681008.9157 | 1251950.4233
7 | 2681053.9352 | 1251802.9767 | 2681053.713 | 1251787.7734
8 | 2681086.4931 | 1251777.9034 | 2681085.2273 | 1251779.9431 | 2681078.4947 | 1251785.444 | 2681071.1035 | 1251787.778 | 2681053.713 | 1251787.7734
9 | 2681086.4931 | 1251777.9034 | 2681093.4304 | 1251780.6114 | 2681103.0815 | 1251784.6687 | 2681106.4003 | 1251786.3388
10 | 2681086.4931 | 1251777.9034 | 2681078.6652 | 1251775.1943 | 2681080.7223 | 1251769.3848 | 2681082.2277 | 1251764.1793
11 | 2681007.7015 | 1251746.3246 | 2681009.6413 | 1251751.2993 | 2681020.9526 | 1251752.0767 | 2681051.073 | 1251755.6579 | 2681065.3075 | 1251759.044 | 2681074.6308 | 1251761.6846 | 2681082.2277 | 1251764.1793
12 | 2681082.2277 | 1251764.1793 | 2681092.2276 | 1251767.5742 | 2681103.0652 | 1251772.0814 | 2681113.5897 | 1251777.0643
13 | 2681007.7015 | 1251746.3246 | 2681019.032 | 1251734.6709 | 2681036.4399 | 1251719.075 | 2681051.8028 | 1251711.157 | 2681069.3528 | 1251705.037 | 2681076.4284 | 1251702.9375
14 | 2681127.9152 | 1251784.2205 | 2681116.8265 | 1251778.5968 | 2681113.5897 | 1251777.0643
15 | 2681106.4003 | 1251786.3388 | 2681137.3079 | 1251801.8921
16 | 2681263.294 | 1251830.9201 | 2681264.3246 | 1251824.5739 | 2681265.6413 | 1251815.2279
17 | 2681263.294 | 1251830.9201 | 2681277.7276 | 1251832.4302 | 2681279.5042 | 1251832.6448
18 | 2681224.998 | 1251824.1678 | 2681235.4958 | 1251826.469 | 2681250.8036 | 1251829.1697 | 2681263.294 | 1251830.9201
19 | 2681268.1808 | 1251797.2012 | 2681265.6413 | 1251815.2279
20 | 2681303.8981 | 1251835.5916 | 2681279.5042 | 1251832.6448
21 | 2681227.6628 | 1251813.1295 | 2681224.998 | 1251824.1678
22 | 2681220.7751 | 1251834.8846 | 2681223.5894 | 1251830.0084 | 2681224.998 | 1251824.1678
23 | 2681233.6573 | 1251837.7855 | 2681220.7751 | 1251834.8846
24 | 2681220.7751 | 1251834.8846 | 2681216.0976 | 1251842.9821 | 2681209.0702 | 1251852.9583
25 | 2681220.7751 | 1251834.8846 | 2681207.6154 | 1251831.3016 | 2681192.7496 | 1251826.6389 | 2681179.2851 | 1251821.6797
26 | 2681233.6573 | 1251837.7855 | 2681241.5016 | 1251839.1529
27 | 2681200.1479 | 1251865.6248 | 2681209.0702 | 1251852.9583
28 | 2681227.6628 | 1251813.1295 | 2681208.3072 | 1251809.4726 | 2681204.5771 | 1251808.357
29 | 2681349.4121 | 1251843.8223 | 2681350.0263 | 1251840.8729 | 2681351.5616 | 1251825.1747
30 | 2681349.4121 | 1251843.8223 | 2681348.2968 | 1251849.1887 | 2681353.9302 | 1251851.1898 | 2681351.4338 | 1251857.0932
31 | 2681349.4121 | 1251843.8223 | 2681361.8589 | 1251849.2972 | 2681364.9524 | 1251851.1426
32 | 2681353.0998 | 1251809.4473 | 2681351.5616 | 1251825.1747
33 | 2681333.4223 | 1251891.883 | 2681327.7595 | 1251886.5235 | 2681336.1475 | 1251878.1102 | 2681343.4513 | 1251870.0489 | 2681349.6316 | 1251861.3606 | 2681351.4338 | 1251857.0932
34 | 2681351.4338 | 1251857.0932 | 2681341.5537 | 1251853.2436 | 2681330.069 | 1251850.2616 | 2681312.9523 | 1251847.925 | 2681312.4185 | 1251847.8629
35 | 2681385.7407 | 1251866.3045 | 2681380.527 | 1251861.7739 | 2681371.8758 | 1251855.2725 | 2681364.9524 | 1251851.1426
36 | 2681197.8071 | 1252008.2655 | 2681191.2928 | 1252015.4705 | 2681181.9053 | 1252019.1891
37 | 2681197.8071 | 1252008.2655 | 2681194.1108 | 1252000.409 | 2681188.7928 | 1251996.322 | 2681185.1537 | 1251995.3048 | 2681181.9752 | 1251993.1707 | 2681181.2616 | 1251990.7147 | 2681183.2786 | 1251985.0826 | 2681180.486 | 1251981.7752
38 | 2681197.8071 | 1252008.2655 | 2681204.026 | 1252001.1343 | 2681207.9156 | 1251999.2172
39 | 2681181.9053 | 1252019.1891 | 2681180.8826 | 1252019.5951
40 | 2681180.486 | 1251981.7752 | 2681188.9071 | 1251971.4718
41 | 2681180.486 | 1251981.7752 | 2681169.2735 | 1251988.6823 | 2681161.9244 | 1251991.2613
42 | 2681214.5517 | 1251989.8257 | 2681215.4624 | 1251993.8634 | 2681213.2665 | 1251996.5798 | 2681207.9156 | 1251999.2172
43 | 2681230.0321 | 1251976.061 | 2681227.9853 | 1251983.3161 | 2681221.3046 | 1251981.7345 | 2681214.5517 | 1251989.8257
44 | 2681230.0321 | 1251976.061 | 2681237.138 | 1251951.0509 | 2681242.5192 | 1251940.072
45 | 2681230.0321 | 1251976.061 | 2681239.5787 | 1251978.905 | 2681248.4648 | 1251979.8276 | 2681252.657 | 1251979.2025
46 | 2681242.5192 | 1251940.072 | 2681244.6336 | 1251937.5034
47 | 2681242.5192 | 1251940.072 | 2681232.8572 | 1251940.6845 | 2681231.0329 | 1251942.0353
48 | 2681333.4223 | 1251891.883 | 2681329.1255 | 1251894.7818 | 2681303.4323 | 1251913.9896
49 | 2681298.9374 | 1251917.35 | 2681303.4323 | 1251913.9896
50 | 2681385.7407 | 1251866.3045 | 2681393.3682 | 1251848.4292 | 2681397.3321 | 1251838.9989
51 | 2681001.8043 | 1252004.7362 | 2681005.2393 | 1252003.0263 | 2681028.8382 | 1251986.6701 | 2681033.6843 | 1251982.7779 | 2681036.4422 | 1251978.8034
52 | 2681036.4422 | 1251978.8034 | 2681037.8651 | 1251976.7528 | 2681038.7414 | 1251974.9808
53 | 2681159.0511 | 1251753.1671 | 2681159.0511 | 1251753.1671 | 2681149.2681 | 1251748.9546
54 | 2681167.801 | 1251758.5465 | 2681159.0511 | 1251753.1671
55 | 2681129.0034 | 1251743.7376 | 2681135.6674 | 1251744.9074 | 2681146.8351 | 1251747.907 | 2681149.2681 | 1251748.9546
56 | 2681167.801 | 1251758.5465 | 2681169.6322 | 1251762.619 | 2681173.6624 | 1251766.4952
57 | 2681129.0034 | 1251743.7376 | 2681129.0034 | 1251743.7376 | 2681118.2925 | 1251748.3732
58 | 2681182.9526 | 1251772.6645 | 2681176.6574 | 1251769.3758 | 2681173.6624 | 1251766.4952
59 | 2681165.4722 | 1251778.118 | 2681164.0037 | 1251791.6413
60 | 2681182.9526 | 1251772.6645 | 2681179.0111 | 1251775.5238 | 2681171.623 | 1251778.7249 | 2681165.4722 | 1251778.118
61 | 2681147.7063 | 1251781.2771 | 2681164.0037 | 1251791.6413
62 | 2681164.0037 | 1251791.6413 | 2681163.5467 | 1251795.7937 | 2681160.6099 | 1251800.8016
63 | 2681182.9526 | 1251772.6645 | 2681197.2716 | 1251774.0883
64 | 2681160.6099 | 1251800.8016 | 2681127.9152 | 1251784.2205
65 | 2681160.6099 | 1251800.8016 | 2681173.0345 | 1251806.8096 | 2681184.4791 | 1251811.6255 | 2681186.3972 | 1251812.3036
66 | 2681212.0215 | 1251776.6801 | 2681199.1662 | 1251774.2767 | 2681197.2716 | 1251774.0883
67 | 2681038.7414 | 1251974.9808 | 2681038.7827 | 1251974.8972
68 | 2681045.2163 | 1251961.8867 | 2681038.7827 | 1251974.8972
69 | 2681045.2163 | 1251961.8867 | 2681059.0071 | 1251957.58
70 | 2681076.6834 | 1251952.0598 | 2681059.0071 | 1251957.58
71 | 2681045.3928 | 1251919.7578 | 2681045.3928 | 1251919.7578 | 2681032.0573 | 1251925.1683
72 | 2681045.3928 | 1251919.7578 | 2681048.9285 | 1251923.3755 | 2681052.9915 | 1251925.9663 | 2681057.105 | 1251925.4222 | 2681059.622 | 1251921.298 | 2681060.8473 | 1251913.9426 | 2681061.3254 | 1251913.7366
73 | 2681082.5465 | 1251950.159 | 2681081.7147 | 1251950.4886 | 2681076.6834 | 1251952.0598
74 | 2681075.9423 | 1251907.4398 | 2681061.3254 | 1251913.7366
75 | 2681083.2619 | 1251949.8756 | 2681082.5465 | 1251950.159
76 | 2681096.5282 | 1251911.0064 | 2681084.2628 | 1251903.8554 | 2681075.9423 | 1251907.4398
77 | 2681096.5282 | 1251911.0064 | 2681097.0443 | 1251909.1454
78 | 2681097.0443 | 1251909.1454 | 2681100.5204 | 1251909.9491 | 2681102.9944 | 1251913.9304
79 | 2681097.0443 | 1251909.1454 | 2681098.346 | 1251904.4819
80 | 2681083.2619 | 1251949.8756 | 2681094.9274 | 1251945.2534
81 | 2681108.3956 | 1251938.9451 | 2681096.1185 | 1251944.7814 | 2681094.9274 | 1251945.2534
82 | 2681108.3956 | 1251938.9451 | 2681121.4263 | 1251932.2026
83 | 2681098.346 | 1251904.4819 | 2681091.4983 | 1251893.01
84 | 2681107.0196 | 1251920.3791 | 2681102.9944 | 1251913.9304
85 | 2681102.9944 | 1251913.9304 | 2681106.5069 | 1251914.2787 | 2681116.7298 | 1251908.5366 | 2681121.0359 | 1251904.9484 | 2681123.9703 | 1251901.2191
86 | 2681123.9703 | 1251901.2191 | 2681127.3996 | 1251905.4359 | 2681129.4781 | 1251908.3123
87 | 2681123.9703 | 1251901.2191 | 2681123.7996 | 1251901.0055 | 2681122.5937 | 1251894.8177 | 2681126.4779 | 1251884.0073 | 2681131.0215 | 1251879.5683
88 | 2681131.0215 | 1251879.5683 | 2681136.2091 | 1251874.5001 | 2681143.5075 | 1251868.0555
89 | 2681155.4816 | 1251857.2325 | 2681151.6348 | 1251860.879 | 2681143.5075 | 1251868.0555
90 | 2681137.8303 | 1251921.991 | 2681135.5551 | 1251916.7226 | 2681129.4781 | 1251908.3123
91 | 2681200.1479 | 1251865.6248 | 2681191.64 | 1251858.5696 | 2681183.3458 | 1251855.3346
92 | 2681200.1479 | 1251865.6248 | 2681193.1496 | 1251873.2865
93 | 2681137.8303 | 1251921.991 | 2681123.8878 | 1251930.929 | 2681121.4263 | 1251932.2026
94 | 2681137.8303 | 1251921.991 | 2681142.3816 | 1251918.6711
95 | 2681192.7033 | 1251873.7751 | 2681193.1496 | 1251873.2865
96 | 2681353.0998 | 1251809.4473 | 2681353.3239 | 1251807.1546
97 | 2681303.8981 | 1251835.5916 | 2681322.0627 | 1251837.6942
98 | 2681303.8981 | 1251835.5916 | 2681306.9825 | 1251828.6398 | 2681306.2598 | 1251818.1701
99 | 2681113.4783 | 1252020.2752 | 2681103.0312 | 1252025.8697 | 2681100.1888 | 1252026.1977
100 | 2681113.4783 | 1252020.2752 | 2681121.094 | 1252014.2083 | 2681130.7169 | 1252009.2808
101 | 2681130.7169 | 1252009.2808 | 2681143.7749 | 1252003.7332 | 2681150.0372 | 1251998.3928 | 2681161.9244 | 1251991.2613 | 2681161.9244 | 1251991.2613
102 | 2681248.0504 | 1251933.486 | 2681247.8231 | 1251933.6288 | 2681244.6336 | 1251937.5034
103 | 2681226.4291 | 1251945.4443 | 2681231.0329 | 1251942.0353
104 | 2681298.9374 | 1251917.35 | 2681294.5106 | 1251920.6594 | 2681293.59 | 1251921.0858
105 | 2681269.5512 | 1251787.4735 | 2681268.1808 | 1251797.2012
106 | 2681162.2486 | 1251903.5108 | 2681163.9517 | 1251902.0791
107 | 2681162.2486 | 1251903.5108 | 2681156.2346 | 1251908.5663 | 2681142.8332 | 1251918.3417
108 | 2681163.9517 | 1251902.0791 | 2681170.1089 | 1251896.9032 | 2681174.8834 | 1251892.3793
109 | 2681142.3816 | 1251918.6711 | 2681142.8332 | 1251918.3417
110 | 2681174.8834 | 1251892.3793 | 2681175.039 | 1251892.2318
111 | 2681175.039 | 1251892.2318 | 2681181.029 | 1251886.5562 | 2681186.6976 | 1251880.3502
112 | 2681186.6976 | 1251880.3502 | 2681192.7033 | 1251873.7751
113 | 2681226.4291 | 1251945.4443 | 2681223.8912 | 1251955.4837 | 2681220.8833 | 1251965.3695
114 | 2681213.6051 | 1251952.6295 | 2681222.1537 | 1251946.2419 | 2681226.4291 | 1251945.4443
115 | 2681220.7687 | 1251965.7464 | 2681220.8833 | 1251965.3695
116 | 2681248.0504 | 1251933.486 | 2681255.1472 | 1251929.0258 | 2681265.6177 | 1251926.701 | 2681276.1163 | 1251926.1297
117 | 2681276.1163 | 1251926.1297 | 2681277.2047 | 1251926.0705 | 2681286.7702 | 1251924.2448 | 2681293.59 | 1251921.0858
118 | 2681354.8737 | 1251791.3026 | 2681353.3239 | 1251807.1546
119 | 2681306.2598 | 1251818.1701 | 2681306.2081 | 1251817.4208 | 2681309.1959 | 1251809.8117 | 2681310.315 | 1251802.313
120 | 2681234.1547 | 1251770.1643 | 2681237.0161 | 1251767.357
121 | 2681234.1547 | 1251770.1643 | 2681220.9241 | 1251778.3446 | 2681212.0215 | 1251776.6801
122 | 2681229.5309 | 1251747.3728 | 2681227.0807 | 1251750.4638 | 2681227.6661 | 1251754.0078 | 2681237.0161 | 1251767.357
123 | 2681237.0161 | 1251767.357 | 2681245.9843 | 1251763.4214 | 2681246.8463 | 1251763.376
124 | 2681312.9752 | 1251784.4876 | 2681310.315 | 1251802.313
125 | 2681311.354 | 1251770.2786 | 2681313.8427 | 1251778.6745 | 2681312.9752 | 1251784.4876
126 | 2681292.2143 | 1251767.3805 | 2681311.354 | 1251770.2786
127 | 2681311.354 | 1251770.2786 | 2681324.2845 | 1251774.0699 | 2681330.9939 | 1251773.9113
128 | 2681292.2143 | 1251767.3805 | 2681286.6369 | 1251766.7065
129 | 2681355.8577 | 1251777.2631 | 2681336.7804 | 1251773.7745 | 2681330.9939 | 1251773.9113
130 | 2681272.5261 | 1251765.0012 | 2681255.3657 | 1251762.9274 | 2681246.8463 | 1251763.376
131 | 2681286.6369 | 1251766.7065 | 2681272.5261 | 1251765.0012
132 | 2681358.148 | 1251777.6819 | 2681365.0173 | 1251780.3782 | 2681371.2607 | 1251778.6404
133 | 2681358.148 | 1251777.6819 | 2681358.6222 | 1251782.1695 | 2681355.842 | 1251788.9475
134 | 2681358.148 | 1251777.6819 | 2681355.8577 | 1251777.2631
135 | 2681355.842 | 1251788.9475 | 2681354.8737 | 1251791.3026 | 2681354.8737 | 1251791.3026

## bus_geodata
| x | y | coords
0 | 2681038.4952 | 1251869.9464
1 | 2681008.7843 | 1251873.534
2 | 2681062.4548 | 1251858.8125
3 | 2681007.762 | 1251875.9885
4 | 2681039.5628 | 1251842.2567
5 | 2681096.0831 | 1251843.1943
6 | 2681008.9157 | 1251950.4233
7 | 2681053.713 | 1251787.7734
8 | 2681053.9352 | 1251802.9767
9 | 2681086.4931 | 1251777.9034
10 | 2681082.2277 | 1251764.1793
11 | 2681007.7015 | 1251746.3246
12 | 2681113.5897 | 1251777.0643
13 | 2681106.4003 | 1251786.3388
14 | 2681263.294 | 1251830.9201
15 | 2681265.6413 | 1251815.2279
16 | 2681279.5042 | 1251832.6448
17 | 2681224.998 | 1251824.1678
18 | 2681220.7751 | 1251834.8846
19 | 2681233.6573 | 1251837.7855
20 | 2681209.0702 | 1251852.9583
21 | 2681179.2851 | 1251821.6797
22 | 2681241.5016 | 1251839.1529
23 | 2681227.6628 | 1251813.1295
24 | 2681349.4121 | 1251843.8223
25 | 2681351.5616 | 1251825.1747
26 | 2681351.4338 | 1251857.0932
27 | 2681364.9524 | 1251851.1426
28 | 2681197.8071 | 1252008.2655
29 | 2681181.9053 | 1252019.1891
30 | 2681180.486 | 1251981.7752
31 | 2681207.9156 | 1251999.2172
32 | 2681230.0321 | 1251976.061
33 | 2681214.5517 | 1251989.8257
34 | 2681242.5192 | 1251940.072
35 | 2681252.657 | 1251979.2025
36 | 2681333.4223 | 1251891.883
37 | 2681312.4185 | 1251847.8629
38 | 2681303.4323 | 1251913.9896
39 | 2681180.8826 | 1252019.5951
40 | 2681385.7407 | 1251866.3045
41 | 2681397.3321 | 1251838.9989
42 | 2681076.4284 | 1251702.9375
43 | 2681001.8043 | 1252004.7362
44 | 2681036.4422 | 1251978.8034
45 | 2681159.0511 | 1251753.1671
46 | 2681149.2681 | 1251748.9546
47 | 2681167.801 | 1251758.5465
48 | 2681129.0034 | 1251743.7376
49 | 2681173.6624 | 1251766.4952
50 | 2681118.2925 | 1251748.3732
51 | 2681165.4722 | 1251778.118
52 | 2681164.0037 | 1251791.6413
53 | 2681182.9526 | 1251772.6645
54 | 2681147.7063 | 1251781.2771
55 | 2681160.6099 | 1251800.8016
56 | 2681197.2716 | 1251774.0883
57 | 2681038.7827 | 1251974.8972
58 | 2681038.7414 | 1251974.9808
59 | 2681045.2163 | 1251961.8867
60 | 2681059.0071 | 1251957.58
61 | 2681032.0573 | 1251925.1683
62 | 2681045.3928 | 1251919.7578
63 | 2681076.6834 | 1251952.0598
64 | 2681061.3254 | 1251913.7366
65 | 2681082.5465 | 1251950.159
66 | 2681075.9423 | 1251907.4398
67 | 2681096.5282 | 1251911.0064
68 | 2681097.0443 | 1251909.1454
69 | 2681083.2619 | 1251949.8756
70 | 2681094.9274 | 1251945.2534
71 | 2681108.3956 | 1251938.9451
72 | 2681091.4983 | 1251893.01
73 | 2681098.346 | 1251904.4819
74 | 2681102.9944 | 1251913.9304
75 | 2681107.0196 | 1251920.3791
76 | 2681123.9703 | 1251901.2191
77 | 2681143.5075 | 1251868.0555
78 | 2681131.0215 | 1251879.5683
79 | 2681155.4816 | 1251857.2325
80 | 2681129.4781 | 1251908.3123
81 | 2681183.3458 | 1251855.3346
82 | 2681200.1479 | 1251865.6248
83 | 2681137.8303 | 1251921.991
84 | 2681193.1496 | 1251873.2865
85 | 2681137.3079 | 1251801.8921
86 | 2681204.5771 | 1251808.357
87 | 2681186.3972 | 1251812.3036
88 | 2681127.9152 | 1251784.2205
89 | 2681353.0998 | 1251809.4473
90 | 2681322.0627 | 1251837.6942
91 | 2681303.8981 | 1251835.5916
92 | 2681100.1888 | 1252026.1977
93 | 2681113.4783 | 1252020.2752
94 | 2681130.7169 | 1252009.2808
95 | 2681188.9071 | 1251971.4718
96 | 2681161.9244 | 1251991.2613
97 | 2681244.6336 | 1251937.5034
98 | 2681231.0329 | 1251942.0353
99 | 2681298.9374 | 1251917.35
100 | 2681268.1808 | 1251797.2012
101 | 2681162.2486 | 1251903.5108
102 | 2681163.9517 | 1251902.0791
103 | 2681142.8332 | 1251918.3417
104 | 2681174.8834 | 1251892.3793
105 | 2681142.3816 | 1251918.6711
106 | 2681175.039 | 1251892.2318
107 | 2681186.6976 | 1251880.3502
108 | 2681121.4263 | 1251932.2026
109 | 2681192.7033 | 1251873.7751
110 | 2681226.4291 | 1251945.4443
111 | 2681220.8833 | 1251965.3695
112 | 2681213.6051 | 1251952.6295
113 | 2681248.0504 | 1251933.486
114 | 2681220.7687 | 1251965.7464
115 | 2681276.1163 | 1251926.1297
116 | 2681293.59 | 1251921.0858
117 | 2681353.3239 | 1251807.1546
118 | 2681306.2598 | 1251818.1701
119 | 2681234.1547 | 1251770.1643
120 | 2681237.0161 | 1251767.357
121 | 2681212.0215 | 1251776.6801
122 | 2681310.315 | 1251802.313
123 | 2681312.9752 | 1251784.4876
124 | 2681311.354 | 1251770.2786
125 | 2681292.2143 | 1251767.3805
126 | 2681330.9939 | 1251773.9113
127 | 2681229.5309 | 1251747.3728
128 | 2681246.8463 | 1251763.376
129 | 2681272.5261 | 1251765.0012
130 | 2681269.5512 | 1251787.4735
131 | 2681371.2607 | 1251778.6404
132 | 2681358.148 | 1251777.6819
133 | 2681355.842 | 1251788.9475
134 | 2681355.8577 | 1251777.2631
135 | 2681354.8737 | 1251791.3026
136 | 2681286.6369 | 1251766.7065
137 | 2681200.1479 | 1251865.6248

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97515 | -0.47946 | 0.0086278 | 0.0021623
1 | 0.97613 | -0.46019 | 0 | 0
2 | 0.97451 | -0.49205 | 0 | 0
3 | 0.97621 | -0.45851 | 0 | 0
4 | 0.97428 | -0.49659 | 0.0087476 | 0.0021924
5 | 0.97391 | -0.50375 | 0.017232 | 0.0043188
6 | 0.97861 | -0.41149 | 0.0043138 | 0.0010811
7 | 0.97055 | -0.56886 | 0 | 0
8 | 0.97035 | -0.57275 | 0.013823 | 0.0034645
9 | 0.97102 | -0.55961 | 0 | 0
10 | 0.97147 | -0.55052 | 0 | 0
11 | 0.9712 | -0.55602 | 0 | 0
12 | 0.97238 | -0.53265 | 0.0043785 | 0.0010973
13 | 0.97079 | -0.56399 | 0.0084524 | 0.0021184
14 | 0.99235 | -0.14514 | 0 | 0
15 | 0.99207 | -0.1505 | 0.0064447 | 0.0016152
16 | 0.9914 | -0.16323 | 0.0047141 | 0.0011815
17 | 0.99478 | -0.098813 | 0 | 0
18 | 0.99552 | -0.084719 | 0 | 0
19 | 0.99547 | -0.085777 | 0 | 0
20 | 0.99694 | -0.057884 | 0.0050091 | 0.0012554
21 | 0.99537 | -0.087594 | 0.0037517 | 0.00094028
22 | 0.99543 | -0.086418 | 0.0045711 | 0.0011456
23 | 0.99472 | -0.099912 | 0 | 0
24 | 0.98234 | -0.33782 | 0 | 0
25 | 0.98377 | -0.31008 | 0.0059308 | 0.0014864
26 | 0.98112 | -0.36145 | 0 | 0
27 | 0.9822 | -0.34054 | 0.0039922 | 0.0010005
28 | 0.97154 | -0.54927 | 0 | 0
29 | 0.97148 | -0.55061 | 0 | 0
30 | 0.97099 | -0.5603 | 0 | 0
31 | 0.97181 | -0.54409 | 0.0032778 | 0.0008215
32 | 0.97266 | -0.52732 | 0 | 0
33 | 0.97211 | -0.53817 | 0 | 0
34 | 0.97364 | -0.50794 | 0 | 0
35 | 0.97257 | -0.52899 | 0.0039399 | 0.00098744
36 | 0.9785 | -0.4126 | 0 | 0
37 | 0.98069 | -0.36998 | 0.011681 | 0.0029275
38 | 0.97636 | -0.45437 | 0.0032137 | 0.00080542
39 | 0.97147 | -0.55069 | 0.0036703 | 0.00091986
40 | 0.98209 | -0.34276 | 0 | 0
41 | 0.98196 | -0.34531 | 0.0047567 | 0.0011921
42 | 0.97091 | -0.56178 | 0.0037528 | 0.00094053
43 | 0.9806 | -0.37267 | 0 | 0
44 | 0.98218 | -0.34196 | 0.00414 | 0.0010376
45 | 0.97546 | -0.47195 | 0.0047628 | 0.0011937
46 | 0.97532 | -0.47473 | 0.0047515 | 0.0011908
47 | 0.97565 | -0.46838 | 0 | 0
48 | 0.97514 | -0.47837 | 0.0047459 | 0.0011894
49 | 0.97582 | -0.46488 | 0.004365 | 0.001094
50 | 0.97509 | -0.47939 | 0.0047326 | 0.0011861
51 | 0.97517 | -0.47765 | 0 | 0
52 | 0.97453 | -0.49022 | 0.0044046 | 0.0011039
53 | 0.97607 | -0.46007 | 0 | 0
54 | 0.97445 | -0.49178 | 0.0044146 | 0.0011064
55 | 0.97415 | -0.49783 | 0 | 0
56 | 0.97706 | -0.44068 | 0.0042758 | 0.0010716
57 | 0.98236 | -0.3384 | 0.0038176 | 0.00095678
58 | 0.98236 | -0.33848 | 0.0038692 | 0.00096971
59 | 0.98304 | -0.3251 | 0 | 0
60 | 0.98373 | -0.31188 | 0.004701 | 0.0011782
61 | 0.98659 | -0.25683 | 0.0041904 | 0.0010502
62 | 0.98665 | -0.25575 | 0.0038251 | 0.00095866
63 | 0.98468 | -0.2934 | 0.0044846 | 0.0011239
64 | 0.98684 | -0.2519 | 0.0039924 | 0.0010006
65 | 0.98502 | -0.28676 | 0.0035576 | 0.00089162
66 | 0.98702 | -0.24848 | 0.0038263 | 0.00095897
67 | 0.98736 | -0.2419 | 0 | 0
68 | 0.98739 | -0.24135 | 0 | 0
69 | 0.98507 | -0.28588 | 0.003779 | 0.00094711
70 | 0.98585 | -0.27073 | 0.00458 | 0.0011479
71 | 0.98684 | -0.25158 | 0.0029319 | 0.00073481
72 | 0.98725 | -0.24398 | 0.0073547 | 0.0018433
73 | 0.98734 | -0.24222 | 0.0027205 | 0.00068182
74 | 0.98758 | -0.23753 | 0 | 0
75 | 0.98756 | -0.23796 | 0.0031833 | 0.00079782
76 | 0.98827 | -0.22425 | 0 | 0
77 | 0.9879 | -0.23143 | 0.0036853 | 0.00092363
78 | 0.98801 | -0.22924 | 0.0042262 | 0.0010592
79 | 0.98784 | -0.23245 | 0.0035284 | 0.0008843
80 | 0.9886 | -0.21776 | 0.0030163 | 0.00075597
81 | 1 | 0 | -0.4486 | -0.11488
82 | 0.99797 | -0.038301 | 0 | 0
83 | 0.98924 | -0.20525 | 0 | 0
84 | 0.99761 | -0.045159 | 0.0042766 | 0.0010718
85 | 0.97071 | -0.56559 | 0.0024977 | 0.00062599
86 | 0.9946 | -0.10219 | 0.0054904 | 0.001376
87 | 0.97403 | -0.50008 | 0.0043294 | 0.0010851
88 | 0.97287 | -0.52294 | 0.0043165 | 0.0010818
89 | 0.98441 | -0.2976 | 0 | 0
90 | 0.98992 | -0.19147 | 0.0043301 | 0.0010852
91 | 0.99 | -0.19006 | 0 | 0
92 | 0.97024 | -0.57501 | 0.0052674 | 0.0013201
93 | 0.97032 | -0.57358 | 0 | 0
94 | 0.97042 | -0.57157 | 0.0036906 | 0.00092496
95 | 0.97095 | -0.56106 | 0.0030866 | 0.00077358
96 | 0.97072 | -0.56556 | 0.004612 | 0.0011559
97 | 0.97375 | -0.50566 | 0.0018305 | 0.00045876
98 | 0.97353 | -0.51005 | 0.0033247 | 0.00083325
99 | 0.97606 | -0.46035 | 0.014225 | 0.0035652
100 | 0.99186 | -0.15458 | 0.0062827 | 0.0015746
101 | 0.99279 | -0.13717 | 0.003517 | 0.00088145
102 | 0.99305 | -0.13207 | 0.0029231 | 0.0007326
103 | 0.98994 | -0.19188 | 0.0026304 | 0.00065923
104 | 0.99484 | -0.097859 | 0.0036446 | 0.00091343
105 | 0.98987 | -0.19311 | 0.0025293 | 0.00063391
106 | 0.99487 | -0.097345 | 0.0026271 | 0.00065841
107 | 0.997 | -0.056687 | 0.0033773 | 0.00084643
108 | 0.98786 | -0.23196 | 0.0026824 | 0.00067226
109 | 0.99759 | -0.045585 | 0.004442 | 0.0011133
110 | 0.9735 | -0.51071 | 0 | 0
111 | 0.97342 | -0.51219 | 0.002619 | 0.00065638
112 | 0.97346 | -0.51138 | 0.0024314 | 0.00060936
113 | 0.97395 | -0.50187 | 0.001512 | 0.00037895
114 | 0.97342 | -0.5122 | 0.0012494 | 0.00031312
115 | 0.97507 | -0.47984 | 0.0018131 | 0.00045441
116 | 0.97579 | -0.46561 | 0.0016657 | 0.00041746
117 | 0.98446 | -0.29669 | 0.0056786 | 0.0014232
118 | 0.98898 | -0.20952 | 0.0064573 | 0.0016183
119 | 0.98006 | -0.38194 | 0 | 0
120 | 0.98037 | -0.37587 | 0 | 0
121 | 0.97815 | -0.41936 | 0.0055954 | 0.0014023
122 | 0.98808 | -0.22683 | 0.0056788 | 0.0014232
123 | 0.98712 | -0.24531 | 0.0055288 | 0.0013857
124 | 0.98636 | -0.25997 | 0.0047337 | 0.0011864
125 | 0.98541 | -0.27827 | 0 | 0
126 | 0.98583 | -0.27024 | 0.0048607 | 0.0012182
127 | 0.98025 | -0.37822 | 0.0054472 | 0.0013652
128 | 0.98126 | -0.35867 | 0.0055971 | 0.0014028
129 | 0.98353 | -0.31454 | 0.005448 | 0.0013654
130 | 0.9918 | -0.15569 | 0.0063662 | 0.0015955
131 | 0.98508 | -0.28481 | 0.0048617 | 0.0012185
132 | 0.98514 | -0.2836 | 0 | 0
133 | 0.98487 | -0.28886 | 0 | 0
134 | 0.98519 | -0.28251 | 0.0047337 | 0.0011864
135 | 0.98481 | -0.28999 | 0.0055299 | 0.0013859
136 | 0.98486 | -0.28893 | 0.0055963 | 0.0014026
137 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.034635 | -0.0086897 | 0.034666 | 0.0087097 | 3.1848e-05 | 2.0003e-05 | 0.052854 | 0.052854 | 0.052854 | 0.97515 | -0.47946 | 0.97613 | -0.46019 | 14.5203
1 | 0.026007 | 0.0065273 | -0.025991 | -0.0065177 | 1.5606e-05 | 9.6585e-06 | 0.039688 | 0.039688 | 0.039688 | 0.97515 | -0.47946 | 0.97451 | -0.49205 | 10.9034
2 | -0.034666 | -0.0087097 | 0.034669 | 0.0087114 | 2.7844e-06 | 1.7488e-06 | 0.052854 | 0.052854 | 0.052854 | 0.97613 | -0.46019 | 0.97621 | -0.45851 | 14.5202
3 | 0.0087495 | 0.0021932 | -0.0087476 | -0.0021924 | 1.891e-06 | 8.5835e-07 | 0.01336 | 0.01336 | 0.01336 | 0.97451 | -0.49205 | 0.97428 | -0.49659 | 3.6704
4 | 0.017242 | 0.0043245 | -0.017232 | -0.0043188 | 9.6151e-06 | 5.6931e-06 | 0.026328 | 0.026328 | 0.026328 | 0.97451 | -0.49205 | 0.97391 | -0.50375 | 7.2331
5 | -0.034669 | -0.0087114 | 0.034747 | 0.0087604 | 7.8004e-05 | 4.8989e-05 | 0.052854 | 0.052853 | 0.052854 | 0.97621 | -0.45851 | 0.97861 | -0.41149 | 14.5202
6 | -0.039061 | -0.0098415 | 0.039134 | 0.0098873 | 7.2661e-05 | 4.5812e-05 | 0.059413 | 0.059412 | 0.059413 | 0.97861 | -0.41149 | 0.9806 | -0.37267 | 16.3221
7 | 0.013826 | 0.0034659 | -0.013823 | -0.0034645 | 2.5623e-06 | 1.452e-06 | 0.021198 | 0.021198 | 0.021198 | 0.97055 | -0.56886 | 0.97035 | -0.57275 | 5.8236
8 | -0.013826 | -0.0034659 | 0.013832 | 0.0034694 | 6.0909e-06 | 3.4512e-06 | 0.021198 | 0.021198 | 0.021198 | 0.97055 | -0.56886 | 0.97102 | -0.55961 | 5.8236
9 | 0.010953 | 0.0027453 | -0.01095 | -0.0027441 | 2.2852e-06 | 1.195e-06 | 0.016784 | 0.016784 | 0.016784 | 0.97102 | -0.55961 | 0.97079 | -0.56399 | 4.6111
10 | -0.024785 | -0.0062146 | 0.024795 | 0.0062212 | 1.0747e-05 | 6.632e-06 | 0.037982 | 0.037982 | 0.037982 | 0.97102 | -0.55961 | 0.97147 | -0.55052 | 10.4346
11 | 0.0037548 | 0.00093982 | -0.0037538 | -0.00094017 | 9.8388e-07 | -3.5224e-07 | 0.0057508 | 0.0057512 | 0.0057512 | 0.97147 | -0.55052 | 0.9712 | -0.55602 | 1.58
12 | -0.02855 | -0.0071611 | 0.028574 | 0.0071762 | 2.4343e-05 | 1.5159e-05 | 0.043733 | 0.043732 | 0.043733 | 0.97147 | -0.55052 | 0.97238 | -0.53265 | 12.0144
13 | 0.0037538 | 0.00094017 | -0.0037528 | -0.00094053 | 1.028e-06 | -3.6731e-07 | 0.0057512 | 0.0057515 | 0.0057515 | 0.9712 | -0.55602 | 0.97091 | -0.56178 | 1.5801
14 | -0.032953 | -0.0082736 | 0.032968 | 0.0082831 | 1.5275e-05 | 9.5769e-06 | 0.050433 | 0.050433 | 0.050433 | 0.97238 | -0.53265 | 0.97287 | -0.52294 | 13.8551
15 | 0.0024979 | 0.00062568 | -0.0024977 | -0.00062599 | 1.902e-07 | -3.0604e-07 | 0.0038286 | 0.0038288 | 0.0038288 | 0.97079 | -0.56399 | 0.97071 | -0.56559 | 1.0519
16 | 0.019101 | 0.0047896 | -0.019096 | -0.0047867 | 4.8818e-06 | 2.9194e-06 | 0.028643 | 0.028643 | 0.028643 | 0.99235 | -0.14514 | 0.99207 | -0.1505 | 7.869
17 | 0.25391 | 0.064901 | -0.25368 | -0.06476 | 0.00022206 | 0.00014128 | 0.38118 | 0.38118 | 0.38118 | 0.99235 | -0.14514 | 0.9914 | -0.16323 | 26.1802
18 | -0.27301 | -0.069691 | 0.27362 | 0.070081 | 0.00061258 | 0.00039003 | 0.40983 | 0.40983 | 0.40983 | 0.99235 | -0.14514 | 0.99478 | -0.098813 | 28.1474
19 | 0.012652 | 0.0031715 | -0.012649 | -0.0031702 | 2.4584e-06 | 1.3384e-06 | 0.018977 | 0.018977 | 0.018977 | 0.99207 | -0.1505 | 0.99186 | -0.15458 | 5.2134
20 | 0.24897 | 0.063578 | -0.24865 | -0.063373 | 0.0003224 | 0.00020507 | 0.37411 | 0.37411 | 0.37411 | 0.9914 | -0.16323 | 0.99 | -0.19006 | 25.6943
21 | 0.0054913 | 0.0013761 | -0.005491 | -0.0013761 | 2.8729e-07 | 3.6459e-08 | 0.008214 | 0.008214 | 0.008214 | 0.99478 | -0.098813 | 0.99472 | -0.099912 | 2.2566
22 | -0.27911 | -0.071457 | 0.2793 | 0.071578 | 0.00019067 | 0.00012142 | 0.41804 | 0.41804 | 0.41804 | 0.99478 | -0.098813 | 0.99552 | -0.084719 | 28.7115
23 | 0.0045714 | 0.0011456 | -0.0045712 | -0.0011456 | 2.3054e-07 | -2.3646e-08 | 0.0068329 | 0.006833 | 0.006833 | 0.99552 | -0.084719 | 0.99547 | -0.085777 | 1.8772
24 | -0.28763 | -0.073664 | 0.288 | 0.073903 | 0.00037446 | 0.00023853 | 0.43048 | 0.43048 | 0.43048 | 0.99552 | -0.084719 | 0.99694 | -0.057884 | 29.5659
25 | 0.0037523 | 0.00094004 | -0.0037517 | -0.00094028 | 5.1391e-07 | -2.3748e-07 | 0.0056084 | 0.0056086 | 0.0056086 | 0.99552 | -0.084719 | 0.99537 | -0.087594 | 1.5408
26 | 0.0045712 | 0.0011456 | -0.0045711 | -0.0011456 | 1.3941e-07 | -1.4289e-08 | 0.006833 | 0.006833 | 0.006833 | 0.99547 | -0.085777 | 0.99543 | -0.086418 | 1.8772
27 | -0.29301 | -0.075158 | 0.29329 | 0.075335 | 0.0002786 | 0.00017749 | 0.43796 | 0.43796 | 0.43796 | 0.99694 | -0.057884 | 0.99797 | -0.038301 | 30.0794
28 | 0.005491 | 0.0013761 | -0.0054904 | -0.001376 | 5.969e-07 | 7.5809e-08 | 0.008214 | 0.0082141 | 0.0082141 | 0.99472 | -0.099912 | 0.9946 | -0.10219 | 2.2566
29 | -0.082402 | -0.020856 | 0.082512 | 0.020926 | 0.00010989 | 7.0089e-05 | 0.12489 | 0.12489 | 0.12489 | 0.98234 | -0.33782 | 0.98377 | -0.31008 | 34.3114
30 | 0.073651 | 0.018663 | -0.073568 | -0.018609 | 8.3513e-05 | 5.3222e-05 | 0.11164 | 0.11164 | 0.11164 | 0.98234 | -0.33782 | 0.98112 | -0.36145 | 30.6698
31 | 0.0087511 | 0.0021932 | -0.00875 | -0.0021927 | 1.1334e-06 | 5.0764e-07 | 0.013256 | 0.013256 | 0.013256 | 0.98234 | -0.33782 | 0.9822 | -0.34054 | 3.6417
32 | -0.088443 | -0.022412 | 0.088496 | 0.022446 | 5.3095e-05 | 3.3579e-05 | 0.13386 | 0.13386 | 0.13386 | 0.98377 | -0.31008 | 0.98441 | -0.2976 | 18.3879
33 | 0.061882 | 0.015679 | -0.06173 | -0.015583 | 0.00015165 | 9.6476e-05 | 0.093914 | 0.093915 | 0.093915 | 0.98112 | -0.36145 | 0.9785 | -0.4126 | 25.8007
34 | 0.011686 | 0.00293 | -0.011681 | -0.0029275 | 4.7451e-06 | 2.5284e-06 | 0.017724 | 0.017724 | 0.017724 | 0.98112 | -0.36145 | 0.98069 | -0.36998 | 4.8692
35 | 0.0047578 | 0.0011921 | -0.0047573 | -0.0011921 | 5.0248e-07 | -4.793e-09 | 0.0072079 | 0.007208 | 0.007208 | 0.9822 | -0.34054 | 0.98209 | -0.34276 | 1.9802
36 | 0.0036705 | 0.00091976 | -0.0036703 | -0.00091986 | 2.3434e-07 | -9.4858e-08 | 0.0056217 | 0.0056218 | 0.0056218 | 0.97154 | -0.54927 | 0.97148 | -0.55061 | 1.5445
37 | 0.016672 | 0.0041828 | -0.016664 | -0.0041777 | 8.7603e-06 | 5.1633e-06 | 0.025537 | 0.025537 | 0.025537 | 0.97154 | -0.54927 | 0.97099 | -0.5603 | 7.0157
38 | -0.020343 | -0.0051026 | 0.020348 | 0.0051057 | 5.0236e-06 | 3.0442e-06 | 0.031159 | 0.031159 | 0.031159 | 0.97154 | -0.54927 | 0.97181 | -0.54409 | 8.5601
39 | 0.0036703 | 0.00091986 | -0.0036703 | -0.00091986 | 1.3041e-08 | -5.2775e-09 | 0.0056218 | 0.0056218 | 0.0056218 | 0.97148 | -0.55061 | 0.97147 | -0.55069 | 1.5445
40 | 0.0030867 | 0.00077349 | -0.0030866 | -0.00077358 | 1.1154e-07 | -9.3029e-08 | 0.0047303 | 0.0047304 | 0.0047304 | 0.97099 | -0.5603 | 0.97095 | -0.56106 | 1.2996
41 | 0.013577 | 0.0034042 | -0.013573 | -0.0034023 | 3.4024e-06 | 1.9184e-06 | 0.020807 | 0.020807 | 0.020807 | 0.97099 | -0.5603 | 0.97072 | -0.56556 | 5.7162
42 | -0.023626 | -0.0059272 | 0.023632 | 0.0059313 | 6.6738e-06 | 4.1027e-06 | 0.036178 | 0.036177 | 0.036178 | 0.97181 | -0.54409 | 0.97211 | -0.53817 | 9.9389
43 | 0.023645 | 0.0059388 | -0.023632 | -0.0059313 | 1.2242e-05 | 7.5254e-06 | 0.036177 | 0.036177 | 0.036177 | 0.97266 | -0.52732 | 0.97211 | -0.53817 | 9.9389
44 | -0.027585 | -0.0069261 | 0.02761 | 0.006942 | 2.5529e-05 | 1.5864e-05 | 0.042205 | 0.042205 | 0.042205 | 0.97266 | -0.52732 | 0.97364 | -0.50794 | 11.5949
45 | 0.0039403 | 0.00098736 | -0.0039399 | -0.00098744 | 3.1523e-07 | -8.5357e-08 | 0.0060279 | 0.006028 | 0.006028 | 0.97266 | -0.52732 | 0.97257 | -0.52899 | 1.6561
46 | -0.037236 | -0.0093544 | 0.03724 | 0.009357 | 4.0415e-06 | 2.5452e-06 | 0.056916 | 0.056916 | 0.056916 | 0.97364 | -0.50794 | 0.97375 | -0.50566 | 15.6364
47 | 0.0096259 | 0.0024124 | -0.009625 | -0.0024119 | 9.6996e-07 | 4.7216e-07 | 0.014711 | 0.014711 | 0.014711 | 0.97364 | -0.50794 | 0.97353 | -0.51005 | 4.0416
48 | 0.06173 | 0.015583 | -0.061607 | -0.015504 | 0.00012325 | 7.841e-05 | 0.093915 | 0.093915 | 0.093915 | 0.9785 | -0.4126 | 0.97636 | -0.45437 | 25.8008
49 | 0.058393 | 0.014699 | -0.058377 | -0.014688 | 1.6677e-05 | 1.0603e-05 | 0.089017 | 0.089017 | 0.089017 | 0.97636 | -0.45437 | 0.97606 | -0.46035 | 24.4552
50 | 0.0047573 | 0.0011921 | -0.0047567 | -0.0011921 | 5.7797e-07 | -5.407e-09 | 0.007208 | 0.0072081 | 0.0072081 | 0.98209 | -0.34276 | 0.98196 | -0.34531 | 1.9803
51 | -0.039134 | -0.0098873 | 0.039191 | 0.0099237 | 5.7717e-05 | 3.6388e-05 | 0.059412 | 0.059412 | 0.059412 | 0.9806 | -0.37267 | 0.98218 | -0.34196 | 16.3221
52 | -0.043331 | -0.010961 | 0.043339 | 0.010966 | 7.2364e-06 | 4.5747e-06 | 0.065684 | 0.065684 | 0.065684 | 0.98218 | -0.34196 | 0.98236 | -0.33848 | 18.0451
53 | 0.014234 | 0.0035682 | -0.014232 | -0.0035672 | 1.8831e-06 | 1.0723e-06 | 0.021713 | 0.021713 | 0.021713 | 0.97546 | -0.47195 | 0.97532 | -0.47473 | 5.9651
54 | -0.018997 | -0.0047619 | 0.019 | 0.0047638 | 3.2345e-06 | 1.9418e-06 | 0.028978 | 0.028978 | 0.028978 | 0.97546 | -0.47195 | 0.97565 | -0.46838 | 7.9611
55 | 0.0094804 | 0.0023763 | -0.0094787 | -0.0023755 | 1.6458e-06 | 7.9156e-07 | 0.014464 | 0.014464 | 0.014464 | 0.97532 | -0.47473 | 0.97514 | -0.47837 | 3.9736
56 | -0.019 | -0.0047638 | 0.019003 | 0.0047657 | 3.167e-06 | 1.9013e-06 | 0.028978 | 0.028978 | 0.028978 | 0.97565 | -0.46838 | 0.97582 | -0.46488 | 7.9611
57 | 0.0047328 | 0.0011861 | -0.0047326 | -0.0011861 | 2.2828e-07 | 5.0813e-10 | 0.007222 | 0.0072221 | 0.0072221 | 0.97514 | -0.47837 | 0.97509 | -0.47939 | 1.9841
58 | -0.023368 | -0.0058597 | 0.023373 | 0.005863 | 5.3608e-06 | 3.2902e-06 | 0.035634 | 0.035634 | 0.035634 | 0.97582 | -0.46488 | 0.97607 | -0.46007 | 9.7897
59 | 0.050524 | 0.012717 | -0.050494 | -0.012698 | 3.0337e-05 | 1.9246e-05 | 0.077115 | 0.077115 | 0.077115 | 0.97517 | -0.47765 | 0.97453 | -0.49022 | 21.1854
60 | -0.050524 | -0.012717 | 0.050567 | 0.012744 | 4.2491e-05 | 2.6956e-05 | 0.077115 | 0.077115 | 0.077115 | 0.97517 | -0.47765 | 0.97607 | -0.46007 | 21.1854
61 | 0.0044149 | 0.0011064 | -0.0044146 | -0.0011064 | 3.2844e-07 | -2.9914e-08 | 0.0067411 | 0.0067412 | 0.0067412 | 0.97453 | -0.49022 | 0.97445 | -0.49178 | 1.852
62 | 0.041675 | 0.010488 | -0.041659 | -0.010478 | 1.5161e-05 | 9.579e-06 | 0.063648 | 0.063648 | 0.063648 | 0.97453 | -0.49022 | 0.97415 | -0.49783 | 17.4858
63 | -0.07394 | -0.018607 | 0.074009 | 0.018651 | 6.8597e-05 | 4.3722e-05 | 0.11275 | 0.11275 | 0.11275 | 0.97607 | -0.46007 | 0.97706 | -0.44068 | 30.975
64 | 0.037329 | 0.0093931 | -0.037285 | -0.009365 | 4.4719e-05 | 2.8164e-05 | 0.057035 | 0.057035 | 0.057035 | 0.97415 | -0.49783 | 0.97287 | -0.52294 | 15.6689
65 | 0.0043299 | 0.001085 | -0.0043294 | -0.0010851 | 4.6345e-07 | -5.5078e-08 | 0.0066139 | 0.006614 | 0.006614 | 0.97415 | -0.49783 | 0.97403 | -0.50008 | 1.817
66 | -0.078285 | -0.019723 | 0.078364 | 0.019773 | 7.9909e-05 | 5.0954e-05 | 0.11926 | 0.11926 | 0.11926 | 0.97706 | -0.44068 | 0.97815 | -0.41936 | 32.764
67 | 0.047208 | 0.011936 | -0.047208 | -0.011936 | 1.79e-07 | 1.1338e-07 | 0.071545 | 0.071545 | 0.071545 | 0.98236 | -0.3384 | 0.98236 | -0.33848 | 19.6552
68 | -0.051026 | -0.012892 | 0.051058 | 0.012913 | 3.2546e-05 | 2.0646e-05 | 0.077328 | 0.077328 | 0.077328 | 0.98236 | -0.3384 | 0.98304 | -0.3251 | 21.2439
69 | -0.051058 | -0.012913 | 0.051091 | 0.012934 | 3.2396e-05 | 2.055e-05 | 0.077328 | 0.077328 | 0.077328 | 0.98304 | -0.3251 | 0.98373 | -0.31188 | 21.2439
70 | -0.055792 | -0.014112 | 0.055841 | 0.014143 | 4.9512e-05 | 3.1452e-05 | 0.084438 | 0.084438 | 0.084438 | 0.98373 | -0.31188 | 0.98468 | -0.2934 | 23.1974
71 | -0.0041904 | -0.0010502 | 0.0041906 | 0.0010502 | 2.1557e-07 | -4.5821e-08 | 0.0063202 | 0.0063201 | 0.0063202 | 0.98659 | -0.25683 | 0.98665 | -0.25575 | 1.7363
72 | -0.0080157 | -0.0020088 | 0.0080172 | 0.0020094 | 1.4707e-06 | 5.9843e-07 | 0.012089 | 0.012089 | 0.012089 | 0.98665 | -0.25575 | 0.98684 | -0.2519 | 3.3211
73 | -0.060326 | -0.015267 | 0.060345 | 0.01528 | 1.9237e-05 | 1.2234e-05 | 0.091215 | 0.091215 | 0.091215 | 0.98468 | -0.2934 | 0.98502 | -0.28676 | 25.0592
74 | -0.01201 | -0.00301 | 0.012012 | 0.0030111 | 1.9572e-06 | 1.0492e-06 | 0.018109 | 0.018109 | 0.018109 | 0.98684 | -0.2519 | 0.98702 | -0.24848 | 4.9749
75 | -0.063902 | -0.016171 | 0.063905 | 0.016173 | 2.6921e-06 | 1.7132e-06 | 0.09659 | 0.09659 | 0.09659 | 0.98502 | -0.28676 | 0.98507 | -0.28588 | 26.5356
76 | -0.015838 | -0.00397 | 0.015843 | 0.0039729 | 4.9723e-06 | 2.8849e-06 | 0.023877 | 0.023877 | 0.023877 | 0.98702 | -0.24848 | 0.98736 | -0.2419 | 6.5597
77 | -0.015843 | -0.0039729 | 0.015843 | 0.0039732 | 4.1284e-07 | 2.3952e-07 | 0.023877 | 0.023877 | 0.023877 | 0.98736 | -0.2419 | 0.98739 | -0.24135 | 6.5596
78 | -0.025919 | -0.0064987 | 0.025924 | 0.0065016 | 4.716e-06 | 2.9128e-06 | 0.039062 | 0.039062 | 0.039062 | 0.98739 | -0.24135 | 0.98758 | -0.23753 | 10.7314
79 | 0.010076 | 0.0025255 | -0.010076 | -0.0025253 | 4.1867e-07 | 2.0602e-07 | 0.015185 | 0.015185 | 0.015185 | 0.98739 | -0.24135 | 0.98734 | -0.24222 | 4.1718
80 | -0.067684 | -0.01712 | 0.067733 | 0.017151 | 4.9242e-05 | 3.1355e-05 | 0.1023 | 0.1023 | 0.1023 | 0.98507 | -0.28588 | 0.98585 | -0.27073 | 28.1039
81 | -0.072313 | -0.018299 | 0.07238 | 0.018342 | 6.653e-05 | 4.239e-05 | 0.10921 | 0.10921 | 0.10921 | 0.98585 | -0.27073 | 0.98684 | -0.25158 | 30.003
82 | -0.075312 | -0.019076 | 0.075383 | 0.019122 | 7.1042e-05 | 4.5279e-05 | 0.11363 | 0.11363 | 0.11363 | 0.98684 | -0.25158 | 0.98786 | -0.23196 | 31.2175
83 | -0.0073547 | -0.0018433 | 0.0073553 | 0.0018435 | 6.1565e-07 | 2.2316e-07 | 0.011085 | 0.011085 | 0.011085 | 0.98725 | -0.24398 | 0.98734 | -0.24222 | 3.0454
84 | 0.0031834 | 0.00079776 | -0.0031833 | -0.00079782 | 6.5534e-08 | -5.5251e-08 | 0.0047965 | 0.0047965 | 0.0047965 | 0.98758 | -0.23753 | 0.98756 | -0.23796 | 1.3177
85 | -0.029108 | -0.0072993 | 0.029126 | 0.0073108 | 1.8433e-05 | 1.147e-05 | 0.043859 | 0.043859 | 0.043859 | 0.98758 | -0.23753 | 0.98827 | -0.22425 | 12.0491
86 | -0.04057 | -0.01018 | 0.040582 | 0.010187 | 1.2573e-05 | 7.9314e-06 | 0.061089 | 0.061089 | 0.061089 | 0.98827 | -0.22425 | 0.9886 | -0.21776 | 16.7828
87 | 0.011444 | 0.0028687 | -0.011441 | -0.0028673 | 2.7185e-06 | 1.427e-06 | 0.017231 | 0.017231 | 0.017231 | 0.98827 | -0.22425 | 0.98801 | -0.22924 | 4.7337
88 | -0.0072139 | -0.0018078 | 0.0072146 | 0.0018081 | 7.5218e-07 | 2.6385e-07 | 0.010866 | 0.010866 | 0.010866 | 0.9879 | -0.23143 | 0.98801 | -0.22924 | 2.9851
89 | 0.0035286 | 0.0008842 | -0.0035284 | -0.0008843 | 1.71e-07 | -9.7236e-08 | 0.0053148 | 0.0053149 | 0.0053149 | 0.9879 | -0.23143 | 0.98784 | -0.23245 | 1.4601
90 | -0.043598 | -0.010943 | 0.043625 | 0.01096 | 2.6029e-05 | 1.6451e-05 | 0.065629 | 0.065629 | 0.065629 | 0.9886 | -0.21776 | 0.98924 | -0.20525 | 18.03
91 | 0.44695 | 0.11488 | -0.44612 | -0.11435 | 0.00083003 | 0.00053018 | 0.66609 | 0.66609 | 0.66609 | 1 | 0 | 0.99797 | -0.038301 | 45.7479
92 | 0.15283 | 0.039015 | -0.15278 | -0.038983 | 5.063e-05 | 3.1861e-05 | 0.22813 | 0.22813 | 0.22813 | 0.99797 | -0.038301 | 0.99761 | -0.045159 | 15.6685
93 | 0.078166 | 0.019858 | -0.078065 | -0.019794 | 0.00010039 | 6.3999e-05 | 0.11767 | 0.11767 | 0.11767 | 0.98924 | -0.20525 | 0.98786 | -0.23196 | 32.3275
94 | -0.12179 | -0.030818 | 0.12186 | 0.030863 | 7.0981e-05 | 4.5355e-05 | 0.1833 | 0.1833 | 0.1833 | 0.98924 | -0.20525 | 0.98987 | -0.19311 | 50.3575
95 | 0.14851 | 0.037912 | -0.1485 | -0.03791 | 3.0509e-06 | 1.918e-06 | 0.22176 | 0.22176 | 0.22176 | 0.99761 | -0.045159 | 0.99759 | -0.045585 | 15.2304
96 | -0.088496 | -0.022446 | 0.0885 | 0.022448 | 3.87e-06 | 2.3596e-06 | 0.13386 | 0.13386 | 0.13386 | 0.98441 | -0.2976 | 0.98446 | -0.29669 | 9.194
97 | -0.0043301 | -0.0010852 | 0.0043304 | 0.0010852 | 2.905e-07 | -4.9184e-08 | 0.0065088 | 0.0065087 | 0.0065088 | 0.98992 | -0.19147 | 0.99 | -0.19006 | 1.7881
98 | 0.24432 | 0.062288 | -0.24409 | -0.062142 | 0.0002293 | 0.00014582 | 0.3676 | 0.3676 | 0.3676 | 0.99 | -0.19006 | 0.98898 | -0.20952 | 25.2473
99 | -0.0052674 | -0.0013201 | 0.0052678 | 0.0013202 | 3.6004e-07 | 4.8716e-08 | 0.0080784 | 0.0080783 | 0.0080784 | 0.97024 | -0.57501 | 0.97032 | -0.57358 | 2.2193
100 | -0.0052678 | -0.0013202 | 0.0052683 | 0.0013203 | 5.0285e-07 | 6.7989e-08 | 0.0080783 | 0.0080782 | 0.0080783 | 0.97032 | -0.57358 | 0.97042 | -0.57157 | 2.2193
101 | -0.0089589 | -0.0022452 | 0.0089615 | 0.0022464 | 2.5674e-06 | 1.1948e-06 | 0.013737 | 0.013737 | 0.013737 | 0.97042 | -0.57157 | 0.97072 | -0.56556 | 3.774
102 | -0.039071 | -0.0098157 | 0.039078 | 0.0098202 | 7.0694e-06 | 4.4586e-06 | 0.059714 | 0.059714 | 0.059714 | 0.97375 | -0.50566 | 0.97395 | -0.50187 | 16.4048
103 | 0.0063003 | 0.0015787 | -0.0063001 | -0.0015786 | 1.9921e-07 | 5.6265e-08 | 0.0096297 | 0.0096297 | 0.0096297 | 0.97353 | -0.51005 | 0.9735 | -0.51071 | 2.6455
104 | 0.044152 | 0.011123 | -0.04414 | -0.011116 | 1.1121e-05 | 7.0356e-06 | 0.06733 | 0.06733 | 0.06733 | 0.97606 | -0.46035 | 0.97579 | -0.46561 | 18.4974
105 | 0.0063665 | 0.0015956 | -0.0063662 | -0.0015955 | 3.3607e-07 | 8.8301e-08 | 0.0095512 | 0.0095513 | 0.0095513 | 0.99186 | -0.15458 | 0.9918 | -0.15569 | 2.624
106 | -0.13088 | -0.033256 | 0.13091 | 0.033277 | 3.216e-05 | 2.0554e-05 | 0.19633 | 0.19633 | 0.19633 | 0.99279 | -0.13717 | 0.99305 | -0.13207 | 53.9364
107 | 0.12736 | 0.032375 | -0.12703 | -0.032161 | 0.00033461 | 0.00021383 | 0.19106 | 0.19106 | 0.19106 | 0.99279 | -0.13717 | 0.98994 | -0.19188 | 52.4882
108 | -0.13384 | -0.034009 | 0.13406 | 0.034151 | 0.00022087 | 0.00014117 | 0.20071 | 0.20071 | 0.20071 | 0.99305 | -0.13207 | 0.99484 | -0.097859 | 55.1397
109 | 0.1244 | 0.031502 | -0.12439 | -0.031497 | 7.3383e-06 | 4.6893e-06 | 0.1871 | 0.1871 | 0.1871 | 0.98994 | -0.19188 | 0.98987 | -0.19311 | 51.402
110 | -0.1377 | -0.035064 | 0.1377 | 0.035066 | 3.4164e-06 | 2.1837e-06 | 0.20616 | 0.20616 | 0.20616 | 0.99484 | -0.097859 | 0.99487 | -0.097345 | 56.6373
111 | -0.14033 | -0.035725 | 0.14061 | 0.035901 | 0.0002757 | 0.00017623 | 0.21009 | 0.21009 | 0.21009 | 0.99487 | -0.097345 | 0.997 | -0.056687 | 57.7168
112 | -0.14398 | -0.036747 | 0.14406 | 0.036796 | 7.7275e-05 | 4.9223e-05 | 0.21513 | 0.21513 | 0.21513 | 0.997 | -0.056687 | 0.99759 | -0.045585 | 29.5508
113 | 0.0038686 | 0.00096941 | -0.0038684 | -0.0009695 | 2.7128e-07 | -8.3584e-08 | 0.0059132 | 0.0059133 | 0.0059133 | 0.9735 | -0.51071 | 0.97342 | -0.51219 | 1.6245
114 | 0.0024315 | 0.00060922 | -0.0024314 | -0.00060936 | 7.7638e-08 | -1.3667e-07 | 0.0037165 | 0.0037165 | 0.0037165 | 0.9735 | -0.51071 | 0.97346 | -0.51138 | 1.021
115 | 0.0012494 | 0.00031311 | -0.0012494 | -0.00031312 | 5.3887e-10 | -4.5523e-09 | 0.0019098 | 0.0019098 | 0.0019098 | 0.97342 | -0.51219 | 0.97342 | -0.5122 | 0.52468
116 | -0.04059 | -0.010199 | 0.040633 | 0.010226 | 4.2732e-05 | 2.698e-05 | 0.062024 | 0.062024 | 0.062024 | 0.97395 | -0.50187 | 0.97507 | -0.47984 | 17.0395
117 | -0.042446 | -0.010681 | 0.042475 | 0.010699 | 2.8877e-05 | 1.8252e-05 | 0.064791 | 0.06479 | 0.064791 | 0.97507 | -0.47984 | 0.97579 | -0.46561 | 17.7996
118 | -0.094179 | -0.023871 | 0.094209 | 0.02389 | 3.0299e-05 | 1.8581e-05 | 0.14245 | 0.14245 | 0.14245 | 0.98446 | -0.29669 | 0.98481 | -0.28999 | 9.7835
119 | 0.23763 | 0.060524 | -0.23743 | -0.060398 | 0.00019822 | 0.00012601 | 0.35788 | 0.35788 | 0.35788 | 0.98898 | -0.20952 | 0.98808 | -0.22683 | 24.58
120 | -0.084111 | -0.021272 | 0.084135 | 0.021288 | 2.4507e-05 | 1.5634e-05 | 0.12777 | 0.12777 | 0.12777 | 0.98006 | -0.38194 | 0.98037 | -0.37587 | 35.1024
121 | 0.084111 | 0.021272 | -0.08396 | -0.021176 | 0.00015068 | 9.6126e-05 | 0.12777 | 0.12777 | 0.12777 | 0.98006 | -0.38194 | 0.97815 | -0.41936 | 35.1025
122 | 0.0054478 | 0.0013653 | -0.0054472 | -0.0013652 | 6.106e-07 | 9.0525e-08 | 0.0082686 | 0.0082687 | 0.0082687 | 0.98037 | -0.37587 | 0.98025 | -0.37822 | 2.2716
123 | -0.089583 | -0.022653 | 0.089657 | 0.0227 | 7.3961e-05 | 4.7201e-05 | 0.13604 | 0.13604 | 0.13604 | 0.98037 | -0.37587 | 0.98126 | -0.35867 | 37.374
124 | 0.23175 | 0.058975 | -0.23155 | -0.058844 | 0.00020619 | 0.00013104 | 0.34933 | 0.34933 | 0.34933 | 0.98808 | -0.22683 | 0.98712 | -0.24531 | 23.9927
125 | 0.22602 | 0.057458 | -0.22586 | -0.057357 | 0.00015953 | 0.00010135 | 0.341 | 0.341 | 0.341 | 0.98712 | -0.24531 | 0.98636 | -0.25997 | 23.4203
126 | 0.10677 | 0.027174 | -0.10668 | -0.027114 | 9.4071e-05 | 5.9713e-05 | 0.16123 | 0.16123 | 0.16123 | 0.98636 | -0.25997 | 0.98541 | -0.27827 | 22.1465
127 | 0.11435 | 0.028996 | -0.1143 | -0.028961 | 5.6398e-05 | 3.5065e-05 | 0.17263 | 0.17263 | 0.17263 | 0.98636 | -0.25997 | 0.98583 | -0.27024 | 11.8566
128 | 0.10668 | 0.027114 | -0.10662 | -0.027079 | 5.4763e-05 | 3.4977e-05 | 0.16123 | 0.16123 | 0.16123 | 0.98541 | -0.27827 | 0.98486 | -0.28893 | 44.293
129 | 0.10944 | 0.027743 | -0.10937 | -0.027703 | 6.4503e-05 | 3.9998e-05 | 0.1653 | 0.1653 | 0.1653 | 0.98583 | -0.27024 | 0.98519 | -0.28251 | 11.3527
130 | -0.095254 | -0.024103 | 0.095456 | 0.024232 | 0.00020223 | 0.0001291 | 0.14453 | 0.14453 | 0.14453 | 0.98126 | -0.35867 | 0.98353 | -0.31454 | 39.7058
131 | -0.1009 | -0.025597 | 0.10103 | 0.025677 | 0.0001244 | 7.9434e-05 | 0.15277 | 0.15277 | 0.15277 | 0.98353 | -0.31454 | 0.98486 | -0.28893 | 41.9701
132 | -0.0048617 | -0.0012185 | 0.004862 | 0.0012185 | 2.8032e-07 | 2.9439e-09 | 0.0073439 | 0.0073438 | 0.0073439 | 0.98508 | -0.28481 | 0.98514 | -0.2836 | 2.0176
133 | 0.099769 | 0.025295 | -0.099744 | -0.025279 | 2.5236e-05 | 1.5549e-05 | 0.1508 | 0.1508 | 0.1508 | 0.98514 | -0.2836 | 0.98487 | -0.28886 | 10.3573
134 | -0.10463 | -0.026513 | 0.10464 | 0.026517 | 5.4589e-06 | 3.3751e-06 | 0.15815 | 0.15815 | 0.15815 | 0.98514 | -0.2836 | 0.98519 | -0.28251 | 10.8617
135 | 0.099744 | 0.025279 | -0.099739 | -0.025276 | 5.429e-06 | 3.3449e-06 | 0.1508 | 0.1508 | 0.1508 | 0.98487 | -0.28886 | 0.98481 | -0.28999 | 10.3573

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.45217 | 0.11577

## res_load
| p_mw | q_mvar
0 | 0.0086278 | 0.0021623
1 | 0.0087476 | 0.0021924
2 | 0.017232 | 0.0043188
3 | 0.0043138 | 0.0010811
4 | 0.013823 | 0.0034645
5 | 0.0043785 | 0.0010973
6 | 0.0084524 | 0.0021184
7 | 0.0064447 | 0.0016152
8 | 0.0047141 | 0.0011815
9 | 0.0050091 | 0.0012554
10 | 0.0037517 | 0.00094028
11 | 0.0045711 | 0.0011456
12 | 0.0059308 | 0.0014864
13 | 0.0039922 | 0.0010005
14 | 0.0032778 | 0.0008215
15 | 0.0039399 | 0.00098744
16 | 0.011681 | 0.0029275
17 | 0.0032137 | 0.00080542
18 | 0.0036703 | 0.00091986
19 | 0.0047567 | 0.0011921
20 | 0.0037528 | 0.00094053
21 | 0.00414 | 0.0010376
22 | 0.0047628 | 0.0011937
23 | 0.0047515 | 0.0011908
24 | 0.0047459 | 0.0011894
25 | 0.004365 | 0.001094
26 | 0.0047326 | 0.0011861
27 | 0.0044046 | 0.0011039
28 | 0.0044146 | 0.0011064
29 | 0.0042758 | 0.0010716
30 | 0.0038176 | 0.00095678
31 | 0.0038692 | 0.00096971
32 | 0.004701 | 0.0011782
33 | 0.0041904 | 0.0010502
34 | 0.0038251 | 0.00095866
35 | 0.0044846 | 0.0011239
36 | 0.0039924 | 0.0010006
37 | 0.0035576 | 0.00089162
38 | 0.0038263 | 0.00095897
39 | 0.003779 | 0.00094711
40 | 0.00458 | 0.0011479
41 | 0.0029319 | 0.00073481
42 | 0.0073547 | 0.0018433
43 | 0.0027205 | 0.00068182
44 | 0.0031833 | 0.00079782
45 | 0.0036853 | 0.00092363
46 | 0.0042262 | 0.0010592
47 | 0.0035284 | 0.0008843
48 | 0.0030163 | 0.00075597
49 | 0.003565 | 0.00089347
50 | 0.0042766 | 0.0010718
51 | 0.0024977 | 0.00062599
52 | 0.0054904 | 0.001376
53 | 0.0043294 | 0.0010851
54 | 0.0043165 | 0.0010818
55 | 0.0043301 | 0.0010852
56 | 0.0052674 | 0.0013201
57 | 0.0036906 | 0.00092496
58 | 0.0030866 | 0.00077358
59 | 0.004612 | 0.0011559
60 | 0.0018305 | 0.00045876
61 | 0.0033247 | 0.00083325
62 | 0.014225 | 0.0035652
63 | 0.0062827 | 0.0015746
64 | 0.003517 | 0.00088145
65 | 0.0029231 | 0.0007326
66 | 0.0026304 | 0.00065923
67 | 0.0036446 | 0.00091343
68 | 0.0025293 | 0.00063391
69 | 0.0026271 | 0.00065841
70 | 0.0033773 | 0.00084643
71 | 0.0026824 | 0.00067226
72 | 0.004442 | 0.0011133
73 | 0.002619 | 0.00065638
74 | 0.0024314 | 0.00060936
75 | 0.001512 | 0.00037895
76 | 0.0012494 | 0.00031312
77 | 0.0018131 | 0.00045441
78 | 0.0016657 | 0.00041746
79 | 0.0056786 | 0.0014232
80 | 0.0064573 | 0.0016183
81 | 0.0055954 | 0.0014023
82 | 0.0056788 | 0.0014232
83 | 0.0055288 | 0.0013857
84 | 0.0047337 | 0.0011864
85 | 0.0048607 | 0.0012182
86 | 0.0054472 | 0.0013652
87 | 0.0055971 | 0.0014028
88 | 0.005448 | 0.0013654
89 | 0.0063662 | 0.0015955
90 | 0.0048617 | 0.0012185
91 | 0.0047337 | 0.0011864
92 | 0.0055299 | 0.0013859
93 | 0.0055963 | 0.0014026

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1