## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-105_1_5_node_16 | 0.4 | n |  | TRUE
1 | bus_LV_261-105_1_5_node_133 | 0.4 | n |  | TRUE
2 | bus_LV_261-105_1_5_node_17 | 0.4 | n |  | TRUE
3 | bus_LV_261-105_1_5_node_20 | 0.4 | n |  | TRUE
4 | bus_LV_261-105_1_5_node_27 | 0.4 | n |  | TRUE
5 | bus_LV_261-105_1_5_node_38 | 0.4 | n |  | TRUE
6 | bus_LV_261-105_1_5_node_63 | 0.4 | n |  | TRUE
7 | bus_LV_261-105_1_5_node_62 | 0.4 | n |  | TRUE
8 | bus_LV_261-105_1_5_node_18 | 0.4 | n |  | TRUE
9 | bus_LV_261-105_1_5_node_26 | 0.4 | n |  | TRUE
10 | bus_LV_261-105_1_5_node_58 | 0.4 | n |  | TRUE
11 | bus_LV_261-105_1_5_node_19 | 0.4 | n |  | TRUE
12 | bus_LV_261-105_1_5_node_29 | 0.4 | n |  | TRUE
13 | bus_LV_261-105_1_5_node_122 | 0.4 | n |  | TRUE
14 | bus_LV_261-105_1_5_node_119 | 0.4 | n |  | TRUE
15 | bus_LV_261-105_1_5_node_21 | 0.4 | n |  | TRUE
16 | bus_LV_261-105_1_5_node_121 | 0.4 | n |  | TRUE
17 | bus_LV_261-105_1_5_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_261-105_1_5_node_23 | 0.4 | n |  | TRUE
19 | bus_LV_261-105_1_5_node_67 | 0.4 | n |  | TRUE
20 | bus_LV_261-105_1_5_node_70 | 0.4 | n |  | TRUE
21 | bus_LV_261-105_1_5_node_126 | 0.4 | n |  | TRUE
22 | bus_LV_261-105_1_5_node_24 | 0.4 | n |  | TRUE
23 | bus_LV_261-105_1_5_node_128 | 0.4 | n |  | TRUE
24 | bus_LV_261-105_1_5_node_127 | 0.4 | n |  | TRUE
25 | bus_LV_261-105_1_5_node_25 | 0.4 | n |  | TRUE
26 | bus_LV_261-105_1_5_node_92 | 0.4 | n |  | TRUE
27 | bus_LV_261-105_1_5_node_90 | 0.4 | n |  | TRUE
28 | bus_LV_261-105_1_5_node_72 | 0.4 | n |  | TRUE
29 | bus_LV_261-105_1_5_node_131 | 0.4 | n |  | TRUE
30 | bus_LV_261-105_1_5_node_80 | 0.4 | n |  | TRUE
31 | bus_LV_261-105_1_5_node_132 | 0.4 | n |  | TRUE
32 | bus_LV_261-105_1_5_node_32 | 0.4 | n |  | TRUE
33 | bus_LV_261-105_1_5_node_60 | 0.4 | n |  | TRUE
34 | bus_LV_261-105_1_5_node_59 | 0.4 | n |  | TRUE
35 | bus_LV_261-105_1_5_node_61 | 0.4 | n |  | TRUE
36 | bus_LV_261-105_1_5_node_118 | 0.4 | n |  | TRUE
37 | bus_LV_261-105_1_5_node_120 | 0.4 | n |  | TRUE
38 | bus_LV_261-105_1_5_node_65 | 0.4 | n |  | TRUE
39 | bus_LV_261-105_1_5_node_71 | 0.4 | n |  | TRUE
40 | bus_LV_261-105_1_5_node_125 | 0.4 | n |  | TRUE
41 | bus_LV_261-105_1_5_node_95 | 0.4 | n |  | TRUE
42 | bus_LV_261-105_1_5_node_91 | 0.4 | n |  | TRUE
43 | bus_LV_261-105_1_5_node_76 | 0.4 | n |  | TRUE
44 | bus_LV_261-105_1_5_node_124 | 0.4 | n |  | TRUE
45 | bus_LV_261-105_1_5_node_123 | 0.4 | n |  | TRUE
46 | bus_LV_261-105_1_5_node_64 | 0.4 | n |  | TRUE
47 | bus_LV_261-105_1_5_node_66 | 0.4 | n |  | TRUE
48 | bus_LV_261-105_1_5_node_68 | 0.4 | n |  | TRUE
49 | bus_LV_261-105_1_5_node_69 | 0.4 | n |  | TRUE
50 | bus_LV_261-105_1_5_node_73 | 0.4 | n |  | TRUE
51 | bus_LV_261-105_1_5_node_74 | 0.4 | n |  | TRUE
52 | bus_LV_261-105_1_5_node_77 | 0.4 | n |  | TRUE
53 | bus_LV_261-105_1_5_node_83 | 0.4 | n |  | TRUE
54 | bus_LV_261-105_1_5_node_84 | 0.4 | n |  | TRUE
55 | bus_LV_261-105_1_5_node_85 | 0.4 | n |  | TRUE
56 | bus_LV_261-105_1_5_node_86 | 0.4 | n |  | TRUE
57 | bus_LV_261-105_1_5_node_87 | 0.4 | n |  | TRUE
58 | bus_LV_261-105_1_5_node_88 | 0.4 | n |  | TRUE
59 | bus_LV_261-105_1_5_node_89 | 0.4 | n |  | TRUE
60 | bus_LV_261-105_1_5_node_98 | 0.4 | n |  | TRUE
61 | bus_LV_261-105_1_5_node_93 | 0.4 | n |  | TRUE
62 | bus_LV_261-105_1_5_node_94 | 0.4 | n |  | TRUE
63 | bus_LV_261-105_1_5_node_96 | 0.4 | n |  | TRUE
64 | bus_LV_261-105_1_5_node_100 | 0.4 | n |  | TRUE
65 | bus_LV_261-105_1_5_node_101 | 0.4 | n |  | TRUE
66 | bus_LV_261-105_1_5_node_102 | 0.4 | n |  | TRUE
67 | bus_LV_261-105_1_5_node_105 | 0.4 | n |  | TRUE
68 | bus_LV_261-105_1_5_node_103 | 0.4 | n |  | TRUE
69 | bus_LV_261-105_1_5_node_111 | 0.4 | n |  | TRUE
70 | bus_LV_261-105_1_5_node_97 | 0.4 | n |  | TRUE
71 | bus_LV_261-105_1_5_node_99 | 0.4 | n |  | TRUE
72 | bus_LV_261-105_1_5_node_106 | 0.4 | n |  | TRUE
73 | bus_LV_261-105_1_5_node_104 | 0.4 | n |  | TRUE
74 | bus_LV_261-105_1_5_node_112 | 0.4 | n |  | TRUE
75 | bus_LV_261-105_1_5_node_107 | 0.4 | n |  | TRUE
76 | bus_LV_261-105_1_5_node_108 | 0.4 | n |  | TRUE
77 | bus_LV_261-105_1_5_node_109 | 0.4 | n |  | TRUE
78 | bus_LV_261-105_1_5_node_110 | 0.4 | n |  | TRUE
79 | bus_LV_261-105_1_5_node_113 | 0.4 | n |  | TRUE
80 | bus_LV_261-105_1_5_node_114 | 0.4 | n |  | TRUE
81 | bus_LV_261-105_1_5_node_115 | 0.4 | n |  | TRUE
82 | bus_LV_261-105_1_5_node_116 | 0.4 | n |  | TRUE
83 | bus_LV_261-105_1_5_node_117 | 0.4 | n |  | TRUE
84 | bus_MV_389_1_node_173 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-105_1_5_load_133 | 1 | 0.0064291 | 0.0016113 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-105_1_5_load_63 | 6 | 0.0094985 | 0.0023806 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-105_1_5_load_62 | 7 | 0.0049372 | 0.0012374 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-105_1_5_load_58 | 10 | 0.045174 | 0.011322 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-105_1_5_load_122 | 13 | 0.0046603 | 0.001168 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-105_1_5_load_119 | 14 | 0.017368 | 0.0043529 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-105_1_5_load_121 | 16 | 0.017348 | 0.0043478 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-105_1_5_load_67 | 19 | 0.00025867 | 6.483e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-105_1_5_load_70 | 20 | 0.0030768 | 0.00077112 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-105_1_5_load_126 | 21 | 0.00028569 | 7.16e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-105_1_5_load_128 | 23 | 0.00078397 | 0.00019648 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-105_1_5_load_127 | 24 | 0.009541 | 0.0023912 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-105_1_5_load_92 | 26 | 0.00062695 | 0.00015713 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-105_1_5_load_90 | 27 | 0.0020662 | 0.00051784 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-105_1_5_load_72 | 28 | 0.0049851 | 0.0012494 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-105_1_5_load_131 | 29 | 0.063356 | 0.015879 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-105_1_5_load_80 | 30 | 0.0090966 | 0.0022798 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-105_1_5_load_132 | 31 | 0.0033044 | 0.00082816 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-105_1_5_load_60 | 33 | 0.0090106 | 0.0022583 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-105_1_5_load_59 | 34 | 0.0049417 | 0.0012385 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-105_1_5_load_61 | 35 | 0.0014132 | 0.00035418 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-105_1_5_load_118 | 36 | 0.016647 | 0.0041721 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-105_1_5_load_120 | 37 | 0.003075 | 0.00077066 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-105_1_5_load_65 | 38 | 0.00025868 | 6.4831e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-105_1_5_load_71 | 39 | 0.003076 | 0.00077093 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-105_1_5_load_125 | 40 | 0.00049796 | 0.0001248 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-105_1_5_load_95 | 41 | 0.00063788 | 0.00015987 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-105_1_5_load_91 | 42 | 0.00064592 | 0.00016188 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-105_1_5_load_124 | 44 | 0.0023596 | 0.00059138 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-105_1_5_load_123 | 45 | 0.0028741 | 0.00072032 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-105_1_5_load_64 | 46 | 0.00026205 | 6.5675e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-105_1_5_load_66 | 47 | 0.00026181 | 6.5616e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-105_1_5_load_68 | 48 | 0.0030789 | 0.00077163 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-105_1_5_load_69 | 49 | 0.0087546 | 0.0021941 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-105_1_5_load_73 | 50 | 0.0065704 | 0.0016467 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-105_1_5_load_83 | 53 | 0.0020304 | 0.00050887 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-105_1_5_load_84 | 54 | 0.0019432 | 0.00048701 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-105_1_5_load_85 | 55 | 0.00097907 | 0.00024538 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-105_1_5_load_86 | 56 | 0.0022367 | 0.00056058 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-105_1_5_load_87 | 57 | 0.0016213 | 0.00040634 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-105_1_5_load_88 | 58 | 0.0020262 | 0.00050781 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-105_1_5_load_98 | 60 | 0.0019924 | 0.00049935 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-105_1_5_load_94 | 62 | 0.00067721 | 0.00016972 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-105_1_5_load_96 | 63 | 0.0019738 | 0.00049469 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-105_1_5_load_100 | 64 | 0.00091728 | 0.00022989 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-105_1_5_load_101 | 65 | 0.00091711 | 0.00022985 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-105_1_5_load_102 | 66 | 0.00067955 | 0.00017031 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-105_1_5_load_105 | 67 | 0.00092673 | 0.00023226 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-105_1_5_load_103 | 68 | 0.00094275 | 0.00023628 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-105_1_5_load_111 | 69 | 0.00067163 | 0.00016833 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-105_1_5_load_97 | 70 | 0.0019564 | 0.00049032 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-105_1_5_load_99 | 71 | 0.003981 | 0.00099773 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-105_1_5_load_106 | 72 | 0.00063258 | 0.00015854 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-105_1_5_load_104 | 73 | 0.00096122 | 0.0002409 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-105_1_5_load_112 | 74 | 0.0006554 | 0.00016426 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-105_1_5_load_107 | 75 | 0.00064827 | 0.00016247 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-105_1_5_load_108 | 76 | 0.00062441 | 0.00015649 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-105_1_5_load_109 | 77 | 0.0006399 | 0.00016037 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-105_1_5_load_110 | 78 | 0.00063394 | 0.00015888 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-105_1_5_load_113 | 79 | 0.00071035 | 0.00017803 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-105_1_5_load_114 | 80 | 0.00069349 | 0.00017381 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-105_1_5_load_115 | 81 | 0.00062503 | 0.00015665 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-105_1_5_load_116 | 82 | 0.00065373 | 0.00016384 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-105_1_5_load_117 | 83 | 0.00096616 | 0.00024214 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 71 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-105_1_5_line_0 |  | 0 | 1 | 0.023027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-105_1_5_line_1 |  | 0 | 2 | 0.083783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-105_1_5_line_2 |  | 0 | 3 | 0.073856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
3 | LV_261-105_1_5_line_3 |  | 0 | 4 | 0.10723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
4 | LV_261-105_1_5_line_4 |  | 2 | 5 | 0.040783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-105_1_5_line_5 |  | 2 | 6 | 0.031241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-105_1_5_line_6 |  | 2 | 7 | 0.088552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-105_1_5_line_7 |  | 3 | 13 | 0.040852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-105_1_5_line_8 |  | 3 | 14 | 0.011274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
9 | LV_261-105_1_5_line_9 |  | 4 | 29 | 0.025165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-105_1_5_line_10 |  | 4 | 30 | 0.056894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
11 | LV_261-105_1_5_line_11 |  | 5 | 35 | 0.023871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-105_1_5_line_12 |  | 7 | 33 | 0.016746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-105_1_5_line_13 |  | 8 | 9 | 0.074192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_261-105_1_5_line_14 |  | 8 | 10 | 0.086947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_261-105_1_5_line_15 |  | 9 | 28 | 0.0058612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
16 | LV_261-105_1_5_line_16 |  | 9 | 15 | 0.015074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
17 | LV_261-105_1_5_line_17 |  | 9 | 22 | 0.015447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-105_1_5_line_18 |  | 11 | 12 | 0.067653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-105_1_5_line_19 |  | 11 | 13 | 0.078863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-105_1_5_line_20 |  | 12 | 31 | 0.098704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-105_1_5_line_21 |  | 14 | 36 | 0.024038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
22 | LV_261-105_1_5_line_22 |  | 15 | 16 | 0.01522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
23 | LV_261-105_1_5_line_23 |  | 16 | 37 | 0.023485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
24 | LV_261-105_1_5_line_24 |  | 17 | 18 | 0.39281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-105_1_5_line_25 |  | 17 | 19 | 0.026688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-105_1_5_line_26 |  | 17 | 20 | 0.040632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_261-105_1_5_line_27 |  | 18 | 21 | 0.02869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-105_1_5_line_28 |  | 19 | 38 | 0.00011659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-105_1_5_line_29 |  | 20 | 39 | 0.0067388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
30 | LV_261-105_1_5_line_30 |  | 21 | 40 | 0.00052448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-105_1_5_line_31 |  | 22 | 23 | 0.044104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-105_1_5_line_32 |  | 22 | 24 | 0.036593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-105_1_5_line_33 |  | 25 | 26 | 0.080362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
34 | LV_261-105_1_5_line_34 |  | 25 | 27 | 0.024856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
35 | LV_261-105_1_5_line_35 |  | 26 | 41 | 0.0077649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
36 | LV_261-105_1_5_line_36 |  | 27 | 42 | 7.3042e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
37 | LV_261-105_1_5_line_37 |  | 28 | 39 | 0.018577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
38 | LV_261-105_1_5_line_38 |  | 30 | 43 | 0.034094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
39 | LV_261-105_1_5_line_39 |  | 32 | 33 | 0.015074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-105_1_5_line_40 |  | 32 | 34 | 0.026716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-105_1_5_line_41 |  | 36 | 37 | 0.0011247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
42 | LV_261-105_1_5_line_42 |  | 38 | 46 | 0.027251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-105_1_5_line_43 |  | 40 | 45 | 0.0012937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-105_1_5_line_44 |  | 41 | 52 | 0.02213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
45 | LV_261-105_1_5_line_45 |  | 42 | 59 | 0.014438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
46 | LV_261-105_1_5_line_46 |  | 43 | 51 | 0.027375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
47 | LV_261-105_1_5_line_47 |  | 44 | 45 | 0.0016632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-105_1_5_line_48 |  | 46 | 47 | 0.0001846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-105_1_5_line_49 |  | 47 | 48 | 0.00017278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-105_1_5_line_50 |  | 48 | 49 | 0.0073491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-105_1_5_line_51 |  | 50 | 51 | 0.035408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-105_1_5_line_52 |  | 51 | 52 | 0.043366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
53 | LV_261-105_1_5_line_53 |  | 53 | 54 | 0.021728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
54 | LV_261-105_1_5_line_54 |  | 53 | 55 | 0.00040463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
55 | LV_261-105_1_5_line_55 |  | 54 | 56 | 0.00061213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
56 | LV_261-105_1_5_line_56 |  | 55 | 57 | 0.0078399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
57 | LV_261-105_1_5_line_57 |  | 56 | 58 | 0.0073026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
58 | LV_261-105_1_5_line_58 |  | 57 | 59 | 0.013998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
59 | LV_261-105_1_5_line_59 |  | 58 | 60 | 0.00033096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
60 | LV_261-105_1_5_line_60 |  | 59 | 61 | 0.041058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-105_1_5_line_61 |  | 59 | 62 | 0.013427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-105_1_5_line_62 |  | 60 | 63 | 0.021802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
63 | LV_261-105_1_5_line_63 |  | 61 | 64 | 0.003379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-105_1_5_line_64 |  | 61 | 65 | 0.0044164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-105_1_5_line_65 |  | 62 | 66 | 0.0077202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-105_1_5_line_66 |  | 63 | 70 | 0.00033989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
67 | LV_261-105_1_5_line_67 |  | 64 | 67 | 0.020081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-105_1_5_line_68 |  | 65 | 68 | 0.024673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-105_1_5_line_69 |  | 66 | 69 | 0.00024526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-105_1_5_line_70 |  | 67 | 72 | 0.0079318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-105_1_5_line_71 |  | 68 | 73 | 0.0062147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-105_1_5_line_72 |  | 69 | 74 | 0.02303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-105_1_5_line_73 |  | 70 | 71 | 0.0065999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
74 | LV_261-105_1_5_line_74 |  | 72 | 75 | 0.020166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-105_1_5_line_75 |  | 74 | 79 | 0.00037759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-105_1_5_line_76 |  | 75 | 76 | 0.0078377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-105_1_5_line_77 |  | 76 | 77 | 0.020048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-105_1_5_line_78 |  | 77 | 78 | 0.010922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-105_1_5_line_79 |  | 79 | 80 | 0.0074999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-105_1_5_line_80 |  | 80 | 81 | 4.1147e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_261-105_1_5_line_81 |  | 81 | 82 | 0.025061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-105_1_5_line_82 |  | 82 | 83 | 0.013019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-105_1_5_trafo_99 | 0.63 MVA 20/0.4 kV | 84 | 71 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29
0 | 2679728.4767 | 1250199.0019 | 2679741.6559 | 1250195.8546 | 2679742.7728 | 1250195.8919 | 2679744.0342 | 1250196.4092 | 2679745.0582 | 1250197.1791 | 2679745.8489 | 1250198.4574 | 2679746.3356 | 1250199.8761 | 2679746.9638 | 1250202.5643
1 | 2679728.4767 | 1250199.0019 | 2679718.1084 | 1250201.4086 | 2679720.1219 | 1250209.9976 | 2679726.9689 | 1250239.2223 | 2679734.7941 | 1250272.6188
2 | 2679663.6602 | 1250200.1424 | 2679668.7203 | 1250198.8984 | 2679674.3409 | 1250197.5174 | 2679675.9502 | 1250199.118 | 2679677.6715 | 1250200.2419 | 2679679.4528 | 1250200.8441 | 2679681.5125 | 1250201.5056 | 2679682.3583 | 1250205.4198 | 2679704.9554 | 1250200.3643 | 2679709.5677 | 1250199.2922 | 2679717.1732 | 1250197.4042 | 2679718.1084 | 1250201.4086 | 2679728.4767 | 1250199.0019
3 | 2679728.4767 | 1250199.0019 | 2679727.5803 | 1250194.9201 | 2679747.7103 | 1250190.8546 | 2679756.7771 | 1250188.6638 | 2679757.3706 | 1250183.279 | 2679764.7375 | 1250181.1765 | 2679770.4128 | 1250179.0958 | 2679778.8682 | 1250175.2179 | 2679793.3478 | 1250165.7836 | 2679814.3266 | 1250148.0418
4 | 2679744.2333 | 1250312.2972 | 2679734.7941 | 1250272.6188
5 | 2679734.7941 | 1250272.6188 | 2679765.1324 | 1250265.1634
6 | 2679734.7941 | 1250272.6188 | 2679723.7768 | 1250275.0168 | 2679695.4092 | 1250278.5936 | 2679646.7582 | 1250276.7778
7 | 2679663.6602 | 1250200.1424 | 2679669.6427 | 1250227.9878 | 2679672.4568 | 1250240.0346
8 | 2679663.6602 | 1250200.1424 | 2679660.9168 | 1250189.2073
9 | 2679814.3266 | 1250148.0418 | 2679817.9851 | 1250163.4135 | 2679819.0135 | 1250167.775 | 2679820.1424 | 1250172.527
10 | 2679814.3266 | 1250148.0418 | 2679858.6744 | 1250112.4016
11 | 2679744.2333 | 1250312.2972 | 2679731.6795 | 1250313.3069 | 2679720.4397 | 1250314.2169
12 | 2679646.7582 | 1250276.7778 | 2679639.5156 | 1250276.5075 | 2679630.0218 | 1250276.2131
13 | 2679633.0534 | 1250120.9062 | 2679630.7486 | 1250114.3149 | 2679642.8554 | 1250109.5184 | 2679640.2751 | 1250102.6454 | 2679646.8035 | 1250098.3299 | 2679649.2889 | 1250096.5398 | 2679659.6771 | 1250089.2963 | 2679666.0032 | 1250084.8669 | 2679672.3644 | 1250080.6382 | 2679680.0968 | 1250078.8741
14 | 2679680.0968 | 1250078.8741 | 2679674.1192 | 1250055.143 | 2679659.8475 | 1249994.3206
15 | 2679633.0534 | 1250120.9062 | 2679627.5407 | 1250122.8971
16 | 2679644.6149 | 1250127.4664 | 2679642.7902 | 1250123.917 | 2679641.1979 | 1250122.1721 | 2679639.3333 | 1250121.0351 | 2679637.6752 | 1250120.2567 | 2679635.3961 | 1250120.1816 | 2679633.0534 | 1250120.9062
17 | 2679627.9492 | 1250106.327 | 2679630.7486 | 1250114.3149 | 2679633.0534 | 1250120.9062
18 | 2679715.3344 | 1250228.0131 | 2679716.2376 | 1250232.1505 | 2679721.3423 | 1250254.5134 | 2679723.4364 | 1250263.2814 | 2679723.7602 | 1250266.1545 | 2679723.3485 | 1250268.1282 | 2679722.2093 | 1250270.3145 | 2679720.7123 | 1250271.5953 | 2679722.654 | 1250282.1514 | 2679724.7078 | 1250293.354
19 | 2679724.7078 | 1250293.354 | 2679716.3073 | 1250289.238 | 2679704.5413 | 1250283.3198 | 2679692.3851 | 1250276.0955 | 2679685.7903 | 1250269.6466 | 2679680.7113 | 1250263.3181 | 2679677.2477 | 1250257.0113 | 2679674.7184 | 1250249.7164 | 2679672.4568 | 1250240.0346
20 | 2679715.3344 | 1250228.0131 | 2679692.5882 | 1250131.9655
21 | 2679655.0675 | 1250165.8921 | 2679660.9168 | 1250189.2073
22 | 2679644.6149 | 1250127.4664 | 2679648.5388 | 1250140.5398 | 2679648.9353 | 1250142.0589
23 | 2679648.9353 | 1250142.0589 | 2679652.8756 | 1250157.1548 | 2679654.7939 | 1250164.8012
24 | 2679536.7165 | 1250137.0915 | 2679520.8093 | 1250138.1678 | 2679490.1146 | 1250140.1465 | 2679488.3519 | 1250139.2889 | 2679487.0693 | 1250139.216 | 2679485.8291 | 1250139.3662 | 2679484.7338 | 1250139.4071 | 2679484.6136 | 1250137.1149 | 2679475.5304 | 1250137.7158 | 2679468.4574 | 1250138.1769 | 2679467.4013 | 1250139.7972 | 2679464.2352 | 1250139.9994 | 2679462.9755 | 1250138.7816 | 2679444.0392 | 1250139.9731 | 2679364.7569 | 1250163.0615 | 2679363.4244 | 1250165.0229 | 2679363.2283 | 1250163.8861 | 2679363.0565 | 1250162.6162 | 2679362.914 | 1250161.9805 | 2679361.8685 | 1250156.6181 | 2679365.7391 | 1250155.6803 | 2679415.6167 | 1250143.6728 | 2679435.4172 | 1250139.4016 | 2679455.2004 | 1250136.4312 | 2679473.8588 | 1250134.5688 | 2679497.9772 | 1250133.169 | 2679538.8544 | 1250130.8156 | 2679550.2499 | 1250130.0679 | 2679556.2404 | 1250129.8148 | 2679562.1184 | 1250129.5157
25 | 2679562.1184 | 1250129.5157 | 2679562.202 | 1250130.5954 | 2679562.4955 | 1250136.2924 | 2679564.4791 | 1250143.1908 | 2679569.2694 | 1250150.2269 | 2679570.001 | 1250154.3731
26 | 2679562.1184 | 1250129.5157 | 2679589.5433 | 1250128.1495 | 2679602.6929 | 1250127.3601
27 | 2679536.7165 | 1250137.0915 | 2679538.8402 | 1250156.6121 | 2679539.2034 | 1250165.6591
28 | 2679570.0213 | 1250154.4879 | 2679570.001 | 1250154.3731
29 | 2679602.6929 | 1250127.3601 | 2679604.6782 | 1250127.2409 | 2679609.3906 | 1250126.6457
30 | 2679539.2034 | 1250165.6591 | 2679539.2244 | 1250166.1831
31 | 2679627.9492 | 1250106.327 | 2679629.3368 | 1250104.1996 | 2679630.0769 | 1250101.9412 | 2679630.3167 | 1250099.2647 | 2679629.729 | 1250097.4888 | 2679625.4605 | 1250089.2699 | 2679618.4135 | 1250078.8009 | 2679610.2265 | 1250069.0285
32 | 2679627.9492 | 1250106.327 | 2679626.0015 | 1250107.4349 | 2679613.8886 | 1250112.1202 | 2679600.7752 | 1250115.9802 | 2679593.2444 | 1250117.5592
33 | 2679822.5571 | 1250127.2373 | 2679885.3073 | 1250077.0337
34 | 2679822.5571 | 1250127.2373 | 2679809.9847 | 1250105.7957
35 | 2679885.3073 | 1250077.0337 | 2679891.3705 | 1250072.1828
36 | 2679809.9847 | 1250105.7957 | 2679809.9477 | 1250105.7327
37 | 2679627.5407 | 1250122.8971 | 2679624.5637 | 1250123.9722 | 2679618.1674 | 1250125.1983 | 2679612.6344 | 1250126.2359 | 2679609.3906 | 1250126.6457
38 | 2679885.25 | 1250091.0441 | 2679858.6744 | 1250112.4016
39 | 2679627.5269 | 1250291.0794 | 2679630.0218 | 1250276.2131
40 | 2679627.5269 | 1250291.0794 | 2679601.2373 | 1250286.3264
41 | 2679655.0675 | 1250165.8921 | 2679654.7939 | 1250164.8012
42 | 2679574.7567 | 1250181.3244 | 2679570.0213 | 1250154.4879
43 | 2679539.2763 | 1250167.4758 | 2679539.2244 | 1250166.1831
44 | 2679908.6507 | 1250058.3576 | 2679891.3705 | 1250072.1828
45 | 2679802.6446 | 1250093.2776 | 2679809.9477 | 1250105.7327
46 | 2679911.7444 | 1250089.2776 | 2679906.9384 | 1250092.3818 | 2679885.25 | 1250091.0441
47 | 2679539.2763 | 1250167.4758 | 2679539.343 | 1250169.1377
48 | 2679574.7888 | 1250181.5062 | 2679574.7567 | 1250181.3244
49 | 2679574.8188 | 1250181.6763 | 2679574.7888 | 1250181.5062
50 | 2679576.0959 | 1250188.9136 | 2679574.8188 | 1250181.6763
51 | 2679911.7444 | 1250089.2776 | 2679913.9591 | 1250091.8872 | 2679920.5138 | 1250086.7607 | 2679934.546 | 1250087.0167 | 2679941.7742 | 1250080.654
52 | 2679908.6507 | 1250058.3576 | 2679912.0703 | 1250062.3177 | 2679913.8322 | 1250064.3541 | 2679915.029 | 1250065.749 | 2679916.9766 | 1250068.0103 | 2679925.2473 | 1250078.3961 | 2679917.087 | 1250085.0132 | 2679911.7444 | 1250089.2776
53 | 2679783.6255 | 1250104.8105 | 2679765.0466 | 1250116.0764
54 | 2679783.6255 | 1250104.8105 | 2679783.9715 | 1250104.6007
55 | 2679764.5232 | 1250116.3938 | 2679765.0466 | 1250116.0764
56 | 2679783.9715 | 1250104.6007 | 2679790.6751 | 1250100.5357
57 | 2679758.2789 | 1250120.1802 | 2679764.5232 | 1250116.3938
58 | 2679802.6446 | 1250093.2776 | 2679790.6751 | 1250100.5357
59 | 2679757.9959 | 1250120.3518 | 2679758.2789 | 1250120.1802
60 | 2679781.762 | 1250057.8927 | 2679802.6446 | 1250093.2776
61 | 2679802.6446 | 1250093.2776 | 2679814.2723 | 1250086.5636
62 | 2679739.3533 | 1250131.6564 | 2679757.9959 | 1250120.3518
63 | 2679781.762 | 1250057.8927 | 2679784.6735 | 1250056.1778
64 | 2679781.762 | 1250057.8927 | 2679777.9807 | 1250060.1745
65 | 2679814.2723 | 1250086.5636 | 2679820.958 | 1250082.7032
66 | 2679739.0626 | 1250131.8327 | 2679739.3533 | 1250131.6564
67 | 2679784.6735 | 1250056.1778 | 2679801.9759 | 1250045.9863
68 | 2679756.8559 | 1250072.9219 | 2679777.9807 | 1250060.1745
69 | 2679820.958 | 1250082.7032 | 2679821.1704 | 1250082.5806
70 | 2679801.9759 | 1250045.9863 | 2679808.8102 | 1250041.9607
71 | 2679751.5349 | 1250076.1327 | 2679756.8559 | 1250072.9219
72 | 2679841.1147 | 1250071.0645 | 2679821.1704 | 1250082.5806
73 | 2679733.4192 | 1250135.2548 | 2679739.0626 | 1250131.8327
74 | 2679808.8102 | 1250041.9607 | 2679826.1863 | 1250031.7258
75 | 2679841.1147 | 1250071.0645 | 2679841.4417 | 1250070.8757
76 | 2679826.1863 | 1250031.7258 | 2679832.9395 | 1250027.748
77 | 2679832.9395 | 1250027.748 | 2679850.214 | 1250017.5729
78 | 2679850.214 | 1250017.5729 | 2679854.9375 | 1250014.7907 | 2679858.5224 | 1250010.6988
79 | 2679841.4417 | 1250070.8757 | 2679847.9366 | 1250067.1254
80 | 2679847.9366 | 1250067.1254 | 2679847.9722 | 1250067.1049
81 | 2679847.9722 | 1250067.1049 | 2679869.6748 | 1250054.5735
82 | 2679869.6748 | 1250054.5735 | 2679875.131 | 1250051.423 | 2679879.7091 | 1250046.5062

## bus_geodata
| x | y | coords
0 | 2679728.4767 | 1250199.0019
1 | 2679746.9638 | 1250202.5643
2 | 2679734.7941 | 1250272.6188
3 | 2679663.6602 | 1250200.1424
4 | 2679814.3266 | 1250148.0418
5 | 2679744.2333 | 1250312.2972
6 | 2679765.1324 | 1250265.1634
7 | 2679646.7582 | 1250276.7778
8 | 2679680.0968 | 1250078.8741
9 | 2679633.0534 | 1250120.9062
10 | 2679659.8475 | 1249994.3206
11 | 2679724.7078 | 1250293.354
12 | 2679715.3344 | 1250228.0131
13 | 2679672.4568 | 1250240.0346
14 | 2679660.9168 | 1250189.2073
15 | 2679644.6149 | 1250127.4664
16 | 2679648.9353 | 1250142.0589
17 | 2679562.1184 | 1250129.5157
18 | 2679536.7165 | 1250137.0915
19 | 2679570.001 | 1250154.3731
20 | 2679602.6929 | 1250127.3601
21 | 2679539.2033 | 1250165.6591
22 | 2679627.9492 | 1250106.327
23 | 2679610.2265 | 1250069.0285
24 | 2679593.2444 | 1250117.5592
25 | 2679822.5571 | 1250127.2373
26 | 2679885.3073 | 1250077.0337
27 | 2679809.9847 | 1250105.7957
28 | 2679627.5407 | 1250122.8971
29 | 2679820.1424 | 1250172.527
30 | 2679858.6744 | 1250112.4016
31 | 2679692.5882 | 1250131.9655
32 | 2679627.5269 | 1250291.0794
33 | 2679630.0218 | 1250276.2131
34 | 2679601.2373 | 1250286.3264
35 | 2679720.4397 | 1250314.2169
36 | 2679655.0675 | 1250165.8921
37 | 2679654.7939 | 1250164.8012
38 | 2679570.0213 | 1250154.4879
39 | 2679609.3906 | 1250126.6457
40 | 2679539.2244 | 1250166.1831
41 | 2679891.3705 | 1250072.1828
42 | 2679809.9477 | 1250105.7327
43 | 2679885.25 | 1250091.0441
44 | 2679539.343 | 1250169.1377
45 | 2679539.2763 | 1250167.4758
46 | 2679574.7567 | 1250181.3244
47 | 2679574.7888 | 1250181.5062
48 | 2679574.8188 | 1250181.6763
49 | 2679576.0959 | 1250188.9136
50 | 2679941.7742 | 1250080.654
51 | 2679911.7444 | 1250089.2776
52 | 2679908.6507 | 1250058.3576
53 | 2679783.6255 | 1250104.8105
54 | 2679765.0466 | 1250116.0764
55 | 2679783.9715 | 1250104.6007
56 | 2679764.5232 | 1250116.3938
57 | 2679790.6751 | 1250100.5357
58 | 2679758.2789 | 1250120.1802
59 | 2679802.6446 | 1250093.2776
60 | 2679757.9959 | 1250120.3518
61 | 2679781.762 | 1250057.8927
62 | 2679814.2723 | 1250086.5636
63 | 2679739.3533 | 1250131.6564
64 | 2679784.6735 | 1250056.1778
65 | 2679777.9807 | 1250060.1745
66 | 2679820.958 | 1250082.7032
67 | 2679801.9759 | 1250045.9863
68 | 2679756.8559 | 1250072.9219
69 | 2679821.1704 | 1250082.5806
70 | 2679739.0626 | 1250131.8327
71 | 2679733.4192 | 1250135.2548
72 | 2679808.8102 | 1250041.9607
73 | 2679751.5349 | 1250076.1327
74 | 2679841.1147 | 1250071.0645
75 | 2679826.1863 | 1250031.7258
76 | 2679832.9395 | 1250027.748
77 | 2679850.214 | 1250017.5729
78 | 2679858.5224 | 1250010.6988
79 | 2679841.4417 | 1250070.8757
80 | 2679847.9366 | 1250067.1254
81 | 2679847.9722 | 1250067.1049
82 | 2679869.6748 | 1250054.5735
83 | 2679879.7091 | 1250046.5062
84 | 2679802.6446 | 1250093.2776

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97692 | -0.44252 | 0 | 0
1 | 0.97678 | -0.44522 | 0.0064291 | 0.0016113
2 | 0.97459 | -0.48824 | 0 | 0
3 | 0.97488 | -0.48253 | 0 | 0
4 | 0.9806 | -0.37062 | 0 | 0
5 | 0.97454 | -0.4893 | 0 | 0
6 | 0.97431 | -0.49369 | 0.0094985 | 0.0023806
7 | 0.97303 | -0.51899 | 0.0049372 | 0.0012374
8 | 0.97245 | -0.53036 | 0 | 0
9 | 0.97308 | -0.51801 | 0 | 0
10 | 0.97062 | -0.56662 | 0.045174 | 0.011322
11 | 0.97433 | -0.49329 | 0 | 0
12 | 0.97412 | -0.4974 | 0 | 0
13 | 0.97457 | -0.4885 | 0.0046603 | 0.001168
14 | 0.97458 | -0.48832 | 0.017368 | 0.0043529
15 | 0.97332 | -0.51326 | 0 | 0
16 | 0.97356 | -0.50847 | 0.017348 | 0.0043478
17 | 0.97257 | -0.52799 | 0 | 0
18 | 0.97036 | -0.5717 | 0 | 0
19 | 0.97225 | -0.53433 | 0.00025867 | 6.483e-05
20 | 0.97293 | -0.52092 | 0.0030768 | 0.00077112
21 | 0.9702 | -0.57489 | 0.00028569 | 7.16e-05
22 | 0.97293 | -0.52094 | 0 | 0
23 | 0.9729 | -0.52158 | 0.00078397 | 0.00019648
24 | 0.9726 | -0.52738 | 0.009541 | 0.0023912
25 | 0.99371 | -0.11867 | 0 | 0
26 | 0.98975 | -0.19403 | 0.00062695 | 0.00015713
27 | 0.99493 | -0.09548 | 0.0020662 | 0.00051784
28 | 0.97304 | -0.51866 | 0.0049851 | 0.0012494
29 | 0.97912 | -0.39956 | 0.063356 | 0.015879
30 | 0.98322 | -0.31968 | 0.0090966 | 0.0022798
31 | 0.97382 | -0.5034 | 0.0033044 | 0.00082816
32 | 0.97274 | -0.52466 | 0 | 0
33 | 0.97281 | -0.52329 | 0.0090106 | 0.0022583
34 | 0.97262 | -0.52709 | 0.0049417 | 0.0012385
35 | 0.9745 | -0.48992 | 0.0014132 | 0.00035418
36 | 0.97403 | -0.49914 | 0.016647 | 0.0041721
37 | 0.97401 | -0.49958 | 0.003075 | 0.00077066
38 | 0.97225 | -0.53435 | 0.00025868 | 6.4831e-05
39 | 0.97296 | -0.52037 | 0.003076 | 0.00077093
40 | 0.9702 | -0.57495 | 0.00049796 | 0.0001248
41 | 0.98937 | -0.20133 | 0.00063788 | 0.00015987
42 | 0.99494 | -0.095412 | 0.00064592 | 0.00016188
43 | 0.98485 | -0.28817 | 0 | 0
44 | 0.97019 | -0.57515 | 0.0023596 | 0.00059138
45 | 0.97019 | -0.57508 | 0.0028741 | 0.00072032
46 | 0.97194 | -0.54056 | 0.00026205 | 6.5675e-05
47 | 0.97193 | -0.54061 | 0.00026181 | 6.5616e-05
48 | 0.97193 | -0.54064 | 0.0030789 | 0.00077163
49 | 0.97187 | -0.54183 | 0.0087546 | 0.0021941
50 | 0.98594 | -0.26712 | 0.0065704 | 0.0016467
51 | 0.98616 | -0.26295 | 0 | 0
52 | 0.98828 | -0.2221 | 0 | 0
53 | 0.99682 | -0.059789 | 0.0020304 | 0.00050887
54 | 0.99798 | -0.038003 | 0.0019432 | 0.00048701
55 | 0.9968 | -0.060193 | 0.00097907 | 0.00024538
56 | 0.99801 | -0.037386 | 0.0022367 | 0.00056058
57 | 0.99639 | -0.067983 | 0.0016213 | 0.00040634
58 | 0.9984 | -0.029969 | 0.0020262 | 0.00050781
59 | 0.99565 | -0.08183 | 0 | 0
60 | 0.99842 | -0.029631 | 0.0019924 | 0.00049935
61 | 0.99536 | -0.087497 | 0 | 0
62 | 0.99558 | -0.083325 | 0.00067721 | 0.00016972
63 | 0.99962 | -0.0072163 | 0.0019738 | 0.00049469
64 | 0.99535 | -0.087796 | 0.00091728 | 0.00022989
65 | 0.99535 | -0.087717 | 0.00091711 | 0.00022985
66 | 0.99554 | -0.084093 | 0.00067955 | 0.00017031
67 | 0.99527 | -0.089248 | 0.00092673 | 0.00023226
68 | 0.99531 | -0.088543 | 0.00094275 | 0.00023628
69 | 0.99554 | -0.084115 | 0.00067163 | 0.00016833
70 | 0.99963 | -0.0068649 | 0.0019564 | 0.00049032
71 | 1 | 0 | -0.30604 | -0.078665
72 | 0.99525 | -0.089692 | 0.00063258 | 0.00015854
73 | 0.9953 | -0.088649 | 0.00096122 | 0.0002409
74 | 0.99545 | -0.085859 | 0.0006554 | 0.00016426
75 | 0.9952 | -0.090596 | 0.00064827 | 0.00016247
76 | 0.99519 | -0.090858 | 0.00062441 | 0.00015649
77 | 0.99516 | -0.091308 | 0.0006399 | 0.00016037
78 | 0.99516 | -0.09143 | 0.00063394 | 0.00015888
79 | 0.99544 | -0.085883 | 0.00071035 | 0.00017803
80 | 0.99542 | -0.086271 | 0.00069349 | 0.00017381
81 | 0.99542 | -0.086273 | 0.00062503 | 0.00015665
82 | 0.99539 | -0.086987 | 0.00065373 | 0.00016384
83 | 0.99538 | -0.087209 | 0.00096616 | 0.00024214
84 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0064299 | 0.0016115 | -0.0064291 | -0.0016113 | 8.2831e-07 | 2.4185e-07 | 0.009794 | 0.0097941 | 0.0097941 | 0.97692 | -0.44252 | 0.97678 | -0.44522 | 2.6907
1 | 0.0299 | 0.0075284 | -0.029835 | -0.0074877 | 6.5206e-05 | 4.0685e-05 | 0.045556 | 0.045557 | 0.045557 | 0.97692 | -0.44252 | 0.97459 | -0.48824 | 12.5156
2 | 0.14855 | 0.037439 | -0.14826 | -0.037262 | 0.00028377 | 0.000177 | 0.22634 | 0.22634 | 0.22634 | 0.97692 | -0.44252 | 0.97488 | -0.48253 | 12.4364
3 | -0.18488 | -0.046579 | 0.18552 | 0.04698 | 0.00063812 | 0.00040166 | 0.28169 | 0.28169 | 0.28169 | 0.97692 | -0.44252 | 0.9806 | -0.37062 | 15.4775
4 | 0.0014133 | 0.00035345 | -0.0014132 | -0.00035391 | 7.1201e-08 | -4.626e-07 | 0.0021576 | 0.0021578 | 0.0021578 | 0.97459 | -0.48824 | 0.97454 | -0.4893 | 0.5928
5 | 0.009501 | 0.0023817 | -0.0094985 | -0.0023806 | 2.4654e-06 | 1.1887e-06 | 0.014506 | 0.014507 | 0.014507 | 0.97459 | -0.48824 | 0.97431 | -0.49369 | 3.9853
6 | 0.018921 | 0.0047525 | -0.018893 | -0.0047358 | 2.7721e-05 | 1.664e-05 | 0.028893 | 0.028893 | 0.028893 | 0.97459 | -0.48824 | 0.97303 | -0.51899 | 7.9376
7 | 0.0079693 | 0.0019955 | -0.007967 | -0.0019946 | 2.2665e-06 | 9.4136e-07 | 0.012163 | 0.012164 | 0.012164 | 0.97488 | -0.48253 | 0.97457 | -0.4885 | 3.3416
8 | 0.14029 | 0.035266 | -0.14026 | -0.035242 | 3.8788e-05 | 2.4121e-05 | 0.21418 | 0.21418 | 0.21418 | 0.97488 | -0.48253 | 0.97458 | -0.48832 | 11.7681
9 | 0.063444 | 0.015934 | -0.063356 | -0.015879 | 8.7488e-05 | 5.5675e-05 | 0.096285 | 0.096285 | 0.096285 | 0.9806 | -0.37062 | 0.97912 | -0.39956 | 26.452
10 | -0.24896 | -0.062915 | 0.24957 | 0.063301 | 0.00060961 | 0.00038655 | 0.37797 | 0.37797 | 0.37797 | 0.9806 | -0.37062 | 0.98322 | -0.31968 | 20.7678
11 | 0.0014132 | 0.00035391 | -0.0014132 | -0.00035418 | 4.1681e-08 | -2.7074e-07 | 0.0021578 | 0.0021579 | 0.0021579 | 0.97454 | -0.4893 | 0.9745 | -0.48992 | 0.59283
12 | 0.013956 | 0.0034985 | -0.013953 | -0.0034968 | 2.8605e-06 | 1.6228e-06 | 0.021343 | 0.021343 | 0.021343 | 0.97303 | -0.51899 | 0.97281 | -0.52329 | 5.8634
13 | -0.045252 | -0.011369 | 0.045278 | 0.011382 | 2.6686e-05 | 1.2474e-05 | 0.069253 | 0.069252 | 0.069253 | 0.97245 | -0.53036 | 0.97308 | -0.51801 | 3.8051
14 | 0.045252 | 0.011369 | -0.045174 | -0.011322 | 7.8188e-05 | 4.7887e-05 | 0.069253 | 0.069254 | 0.069254 | 0.97245 | -0.53036 | 0.97062 | -0.56662 | 9.5129
15 | 0.030062 | 0.0075374 | -0.030061 | -0.0075372 | 9.2899e-07 | 2.3052e-07 | 0.045971 | 0.045971 | 0.045971 | 0.97308 | -0.51801 | 0.97304 | -0.51866 | 2.5259
16 | -0.085669 | -0.021509 | 0.085689 | 0.02152 | 1.9407e-05 | 1.1484e-05 | 0.13102 | 0.13102 | 0.13102 | 0.97308 | -0.51801 | 0.97332 | -0.51326 | 7.1988
17 | 0.010329 | 0.0025893 | -0.010328 | -0.0025886 | 1.4453e-06 | 7.3313e-07 | 0.015796 | 0.015796 | 0.015796 | 0.97308 | -0.51801 | 0.97293 | -0.52094 | 4.3395
18 | 0.003306 | 0.00082711 | -0.0033053 | -0.00082754 | 6.4663e-07 | -4.2855e-07 | 0.0050484 | 0.0050487 | 0.0050487 | 0.97433 | -0.49329 | 0.97412 | -0.4974 | 1.387
19 | -0.003306 | -0.00082711 | 0.0033067 | 0.00082661 | 7.5368e-07 | -5.0008e-07 | 0.0050484 | 0.0050481 | 0.0050484 | 0.97433 | -0.49329 | 0.97457 | -0.4885 | 1.3869
20 | 0.0033053 | 0.00082754 | -0.0033044 | -0.00082816 | 9.4356e-07 | -6.2452e-07 | 0.0050487 | 0.0050492 | 0.0050492 | 0.97412 | -0.4974 | 0.97382 | -0.5034 | 1.3871
21 | 0.12289 | 0.030889 | -0.12282 | -0.03085 | 6.3489e-05 | 3.9136e-05 | 0.18766 | 0.18766 | 0.18766 | 0.97458 | -0.48832 | 0.97403 | -0.49914 | 10.311
22 | -0.085689 | -0.02152 | 0.085708 | 0.021532 | 1.9594e-05 | 1.1594e-05 | 0.13102 | 0.13102 | 0.13102 | 0.97332 | -0.51326 | 0.97356 | -0.50847 | 7.1988
23 | -0.10306 | -0.02588 | 0.1031 | 0.025906 | 4.3711e-05 | 2.6514e-05 | 0.15753 | 0.15753 | 0.15753 | 0.97356 | -0.50847 | 0.97401 | -0.49958 | 8.6556
24 | 0.0060309 | 0.0015115 | -0.0060184 | -0.0015083 | 1.2544e-05 | 3.1646e-06 | 0.0092272 | 0.0092289 | 0.0092289 | 0.97257 | -0.52799 | 0.97036 | -0.5717 | 2.5354
25 | 0.012883 | 0.0032311 | -0.012879 | -0.003229 | 3.8884e-06 | 2.1575e-06 | 0.019711 | 0.019711 | 0.019711 | 0.97257 | -0.52799 | 0.97225 | -0.53433 | 5.4152
26 | -0.018914 | -0.0047426 | 0.01892 | 0.0047457 | 6.38e-06 | 3.0744e-06 | 0.028938 | 0.028938 | 0.028938 | 0.97257 | -0.52799 | 0.97293 | -0.52092 | 3.9751
27 | 0.0060184 | 0.0015083 | -0.0060174 | -0.0015081 | 9.1637e-07 | 2.3212e-07 | 0.0092289 | 0.009229 | 0.009229 | 0.97036 | -0.5717 | 0.9702 | -0.57489 | 2.5355
28 | 0.01262 | 0.0031641 | -0.01262 | -0.0031641 | 1.6311e-08 | 8.9932e-09 | 0.019316 | 0.019316 | 0.019316 | 0.97225 | -0.53433 | 0.97225 | -0.53435 | 5.3065
29 | -0.021997 | -0.0055168 | 0.021997 | 0.0055168 | 5.7207e-07 | -5.2316e-08 | 0.033644 | 0.033644 | 0.033644 | 0.97293 | -0.52092 | 0.97296 | -0.52037 | 1.8486
30 | 0.0057317 | 0.0014365 | -0.0057317 | -0.0014365 | 1.5199e-08 | 3.2508e-09 | 0.0087909 | 0.0087909 | 0.0087909 | 0.9702 | -0.57489 | 0.9702 | -0.57495 | 2.4151
31 | 0.00078399 | 0.00019595 | -0.00078397 | -0.00019648 | 2.3775e-08 | -5.3247e-07 | 0.0011989 | 0.0011991 | 0.0011991 | 0.97293 | -0.52094 | 0.9729 | -0.52158 | 0.32941
32 | 0.0095439 | 0.0023926 | -0.009541 | -0.0023912 | 2.9238e-06 | 1.417e-06 | 0.014597 | 0.014597 | 0.014597 | 0.97293 | -0.52094 | 0.9726 | -0.52738 | 4.0102
33 | 0.26908 | 0.06918 | -0.2681 | -0.068557 | 0.00098155 | 0.000623 | 0.40355 | 0.40355 | 0.40355 | 0.99371 | -0.11867 | 0.98975 | -0.19403 | 22.1733
34 | -0.26908 | -0.06918 | 0.26938 | 0.069373 | 0.00030359 | 0.00019269 | 0.40355 | 0.40355 | 0.40355 | 0.99371 | -0.11867 | 0.99493 | -0.09548 | 22.1732
35 | 0.26747 | 0.0684 | -0.26738 | -0.06834 | 9.4399e-05 | 5.9917e-05 | 0.40261 | 0.40261 | 0.40261 | 0.98975 | -0.19403 | 0.98937 | -0.20133 | 22.1215
36 | -0.27145 | -0.06989 | 0.27145 | 0.069891 | 9.0585e-07 | 5.7501e-07 | 0.40664 | 0.40664 | 0.40664 | 0.99493 | -0.09548 | 0.99494 | -0.095412 | 22.3429
37 | 0.025076 | 0.0062878 | -0.025073 | -0.0062877 | 2.0489e-06 | 1.5762e-07 | 0.038348 | 0.038348 | 0.038348 | 0.97304 | -0.51866 | 0.97296 | -0.52037 | 2.107
38 | -0.25867 | -0.065581 | 0.25906 | 0.06583 | 0.0003924 | 0.00024897 | 0.39174 | 0.39174 | 0.39174 | 0.98322 | -0.31968 | 0.98485 | -0.28817 | 21.5241
39 | -0.0049423 | -0.0012385 | 0.0049426 | 0.0012386 | 3.231e-07 | 1.964e-08 | 0.0075602 | 0.0075602 | 0.0075602 | 0.97274 | -0.52466 | 0.97281 | -0.52329 | 2.077
40 | 0.0049423 | 0.0012385 | -0.0049417 | -0.0012385 | 5.7263e-07 | 3.4882e-08 | 0.0075602 | 0.0075604 | 0.0075604 | 0.97274 | -0.52466 | 0.97262 | -0.52709 | 2.077
41 | 0.10618 | 0.026678 | -0.10618 | -0.026677 | 2.2201e-06 | 1.3509e-06 | 0.16223 | 0.16223 | 0.16223 | 0.97403 | -0.49914 | 0.97401 | -0.49958 | 8.9137
42 | 0.012362 | 0.0030993 | -0.012358 | -0.0030973 | 3.658e-06 | 2.0033e-06 | 0.01892 | 0.01892 | 0.01892 | 0.97225 | -0.53435 | 0.97194 | -0.54056 | 5.1977
43 | 0.0052338 | 0.0013117 | -0.0052337 | -0.0013117 | 3.1261e-08 | 4.0308e-09 | 0.0080272 | 0.0080272 | 0.0080272 | 0.9702 | -0.57495 | 0.97019 | -0.57508 | 2.2053
44 | 0.26674 | 0.06818 | -0.26647 | -0.06801 | 0.00026776 | 0.00016995 | 0.40165 | 0.40165 | 0.40165 | 0.98937 | -0.20133 | 0.98828 | -0.2221 | 22.0688
45 | -0.2721 | -0.070053 | 0.27228 | 0.070167 | 0.00017991 | 0.00011421 | 0.40761 | 0.40761 | 0.40761 | 0.99494 | -0.095412 | 0.99565 | -0.08183 | 22.396
46 | -0.25906 | -0.06583 | 0.25937 | 0.06603 | 0.00031507 | 0.0001999 | 0.39174 | 0.39174 | 0.39174 | 0.98485 | -0.28817 | 0.98616 | -0.26295 | 21.5241
47 | -0.0023596 | -0.00059138 | 0.0023596 | 0.00059136 | 8.169e-09 | -1.5311e-08 | 0.003619 | 0.003619 | 0.003619 | 0.97019 | -0.57515 | 0.97019 | -0.57508 | 0.99424
48 | 0.012096 | 0.0030316 | -0.012096 | -0.0030316 | 2.3739e-08 | 1.2905e-08 | 0.018519 | 0.018519 | 0.018519 | 0.97194 | -0.54056 | 0.97193 | -0.54061 | 5.0875
49 | 0.011834 | 0.002966 | -0.011834 | -0.002966 | 2.1269e-08 | 1.1471e-08 | 0.018118 | 0.018118 | 0.018118 | 0.97193 | -0.54061 | 0.97193 | -0.54064 | 4.9774
50 | 0.0087551 | 0.0021943 | -0.0087546 | -0.0021941 | 4.9516e-07 | 2.2583e-07 | 0.013404 | 0.013404 | 0.013404 | 0.97193 | -0.54064 | 0.97187 | -0.54183 | 3.6824
51 | -0.0065704 | -0.0016467 | 0.0065718 | 0.0016471 | 1.3057e-06 | 3.8396e-07 | 0.0099163 | 0.0099162 | 0.0099163 | 0.98594 | -0.26712 | 0.98616 | -0.26295 | 2.7243
52 | -0.26595 | -0.067677 | 0.26647 | 0.06801 | 0.0005247 | 0.00033304 | 0.40165 | 0.40165 | 0.40165 | 0.98616 | -0.26295 | 0.98828 | -0.2221 | 22.0689
53 | -0.29139 | -0.075076 | 0.2917 | 0.075272 | 0.00030937 | 0.00019658 | 0.43571 | 0.43571 | 0.43571 | 0.99682 | -0.059789 | 0.99798 | -0.038003 | 23.9402
54 | 0.28936 | 0.074567 | -0.28936 | -0.074563 | 5.6814e-06 | 3.6097e-06 | 0.43268 | 0.43268 | 0.43268 | 0.99682 | -0.059789 | 0.9968 | -0.060193 | 23.7737
55 | -0.29365 | -0.075759 | 0.29366 | 0.075765 | 8.832e-06 | 5.6125e-06 | 0.43861 | 0.43861 | 0.43861 | 0.99798 | -0.038003 | 0.99801 | -0.037386 | 24.0994
56 | 0.28838 | 0.074318 | -0.28827 | -0.074248 | 0.00010934 | 6.9465e-05 | 0.43122 | 0.43122 | 0.43122 | 0.9968 | -0.060193 | 0.99639 | -0.067983 | 23.6934
57 | -0.29589 | -0.076325 | 0.296 | 0.076393 | 0.00010697 | 6.7985e-05 | 0.44194 | 0.44194 | 0.44194 | 0.99801 | -0.037386 | 0.9984 | -0.029969 | 24.2826
58 | 0.28665 | 0.073842 | -0.28646 | -0.073719 | 0.00019304 | 0.00012263 | 0.4288 | 0.4288 | 0.4288 | 0.99639 | -0.067983 | 0.99565 | -0.08183 | 23.5604
59 | -0.29803 | -0.076901 | 0.29803 | 0.076904 | 4.9145e-06 | 3.1237e-06 | 0.44496 | 0.44496 | 0.44496 | 0.9984 | -0.029969 | 0.99842 | -0.029631 | 24.4485
60 | 0.007847 | 0.0019656 | -0.0078449 | -0.0019648 | 2.1175e-06 | 8.2135e-07 | 0.011727 | 0.011727 | 0.011727 | 0.99565 | -0.08183 | 0.99536 | -0.087497 | 3.2218
61 | 0.0063337 | 0.0015866 | -0.0063332 | -0.0015865 | 4.5113e-07 | 1.1411e-07 | 0.0094655 | 0.0094656 | 0.0094656 | 0.99565 | -0.08183 | 0.99558 | -0.083325 | 2.6004
62 | -0.30002 | -0.077404 | 0.30035 | 0.077612 | 0.00032809 | 0.00020855 | 0.44793 | 0.44793 | 0.44793 | 0.99842 | -0.029631 | 0.99962 | -0.0072163 | 24.6117
63 | 0.0050237 | 0.0012581 | -0.0050236 | -0.0012581 | 7.1463e-08 | 1.8174e-09 | 0.0075098 | 0.0075099 | 0.0075099 | 0.99536 | -0.087497 | 0.99535 | -0.087796 | 2.0631
64 | 0.0028212 | 0.00070664 | -0.0028212 | -0.00070668 | 2.9457e-08 | -3.8551e-08 | 0.0042174 | 0.0042174 | 0.0042174 | 0.99536 | -0.087497 | 0.99535 | -0.087717 | 1.1586
65 | 0.005656 | 0.0014168 | -0.0056558 | -0.0014168 | 2.0688e-07 | 3.202e-08 | 0.0084534 | 0.0084534 | 0.0084534 | 0.99558 | -0.083325 | 0.99554 | -0.084093 | 2.3224
66 | -0.30233 | -0.078107 | 0.30233 | 0.07811 | 5.1821e-06 | 3.2942e-06 | 0.45087 | 0.45087 | 0.45087 | 0.99962 | -0.0072163 | 0.99963 | -0.0068649 | 24.7731
67 | 0.0041063 | 0.0010282 | -0.0041061 | -0.0010283 | 2.8376e-07 | -7.9374e-08 | 0.0061385 | 0.0061386 | 0.0061386 | 0.99535 | -0.087796 | 0.99527 | -0.089248 | 1.6864
68 | 0.0019041 | 0.00047683 | -0.001904 | -0.0004771 | 7.4964e-08 | -2.727e-07 | 0.0028464 | 0.0028465 | 0.0028465 | 0.99535 | -0.087717 | 0.99531 | -0.088543 | 0.782
69 | 0.0049763 | 0.0012465 | -0.0049763 | -0.0012465 | 5.0877e-09 | 6.7272e-11 | 0.0074377 | 0.0074377 | 0.0074377 | 0.99554 | -0.084093 | 0.99554 | -0.084115 | 2.0433
70 | 0.0031793 | 0.00079604 | -0.0031793 | -0.0007961 | 6.7199e-08 | -6.0068e-08 | 0.0047531 | 0.0047531 | 0.0047531 | 0.99527 | -0.089248 | 0.99525 | -0.089692 | 1.3058
71 | 0.00096122 | 0.00024083 | -0.00096122 | -0.0002409 | 4.8127e-09 | -7.7688e-08 | 0.001437 | 0.0014371 | 0.0014371 | 0.99531 | -0.088543 | 0.9953 | -0.088649 | 0.3948
72 | 0.0043046 | 0.0010781 | -0.0043043 | -0.0010782 | 3.575e-07 | -7.0621e-08 | 0.0064338 | 0.006434 | 0.006434 | 0.99554 | -0.084115 | 0.99545 | -0.085859 | 1.7676
73 | -0.30429 | -0.078601 | 0.30439 | 0.078665 | 0.00010193 | 6.4802e-05 | 0.45378 | 0.45378 | 0.45378 | 0.99963 | -0.0068649 | 1 | 0 | 24.9331
74 | 0.0025467 | 0.00063756 | -0.0025466 | -0.00063775 | 1.0963e-07 | -1.9189e-07 | 0.0038074 | 0.0038075 | 0.0038075 | 0.99525 | -0.089692 | 0.9952 | -0.090596 | 1.046
75 | 0.0036489 | 0.00091395 | -0.0036489 | -0.00091395 | 4.2123e-09 | -2.2127e-09 | 0.0054543 | 0.0054543 | 0.0054543 | 0.99545 | -0.085859 | 0.99544 | -0.085883 | 1.4984
76 | 0.0018983 | 0.00047528 | -0.0018983 | -0.00047537 | 2.3675e-08 | -8.6686e-08 | 0.0028382 | 0.0028382 | 0.0028382 | 0.9952 | -0.090596 | 0.99519 | -0.090858 | 0.77973
77 | 0.0012739 | 0.00031887 | -0.0012738 | -0.00031912 | 2.7273e-08 | -2.4304e-07 | 0.0019046 | 0.0019047 | 0.0019047 | 0.99519 | -0.090858 | 0.99516 | -0.091308 | 0.52326
78 | 0.00063395 | 0.00015874 | -0.00063394 | -0.00015888 | 3.68e-09 | -1.3955e-07 | 0.00094786 | 0.00094791 | 0.00094791 | 0.99516 | -0.091308 | 0.99516 | -0.09143 | 0.26041
79 | 0.0029385 | 0.00073592 | -0.0029385 | -0.00073598 | 5.4262e-08 | -6.277e-08 | 0.0043924 | 0.0043924 | 0.0043924 | 0.99544 | -0.085883 | 0.99542 | -0.086271 | 1.2067
80 | 0.002245 | 0.00056218 | -0.002245 | -0.00056218 | 1.7296e-10 | -4.2113e-10 | 0.0033558 | 0.0033558 | 0.0033558 | 0.99542 | -0.086271 | 0.99542 | -0.086273 | 0.92191
81 | 0.00162 | 0.00040553 | -0.0016199 | -0.00040582 | 5.5105e-08 | -2.905e-07 | 0.0024214 | 0.0024215 | 0.0024215 | 0.99542 | -0.086273 | 0.99539 | -0.086987 | 0.66526
82 | 0.00096617 | 0.00024198 | -0.00096616 | -0.00024214 | 1.0184e-08 | -1.627e-07 | 0.0014443 | 0.0014443 | 0.0014443 | 0.99539 | -0.086987 | 0.99538 | -0.087209 | 0.3968

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.31002 | 0.079663

## res_load
| p_mw | q_mvar
0 | 0.0064291 | 0.0016113
1 | 0.0094985 | 0.0023806
2 | 0.0049372 | 0.0012374
3 | 0.045174 | 0.011322
4 | 0.0046603 | 0.001168
5 | 0.017368 | 0.0043529
6 | 0.017348 | 0.0043478
7 | 0.00025867 | 6.483e-05
8 | 0.0030768 | 0.00077112
9 | 0.00028569 | 7.16e-05
10 | 0.00078397 | 0.00019648
11 | 0.009541 | 0.0023912
12 | 0.00062695 | 0.00015713
13 | 0.0020662 | 0.00051784
14 | 0.0049851 | 0.0012494
15 | 0.063356 | 0.015879
16 | 0.0090966 | 0.0022798
17 | 0.0033044 | 0.00082816
18 | 0.0090106 | 0.0022583
19 | 0.0049417 | 0.0012385
20 | 0.0014132 | 0.00035418
21 | 0.016647 | 0.0041721
22 | 0.003075 | 0.00077066
23 | 0.00025868 | 6.4831e-05
24 | 0.003076 | 0.00077093
25 | 0.00049796 | 0.0001248
26 | 0.00063788 | 0.00015987
27 | 0.00064592 | 0.00016188
28 | 0.0023596 | 0.00059138
29 | 0.0028741 | 0.00072032
30 | 0.00026205 | 6.5675e-05
31 | 0.00026181 | 6.5616e-05
32 | 0.0030789 | 0.00077163
33 | 0.0087546 | 0.0021941
34 | 0.0065704 | 0.0016467
35 | 0.0020304 | 0.00050887
36 | 0.0019432 | 0.00048701
37 | 0.00097907 | 0.00024538
38 | 0.0022367 | 0.00056058
39 | 0.0016213 | 0.00040634
40 | 0.0020262 | 0.00050781
41 | 0.0019924 | 0.00049935
42 | 0.00067721 | 0.00016972
43 | 0.0019738 | 0.00049469
44 | 0.00091728 | 0.00022989
45 | 0.00091711 | 0.00022985
46 | 0.00067955 | 0.00017031
47 | 0.00092673 | 0.00023226
48 | 0.00094275 | 0.00023628
49 | 0.00067163 | 0.00016833
50 | 0.0019564 | 0.00049032
51 | 0.003981 | 0.00099773
52 | 0.00063258 | 0.00015854
53 | 0.00096122 | 0.0002409
54 | 0.0006554 | 0.00016426
55 | 0.00064827 | 0.00016247
56 | 0.00062441 | 0.00015649
57 | 0.0006399 | 0.00016037
58 | 0.00063394 | 0.00015888
59 | 0.00071035 | 0.00017803
60 | 0.00069349 | 0.00017381
61 | 0.00062503 | 0.00015665
62 | 0.00065373 | 0.00016384
63 | 0.00096616 | 0.00024214

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1