## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-117_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-117_0_6_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_261-117_0_6_node_14 | 0.4 | n |  | TRUE
3 | bus_LV_261-117_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-117_0_6_node_16 | 0.4 | n |  | TRUE
5 | bus_LV_261-117_0_6_node_22 | 0.4 | n |  | TRUE
6 | bus_LV_261-117_0_6_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_261-117_0_6_node_12 | 0.4 | n |  | TRUE
8 | bus_LV_261-117_0_6_node_29 | 0.4 | n |  | TRUE
9 | bus_LV_261-117_0_6_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_261-117_0_6_node_94 | 0.4 | n |  | TRUE
11 | bus_LV_261-117_0_6_node_95 | 0.4 | n |  | TRUE
12 | bus_LV_261-117_0_6_node_93 | 0.4 | n |  | TRUE
13 | bus_LV_261-117_0_6_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_261-117_0_6_node_27 | 0.4 | n |  | TRUE
15 | bus_LV_261-117_0_6_node_25 | 0.4 | n |  | TRUE
16 | bus_LV_261-117_0_6_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_261-117_0_6_node_24 | 0.4 | n |  | TRUE
18 | bus_LV_261-117_0_6_node_23 | 0.4 | n |  | TRUE
19 | bus_LV_261-117_0_6_node_8 | 0.4 | n |  | TRUE
20 | bus_LV_261-117_0_6_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_261-117_0_6_node_9 | 0.4 | n |  | TRUE
22 | bus_LV_261-117_0_6_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_261-117_0_6_node_10 | 0.4 | n |  | TRUE
24 | bus_LV_261-117_0_6_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_261-117_0_6_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_261-117_0_6_node_11 | 0.4 | n |  | TRUE
27 | bus_LV_261-117_0_6_node_28 | 0.4 | n |  | TRUE
28 | bus_LV_261-117_0_6_node_101 | 0.4 | n |  | TRUE
29 | bus_LV_261-117_0_6_node_108 | 0.4 | n |  | TRUE
30 | bus_LV_261-117_0_6_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_261-117_0_6_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_261-117_0_6_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_261-117_0_6_node_78 | 0.4 | n |  | TRUE
34 | bus_LV_261-117_0_6_node_68 | 0.4 | n |  | TRUE
35 | bus_LV_261-117_0_6_node_70 | 0.4 | n |  | TRUE
36 | bus_LV_261-117_0_6_node_66 | 0.4 | n |  | TRUE
37 | bus_LV_261-117_0_6_node_79 | 0.4 | n |  | TRUE
38 | bus_LV_261-117_0_6_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_261-117_0_6_node_31 | 0.4 | n |  | TRUE
40 | bus_LV_261-117_0_6_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_261-117_0_6_node_33 | 0.4 | n |  | TRUE
42 | bus_LV_261-117_0_6_node_38 | 0.4 | n |  | TRUE
43 | bus_LV_261-117_0_6_node_41 | 0.4 | n |  | TRUE
44 | bus_LV_261-117_0_6_node_40 | 0.4 | n |  | TRUE
45 | bus_LV_261-117_0_6_node_34 | 0.4 | n |  | TRUE
46 | bus_LV_261-117_0_6_node_46 | 0.4 | n |  | TRUE
47 | bus_LV_261-117_0_6_node_56 | 0.4 | n |  | TRUE
48 | bus_LV_261-117_0_6_node_36 | 0.4 | n |  | TRUE
49 | bus_LV_261-117_0_6_node_37 | 0.4 | n |  | TRUE
50 | bus_LV_261-117_0_6_node_145 | 0.4 | n |  | TRUE
51 | bus_LV_261-117_0_6_node_54 | 0.4 | n |  | TRUE
52 | bus_LV_261-117_0_6_node_42 | 0.4 | n |  | TRUE
53 | bus_LV_261-117_0_6_node_43 | 0.4 | n |  | TRUE
54 | bus_LV_261-117_0_6_node_60 | 0.4 | n |  | TRUE
55 | bus_LV_261-117_0_6_node_65 | 0.4 | n |  | TRUE
56 | bus_LV_261-117_0_6_node_58 | 0.4 | n |  | TRUE
57 | bus_LV_261-117_0_6_node_57 | 0.4 | n |  | TRUE
58 | bus_LV_261-117_0_6_node_126 | 0.4 | n |  | TRUE
59 | bus_LV_261-117_0_6_node_47 | 0.4 | n |  | TRUE
60 | bus_LV_261-117_0_6_node_50 | 0.4 | n |  | TRUE
61 | bus_LV_261-117_0_6_node_48 | 0.4 | n |  | TRUE
62 | bus_LV_261-117_0_6_node_71 | 0.4 | n |  | TRUE
63 | bus_LV_261-117_0_6_node_76 | 0.4 | n |  | TRUE
64 | bus_LV_261-117_0_6_node_74 | 0.4 | n |  | TRUE
65 | bus_LV_261-117_0_6_node_151 | 0.4 | n |  | TRUE
66 | bus_LV_261-117_0_6_node_73 | 0.4 | n |  | TRUE
67 | bus_LV_261-117_0_6_node_90 | 0.4 | n |  | TRUE
68 | bus_LV_261-117_0_6_node_115 | 0.4 | n |  | TRUE
69 | bus_LV_261-117_0_6_node_124 | 0.4 | n |  | TRUE
70 | bus_LV_261-117_0_6_node_133 | 0.4 | n |  | TRUE
71 | bus_LV_261-117_0_6_node_77 | 0.4 | n |  | TRUE
72 | bus_LV_261-117_0_6_node_106 | 0.4 | n |  | TRUE
73 | bus_LV_261-117_0_6_node_107 | 0.4 | n |  | TRUE
74 | bus_LV_261-117_0_6_node_142 | 0.4 | n |  | TRUE
75 | bus_LV_261-117_0_6_node_143 | 0.4 | n |  | TRUE
76 | bus_LV_261-117_0_6_node_140 | 0.4 | n |  | TRUE
77 | bus_LV_261-117_0_6_node_52 | 0.4 | n |  | TRUE
78 | bus_LV_261-117_0_6_node_59 | 0.4 | n |  | TRUE
79 | bus_LV_261-117_0_6_node_64 | 0.4 | n |  | TRUE
80 | bus_LV_261-117_0_6_node_149 | 0.4 | n |  | TRUE
81 | bus_LV_261-117_0_6_node_88 | 0.4 | n |  | TRUE
82 | bus_LV_261-117_0_6_node_61 | 0.4 | n |  | TRUE
83 | bus_LV_261-117_0_6_node_62 | 0.4 | n |  | TRUE
84 | bus_LV_261-117_0_6_node_112 | 0.4 | n |  | TRUE
85 | bus_LV_261-117_0_6_node_113 | 0.4 | n |  | TRUE
86 | bus_LV_261-117_0_6_node_49 | 0.4 | n |  | TRUE
87 | bus_LV_261-117_0_6_node_146 | 0.4 | n |  | TRUE
88 | bus_LV_261-117_0_6_node_51 | 0.4 | n |  | TRUE
89 | bus_LV_261-117_0_6_node_53 | 0.4 | n |  | TRUE
90 | bus_LV_261-117_0_6_node_55 | 0.4 | n |  | TRUE
91 | bus_LV_261-117_0_6_node_86 | 0.4 | n |  | TRUE
92 | bus_LV_261-117_0_6_node_63 | 0.4 | n |  | TRUE
93 | bus_LV_261-117_0_6_node_67 | 0.4 | n |  | TRUE
94 | bus_LV_261-117_0_6_node_69 | 0.4 | n |  | TRUE
95 | bus_LV_261-117_0_6_node_102 | 0.4 | n |  | TRUE
96 | bus_LV_261-117_0_6_node_103 | 0.4 | n |  | TRUE
97 | bus_LV_261-117_0_6_node_109 | 0.4 | n |  | TRUE
98 | bus_LV_261-117_0_6_node_132 | 0.4 | n |  | TRUE
99 | bus_LV_261-117_0_6_node_131 | 0.4 | n |  | TRUE
100 | bus_LV_261-117_0_6_node_150 | 0.4 | n |  | TRUE
101 | bus_LV_261-117_0_6_node_141 | 0.4 | n |  | TRUE
102 | bus_LV_261-117_0_6_node_87 | 0.4 | n |  | TRUE
103 | bus_LV_261-117_0_6_node_110 | 0.4 | n |  | TRUE
104 | bus_LV_261-117_0_6_node_122 | 0.4 | n |  | TRUE
105 | bus_LV_261-117_0_6_node_134 | 0.4 | n |  | TRUE
106 | bus_LV_261-117_0_6_node_138 | 0.4 | n |  | TRUE
107 | bus_LV_261-117_0_6_node_135 | 0.4 | n |  | TRUE
108 | bus_LV_261-117_0_6_node_105 | 0.4 | n |  | TRUE
109 | bus_LV_261-117_0_6_node_80 | 0.4 | n |  | TRUE
110 | bus_LV_261-117_0_6_node_81 | 0.4 | n |  | TRUE
111 | bus_LV_261-117_0_6_node_82 | 0.4 | n |  | TRUE
112 | bus_LV_261-117_0_6_node_83 | 0.4 | n |  | TRUE
113 | bus_LV_261-117_0_6_node_84 | 0.4 | n |  | TRUE
114 | bus_LV_261-117_0_6_node_96 | 0.4 | n |  | TRUE
115 | bus_LV_261-117_0_6_node_97 | 0.4 | n |  | TRUE
116 | bus_LV_261-117_0_6_node_85 | 0.4 | n |  | TRUE
117 | bus_LV_261-117_0_6_node_89 | 0.4 | n |  | TRUE
118 | bus_LV_261-117_0_6_node_91 | 0.4 | n |  | TRUE
119 | bus_LV_261-117_0_6_node_92 | 0.4 | n |  | TRUE
120 | bus_LV_261-117_0_6_node_139 | 0.4 | n |  | TRUE
121 | bus_LV_261-117_0_6_node_111 | 0.4 | n |  | TRUE
122 | bus_LV_261-117_0_6_node_116 | 0.4 | n |  | TRUE
123 | bus_LV_261-117_0_6_node_100 | 0.4 | n |  | TRUE
124 | bus_LV_261-117_0_6_node_98 | 0.4 | n |  | TRUE
125 | bus_LV_261-117_0_6_node_99 | 0.4 | n |  | TRUE
126 | bus_LV_261-117_0_6_node_104 | 0.4 | n |  | TRUE
127 | bus_LV_261-117_0_6_node_130 | 0.4 | n |  | TRUE
128 | bus_LV_261-117_0_6_node_114 | 0.4 | n |  | TRUE
129 | bus_LV_261-117_0_6_node_119 | 0.4 | n |  | TRUE
130 | bus_LV_261-117_0_6_node_117 | 0.4 | n |  | TRUE
131 | bus_LV_261-117_0_6_node_118 | 0.4 | n |  | TRUE
132 | bus_LV_261-117_0_6_node_120 | 0.4 | n |  | TRUE
133 | bus_LV_261-117_0_6_node_123 | 0.4 | n |  | TRUE
134 | bus_LV_261-117_0_6_node_125 | 0.4 | n |  | TRUE
135 | bus_LV_261-117_0_6_node_121 | 0.4 | n |  | TRUE
136 | bus_LV_261-117_0_6_node_129 | 0.4 | n |  | TRUE
137 | bus_LV_261-117_0_6_node_127 | 0.4 | n |  | TRUE
138 | bus_LV_261-117_0_6_node_128 | 0.4 | n |  | TRUE
139 | bus_LV_261-117_0_6_node_136 | 0.4 | n |  | TRUE
140 | bus_MV_524_0_node_26 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-117_0_6_load_0 | 0 | 0.0035906 | 0.00089988 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-117_0_6_load_14 | 2 | 0.0049976 | 0.0012525 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-117_0_6_load_16 | 4 | 0.0038629 | 0.00096813 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-117_0_6_load_22 | 5 | 0.0037296 | 0.00093473 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-117_0_6_load_29 | 8 | 0.0022164 | 0.00055548 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-117_0_6_load_95 | 11 | 0.0030382 | 0.00076144 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-117_0_6_load_93 | 12 | 0.0038979 | 0.0009769 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-117_0_6_load_27 | 14 | 0.0016163 | 0.00040509 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-117_0_6_load_25 | 15 | 0.0038762 | 0.00097147 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-117_0_6_load_24 | 17 | 0.0084367 | 0.0021144 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-117_0_6_load_23 | 18 | 0.0055411 | 0.0013887 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-117_0_6_load_15 | 22 | 0.0034246 | 0.00085828 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-117_0_6_load_17 | 25 | 0.0059301 | 0.0014862 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-117_0_6_load_28 | 27 | 0.0038705 | 0.00097005 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-117_0_6_load_101 | 28 | 0.00098439 | 0.00024671 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-117_0_6_load_108 | 29 | 0.0055965 | 0.0014026 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-117_0_6_load_20 | 32 | 0.0043702 | 0.0010953 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-117_0_6_load_78 | 33 | 0.002436 | 0.00061051 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-117_0_6_load_70 | 35 | 0.0048783 | 0.0012226 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-117_0_6_load_66 | 36 | 0.0050212 | 0.0012584 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-117_0_6_load_79 | 37 | 0.0018407 | 0.00046132 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-117_0_6_load_30 | 38 | 0.0041544 | 0.0010412 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-117_0_6_load_41 | 43 | 0.01487 | 0.0037268 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-117_0_6_load_40 | 44 | 0.0085259 | 0.0021368 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-117_0_6_load_56 | 47 | 0.0040855 | 0.0010239 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-117_0_6_load_145 | 50 | 0.0052895 | 0.0013257 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-117_0_6_load_54 | 51 | 0.0012209 | 0.00030599 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-117_0_6_load_60 | 54 | 0.0033668 | 0.00084379 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-117_0_6_load_65 | 55 | 0.0039455 | 0.00098885 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-117_0_6_load_57 | 57 | 0.0059133 | 0.001482 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-117_0_6_load_126 | 58 | 0.0039116 | 0.00098034 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-117_0_6_load_48 | 61 | 0.0023383 | 0.00058602 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-117_0_6_load_151 | 65 | 0.0087456 | 0.0021919 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-117_0_6_load_115 | 68 | 0.012451 | 0.0031205 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-117_0_6_load_124 | 69 | 0.0054443 | 0.0013645 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-117_0_6_load_133 | 70 | 0.0032827 | 0.00082271 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-117_0_6_load_106 | 72 | 0.0060421 | 0.0015143 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-117_0_6_load_107 | 73 | 0.0045054 | 0.0011292 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-117_0_6_load_143 | 75 | 0.015745 | 0.0039462 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-117_0_6_load_140 | 76 | 0.026268 | 0.0065835 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-117_0_6_load_52 | 77 | 0.0026884 | 0.00067378 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-117_0_6_load_59 | 78 | 0.0031151 | 0.00078072 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-117_0_6_load_64 | 79 | 0.003071 | 0.00076966 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-117_0_6_load_149 | 80 | 0.0025441 | 0.00063762 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-117_0_6_load_88 | 81 | 0.0025103 | 0.00062914 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-117_0_6_load_61 | 82 | 0.0031501 | 0.00078949 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-117_0_6_load_62 | 83 | 0.0031078 | 0.00077888 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-117_0_6_load_112 | 84 | 0.0044512 | 0.0011156 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-117_0_6_load_113 | 85 | 0.0018618 | 0.0004666 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-117_0_6_load_49 | 86 | 0.0011502 | 0.00028826 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-117_0_6_load_146 | 87 | 0.0018972 | 0.00047548 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-117_0_6_load_51 | 88 | 0.0026901 | 0.00067419 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-117_0_6_load_53 | 89 | 0.0026371 | 0.00066092 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-117_0_6_load_55 | 90 | 0.0026701 | 0.00066918 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-117_0_6_load_86 | 91 | 0.0045085 | 0.0011299 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-117_0_6_load_63 | 92 | 0.003404 | 0.00085312 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-117_0_6_load_67 | 93 | 0.031209 | 0.0078216 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-117_0_6_load_69 | 94 | 0.0057803 | 0.0014487 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-117_0_6_load_102 | 95 | 0.0033152 | 0.00083087 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-117_0_6_load_103 | 96 | 0.0032578 | 0.00081649 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-117_0_6_load_132 | 98 | 0.0047196 | 0.0011828 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-117_0_6_load_131 | 99 | 0.0013579 | 0.00034031 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-117_0_6_load_150 | 100 | 0.011241 | 0.0028174 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-117_0_6_load_141 | 101 | 0.0065675 | 0.001646 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-117_0_6_load_122 | 104 | 0.0050464 | 0.0012647 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-117_0_6_load_134 | 105 | 0.0048611 | 0.0012183 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-117_0_6_load_138 | 106 | 0.0060306 | 0.0015114 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-117_0_6_load_105 | 108 | 0.0085702 | 0.0021479 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-117_0_6_load_80 | 109 | 0.0081385 | 0.0020397 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-117_0_6_load_81 | 110 | 0.003673 | 0.00092054 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-117_0_6_load_82 | 111 | 0.0079775 | 0.0019993 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-117_0_6_load_83 | 112 | 0.0036548 | 0.00091599 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-117_0_6_load_84 | 113 | 0.0048073 | 0.0012048 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-117_0_6_load_96 | 114 | 0.0031222 | 0.00078251 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-117_0_6_load_97 | 115 | 0.00098144 | 0.00024597 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-117_0_6_load_85 | 116 | 0.008579 | 0.0021501 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-117_0_6_load_89 | 117 | 0.01133 | 0.0028395 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-117_0_6_load_91 | 118 | 0.0044599 | 0.0011177 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-117_0_6_load_139 | 120 | 0.032047 | 0.0080317 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-117_0_6_load_116 | 122 | 0.0099632 | 0.002497 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-117_0_6_load_100 | 123 | 0.0042969 | 0.0010769 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-117_0_6_load_98 | 124 | 0.0052632 | 0.0013191 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_261-117_0_6_load_99 | 125 | 0.0010342 | 0.0002592 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_261-117_0_6_load_104 | 126 | 0.0059389 | 0.0014884 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_261-117_0_6_load_130 | 127 | 0.0027574 | 0.00069108 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_261-117_0_6_load_114 | 128 | 0.0036388 | 0.00091197 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_261-117_0_6_load_119 | 129 | 0.0039185 | 0.00098206 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_261-117_0_6_load_117 | 130 | 0.0075297 | 0.0018871 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_261-117_0_6_load_118 | 131 | 0.0035311 | 0.00088498 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_261-117_0_6_load_120 | 132 | 0.0036489 | 0.0009145 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_261-117_0_6_load_125 | 134 | 0.0014697 | 0.00036835 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_261-117_0_6_load_121 | 135 | 0.0032453 | 0.00081336 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_261-117_0_6_load_129 | 136 | 0.001153 | 0.00028897 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_261-117_0_6_load_127 | 137 | 0.0032559 | 0.00081601 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_261-117_0_6_load_128 | 138 | 0.0036457 | 0.00091371 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_261-117_0_6_load_136 | 139 | 0.0069526 | 0.0017425 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 68 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-117_0_6_line_0 |  | 0 | 1 | 0.019761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-117_0_6_line_1 |  | 1 | 2 | 0.008764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-117_0_6_line_2 |  | 2 | 21 | 0.010916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-117_0_6_line_3 |  | 3 | 4 | 0.019935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-117_0_6_line_4 |  | 3 | 5 | 0.01558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-117_0_6_line_5 |  | 4 | 22 | 0.032841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-117_0_6_line_6 |  | 5 | 7 | 0.040483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-117_0_6_line_7 |  | 6 | 7 | 0.037255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-117_0_6_line_8 |  | 6 | 8 | 0.011093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-117_0_6_line_9 |  | 8 | 20 | 0.021774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-117_0_6_line_10 |  | 9 | 10 | 0.024484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-117_0_6_line_11 |  | 9 | 11 | 0.017722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-117_0_6_line_12 |  | 9 | 12 | 0.022959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-117_0_6_line_13 |  | 10 | 28 | 0.014012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-117_0_6_line_14 |  | 11 | 29 | 0.013828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-117_0_6_line_15 |  | 12 | 19 | 0.0035942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-117_0_6_line_16 |  | 13 | 14 | 0.0084667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-117_0_6_line_17 |  | 13 | 15 | 0.021424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-117_0_6_line_18 |  | 14 | 27 | 0.011808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-117_0_6_line_19 |  | 15 | 26 | 0.015241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-117_0_6_line_20 |  | 16 | 17 | 0.022654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-117_0_6_line_21 |  | 16 | 18 | 0.015381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-117_0_6_line_22 |  | 17 | 24 | 0.029561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-117_0_6_line_23 |  | 18 | 26 | 0.021887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-117_0_6_line_24 |  | 19 | 20 | 0.032995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-117_0_6_line_25 |  | 21 | 22 | 0.013141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-117_0_6_line_26 |  | 23 | 24 | 0.017516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-117_0_6_line_27 |  | 23 | 25 | 0.030267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-117_0_6_line_28 |  | 24 | 30 | 0.027867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-117_0_6_line_29 |  | 25 | 31 | 0.02878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-117_0_6_line_30 |  | 28 | 123 | 0.0016035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-117_0_6_line_31 |  | 29 | 73 | 0.0043797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
32 | LV_261-117_0_6_line_32 |  | 30 | 33 | 0.013796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-117_0_6_line_33 |  | 31 | 32 | 0.017903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-117_0_6_line_34 |  | 33 | 37 | 0.0098253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-117_0_6_line_35 |  | 34 | 35 | 0.010996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-117_0_6_line_36 |  | 34 | 36 | 0.013269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-117_0_6_line_37 |  | 35 | 48 | 0.008307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-117_0_6_line_38 |  | 36 | 93 | 0.026559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-117_0_6_line_39 |  | 37 | 109 | 0.035622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-117_0_6_line_40 |  | 38 | 39 | 0.022714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-117_0_6_line_41 |  | 38 | 40 | 0.051521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-117_0_6_line_42 |  | 39 | 41 | 0.004469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-117_0_6_line_43 |  | 40 | 42 | 0.033327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-117_0_6_line_44 |  | 41 | 43 | 0.029704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-117_0_6_line_45 |  | 41 | 44 | 0.013992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-117_0_6_line_46 |  | 42 | 51 | 0.013065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-117_0_6_line_47 |  | 45 | 46 | 0.14758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-117_0_6_line_48 |  | 45 | 47 | 0.014946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-117_0_6_line_49 |  | 46 | 58 | 0.090487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-117_0_6_line_50 |  | 47 | 57 | 0.034185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-117_0_6_line_51 |  | 48 | 49 | 0.014076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-117_0_6_line_52 |  | 49 | 50 | 0.010737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-117_0_6_line_53 |  | 51 | 77 | 0.009364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-117_0_6_line_54 |  | 52 | 53 | 0.018415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-117_0_6_line_55 |  | 52 | 54 | 0.023872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-117_0_6_line_56 |  | 52 | 55 | 0.00022312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-117_0_6_line_57 |  | 53 | 56 | 0.031444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-117_0_6_line_58 |  | 53 | 57 | 0.017411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-117_0_6_line_59 |  | 54 | 78 | 0.018341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-117_0_6_line_60 |  | 55 | 79 | 0.018212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-117_0_6_line_61 |  | 56 | 80 | 0.021018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-117_0_6_line_62 |  | 56 | 81 | 0.012008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-117_0_6_line_63 |  | 58 | 60 | 0.1888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-117_0_6_line_64 |  | 59 | 60 | 0.19418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-117_0_6_line_65 |  | 59 | 61 | 0.025946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-117_0_6_line_66 |  | 61 | 86 | 0.011567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-117_0_6_line_67 |  | 62 | 63 | 0.035535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_261-117_0_6_line_68 |  | 62 | 64 | 0.024285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-117_0_6_line_69 |  | 62 | 65 | 0.035955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_261-117_0_6_line_70 |  | 63 | 71 | 0.015368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
71 | LV_261-117_0_6_line_71 |  | 63 | 72 | 0.018489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-117_0_6_line_72 |  | 64 | 69 | 0.024236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-117_0_6_line_73 |  | 64 | 70 | 0.0076927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-117_0_6_line_74 |  | 65 | 100 | 0.0067404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
75 | LV_261-117_0_6_line_75 |  | 66 | 67 | 0.014308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
76 | LV_261-117_0_6_line_76 |  | 66 | 68 | 0.022563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_261-117_0_6_line_77 |  | 67 | 101 | 0.028674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-117_0_6_line_78 |  | 67 | 102 | 0.005949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-117_0_6_line_79 |  | 68 | 103 | 0.025421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_261-117_0_6_line_80 |  | 69 | 104 | 0.017395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_261-117_0_6_line_81 |  | 70 | 105 | 0.012685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-117_0_6_line_82 |  | 71 | 73 | 0.012987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
83 | LV_261-117_0_6_line_83 |  | 72 | 108 | 0.017919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_261-117_0_6_line_84 |  | 74 | 75 | 0.018321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_261-117_0_6_line_85 |  | 74 | 76 | 0.015137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_261-117_0_6_line_86 |  | 76 | 120 | 0.0096111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_261-117_0_6_line_87 |  | 77 | 88 | 0.0023929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_261-117_0_6_line_88 |  | 79 | 92 | 0.032626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_261-117_0_6_line_89 |  | 80 | 90 | 0.01221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_261-117_0_6_line_90 |  | 81 | 91 | 0.0087158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_261-117_0_6_line_91 |  | 82 | 83 | 0.018187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_261-117_0_6_line_92 |  | 83 | 92 | 0.017211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_261-117_0_6_line_93 |  | 84 | 85 | 0.0074838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_261-117_0_6_line_94 |  | 85 | 128 | 0.00026594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_261-117_0_6_line_95 |  | 86 | 87 | 0.17541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_261-117_0_6_line_96 |  | 88 | 89 | 0.0097348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_261-117_0_6_line_97 |  | 89 | 90 | 0.010142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_261-117_0_6_line_98 |  | 91 | 116 | 0.021527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_261-117_0_6_line_99 |  | 93 | 94 | 0.034784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_261-117_0_6_line_100 |  | 94 | 95 | 0.021025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_261-117_0_6_line_101 |  | 95 | 96 | 0.008907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_261-117_0_6_line_102 |  | 96 | 126 | 0.012782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_261-117_0_6_line_103 |  | 97 | 98 | 0.013105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_261-117_0_6_line_104 |  | 97 | 99 | 0.0070134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_261-117_0_6_line_105 |  | 99 | 127 | 0.019576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_261-117_0_6_line_106 |  | 100 | 121 | 0.01452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
107 | LV_261-117_0_6_line_107 |  | 101 | 120 | 0.003281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_261-117_0_6_line_108 |  | 102 | 116 | 0.022317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_261-117_0_6_line_109 |  | 103 | 122 | 0.0053554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
110 | LV_261-117_0_6_line_110 |  | 104 | 135 | 0.015592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_261-117_0_6_line_111 |  | 105 | 107 | 0.012064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_261-117_0_6_line_112 |  | 106 | 107 | 0.0059798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_261-117_0_6_line_113 |  | 107 | 139 | 0.02917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_261-117_0_6_line_114 |  | 108 | 126 | 0.02349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_261-117_0_6_line_115 |  | 109 | 110 | 0.012717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_261-117_0_6_line_116 |  | 110 | 111 | 0.018967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_261-117_0_6_line_117 |  | 111 | 112 | 0.001044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_261-117_0_6_line_118 |  | 112 | 113 | 0.022374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_261-117_0_6_line_119 |  | 113 | 114 | 0.0036523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_261-117_0_6_line_120 |  | 114 | 115 | 0.0087097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_261-117_0_6_line_121 |  | 115 | 124 | 0.009022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_261-117_0_6_line_122 |  | 117 | 118 | 0.015025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_261-117_0_6_line_123 |  | 118 | 119 | 0.024324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_261-117_0_6_line_124 |  | 119 | 121 | 0.007044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_261-117_0_6_line_125 |  | 121 | 122 | 0.0067502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
126 | LV_261-117_0_6_line_126 |  | 123 | 125 | 0.0071549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_261-117_0_6_line_127 |  | 124 | 125 | 0.014465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_261-117_0_6_line_128 |  | 127 | 138 | 0.00088581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_261-117_0_6_line_129 |  | 128 | 129 | 0.01838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_261-117_0_6_line_130 |  | 129 | 130 | 0.0082033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_261-117_0_6_line_131 |  | 130 | 131 | 0.023712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_261-117_0_6_line_132 |  | 131 | 132 | 0.001528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_261-117_0_6_line_133 |  | 132 | 133 | 0.0043904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_261-117_0_6_line_134 |  | 133 | 134 | 0.014181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_261-117_0_6_line_135 |  | 133 | 135 | 0.021991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_261-117_0_6_line_136 |  | 134 | 136 | 0.00091379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_261-117_0_6_line_137 |  | 136 | 137 | 0.013086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_261-117_0_6_line_138 |  | 137 | 138 | 0.00098858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-117_0_6_trafo_115 | 0.63 MVA 20/0.4 kV | 140 | 68 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2681071.3643 | 1252061.4851 | 2681070.2136 | 1252057.3219 | 2681071.2083 | 1252050.2747 | 2681074.3277 | 1252045.7028 | 2681076.1583 | 1252043.597
1 | 2681071.3643 | 1252061.4851 | 2681072.7738 | 1252066.586 | 2681074.4179 | 1252069.644
2 | 2681079.6122 | 1252079.2445 | 2681078.3748 | 1252077.0037 | 2681074.4179 | 1252069.644
3 | 2681133.9576 | 1252044.885 | 2681129.6843 | 1252051.5981 | 2681122.5577 | 1252054.4694 | 2681120.324 | 1252054.4388 | 2681118.4603 | 1252055.3167
4 | 2681133.9576 | 1252044.885 | 2681148.2181 | 1252038.6089
5 | 2681090.0091 | 1252071.4177 | 2681097.8341 | 1252067.5185 | 2681106.3538 | 1252061.0191 | 2681118.4603 | 1252055.3167
6 | 2681181.9053 | 1252019.1891 | 2681168.2603 | 1252024.6063 | 2681164.5612 | 1252027.9692 | 2681160.4417 | 1252034.4621 | 2681152.2519 | 1252038.3639 | 2681148.2181 | 1252038.6089
7 | 2681181.9053 | 1252019.1891 | 2681183.2812 | 1252022.8774 | 2681180.8488 | 1252026.3355 | 2681181.0095 | 1252030.5742 | 2681183.1175 | 1252035.3734 | 2681184.9498 | 1252034.3977 | 2681187.1434 | 1252032.9489 | 2681193.2974 | 1252046.5211
8 | 2681193.2974 | 1252046.5211 | 2681203.4154 | 1252041.9736
9 | 2681212.9011 | 1252025.9744 | 2681210.8636 | 1252029.249 | 2681212.2419 | 1252036.6178 | 2681208.6381 | 1252039.6262 | 2681203.4154 | 1252041.9736
10 | 2681214.8391 | 1252089.3927 | 2681237.4103 | 1252079.7504
11 | 2681237.4103 | 1252079.7504 | 2681242.6178 | 1252096.6902
12 | 2681237.4103 | 1252079.7504 | 2681229.9029 | 1252058.0538
13 | 2681214.8391 | 1252089.3927 | 2681202.0584 | 1252095.1367
14 | 2681243.913 | 1252110.4157 | 2681243.1326 | 1252098.3649 | 2681242.6178 | 1252096.6902
15 | 2681228.7276 | 1252054.6571 | 2681229.9029 | 1252058.0538
16 | 2681152.6846 | 1252076.1869 | 2681160.3366 | 1252072.5631
17 | 2681152.6846 | 1252076.1869 | 2681148.6171 | 1252078.8888 | 2681146.1051 | 1252082.6461 | 2681138.7429 | 1252086.1923 | 2681135.9111 | 1252086.2981 | 2681134.9859 | 1252086.7165
18 | 2681160.3366 | 1252072.5631 | 2681171.0083 | 1252067.5092 | 2681171.0083 | 1252067.5092
19 | 2681121.6918 | 1252093.9869 | 2681125.6963 | 1252090.9172 | 2681134.9859 | 1252086.7165
20 | 2681089.2423 | 1252111.2557 | 2681082.7215 | 1252117.8491 | 2681070.3654 | 1252122.9839
21 | 2681089.2423 | 1252111.2557 | 2681091.4235 | 1252109.0506 | 2681102.5654 | 1252103.8882
22 | 2681043.7418 | 1252135.8071 | 2681065.3919 | 1252125.0508 | 2681070.3654 | 1252122.9839
23 | 2681121.6918 | 1252093.9869 | 2681114.2322 | 1252099.6891 | 2681108.6773 | 1252102.4373 | 2681103.2881 | 1252103.5533 | 2681102.5654 | 1252103.8882
24 | 2681212.9011 | 1252025.9744 | 2681216.229 | 1252029.3225 | 2681221.7309 | 1252038.7049 | 2681228.7276 | 1252054.6571
25 | 2681079.6122 | 1252079.2445 | 2681083.5979 | 1252076.9974 | 2681088.5172 | 1252072.1611 | 2681090.0091 | 1252071.4177
26 | 2681036.1234 | 1252120.0245 | 2681043.7418 | 1252135.8071
27 | 2681036.1234 | 1252120.0245 | 2681030.5043 | 1252105.9594 | 2681025.2218 | 1252091.7907
28 | 2681057.0751 | 1252160.2966 | 2681046.1272 | 1252140.1874 | 2681043.7418 | 1252135.8071
29 | 2681016.7643 | 1252064.285 | 2681024.629 | 1252090.2007 | 2681025.2218 | 1252091.7907
30 | 2681200.5958 | 1252095.794 | 2681202.0584 | 1252095.1367
31 | 2681242.3902 | 1252114.0252 | 2681244.0544 | 1252112.5993 | 2681243.913 | 1252110.4157
32 | 2681057.0751 | 1252160.2966 | 2681069.6584 | 1252154.6413
33 | 2681020.277 | 1252049.1662 | 2681022.244 | 1252059.8566 | 2681016.7643 | 1252064.285
34 | 2681069.6584 | 1252154.6413 | 2681078.6202 | 1252150.6135
35 | 2681072.4189 | 1252200.5587 | 2681063.056 | 1252206.3682
36 | 2681072.4189 | 1252200.5587 | 2681084.3803 | 1252194.816
37 | 2681067.4729 | 1252213.4117 | 2681063.056 | 1252206.3682
38 | 2681084.3803 | 1252194.816 | 2681103.6518 | 1252185.5638 | 2681108.3907 | 1252183.4694
39 | 2681111.1114 | 1252136.011 | 2681078.6202 | 1252150.6135
40 | 2681138.6152 | 1252395.1541 | 2681129.2482 | 1252384.2066 | 2681123.6983 | 1252378.0266
41 | 2681095.6193 | 1252335.0541 | 2681106.1659 | 1252353.0118 | 2681115.4882 | 1252368.8846 | 2681123.6983 | 1252378.0266
42 | 2681138.6152 | 1252395.1541 | 2681141.8942 | 1252398.2013
43 | 2681095.6193 | 1252335.0541 | 2681100.3156 | 1252332.1606 | 2681107.8515 | 1252327.4825 | 2681117.6279 | 1252321.7787 | 2681124.371 | 1252318.224
44 | 2681163.7932 | 1252404.4725 | 2681156.1057 | 1252411.4057 | 2681141.8942 | 1252398.2013
45 | 2681141.8942 | 1252398.2013 | 2681131.7782 | 1252407.8671
46 | 2681124.371 | 1252318.224 | 2681136.0754 | 1252312.4188
47 | 2681176.9934 | 1252356.5621 | 2681179.47 | 1252359.7873 | 2681182.0421 | 1252363.2028 | 2681201.3274 | 1252394.4126 | 2681214.5851 | 1252414.4203 | 2681219.3787 | 1252422.5921 | 2681221.1917 | 1252419.1699 | 2681229.488 | 1252404.1724 | 2681242.7587 | 1252408.9246 | 2681265.6105 | 1252404.0454 | 2681274.5418 | 1252398.3303
48 | 2681176.9934 | 1252356.5621 | 2681186.0182 | 1252344.6477
49 | 2681274.5418 | 1252398.3303 | 2681276.5449 | 1252391.5082 | 2681285.5295 | 1252363.2215 | 2681288.5686 | 1252355.702 | 2681301.9474 | 1252339.9405 | 2681318.2017 | 1252321.0608
50 | 2681186.0182 | 1252344.6477 | 2681186.855 | 1252343.543 | 2681197.1503 | 1252326.9717 | 2681203.1677 | 1252315.1214
51 | 2681067.4729 | 1252213.4117 | 2681072.5692 | 1252221.5541 | 2681076.0269 | 1252218.7216
52 | 2681076.0269 | 1252218.7216 | 2681082.5301 | 1252213.4066 | 2681084.5646 | 1252212.2543
53 | 2681144.4643 | 1252308.2581 | 2681136.0754 | 1252312.4188
54 | 2681211.0505 | 1252299.5973 | 2681215.0065 | 1252301.7087 | 2681227.5578 | 1252307.7519
55 | 2681227.5578 | 1252307.7519 | 2681228.7519 | 1252312.0381 | 2681230.7498 | 1252316.5911 | 2681224.1212 | 1252329.4315
56 | 2681227.7577 | 1252307.8509 | 2681227.5578 | 1252307.7519
57 | 2681211.0505 | 1252299.5973 | 2681206.398 | 1252287.7359 | 2681202.7919 | 1252279.3691 | 2681194.1827 | 1252283.5987
58 | 2681211.0505 | 1252299.5973 | 2681203.1677 | 1252315.1214
59 | 2681215.7077 | 1252345.7293 | 2681224.1212 | 1252329.4315
60 | 2681227.7577 | 1252307.8509 | 2681244.0773 | 1252315.9339
61 | 2681194.1827 | 1252283.5987 | 2681175.3538 | 1252292.9375
62 | 2681194.1827 | 1252283.5987 | 2681191.0765 | 1252276.7511 | 2681189.3483 | 1252272.6081
63 | 2681458.1915 | 1252204.9299 | 2681454.5538 | 1252202.1779 | 2681448.5663 | 1252210.5796 | 2681446.1631 | 1252216.2953 | 2681442.7537 | 1252221.0854 | 2681432.0661 | 1252232.6471 | 2681404.9746 | 1252259.8285 | 2681395.5423 | 1252268.472 | 2681385.3205 | 1252275.8038 | 2681347.8167 | 1252294.5584 | 2681339.2584 | 1252298.3771 | 2681334.2453 | 1252302.3445 | 2681319.1196 | 1252319.9946 | 2681318.2017 | 1252321.0608
64 | 2681314.581 | 1252331.1851 | 2681335.7523 | 1252306.9242 | 2681340.8448 | 1252302.6687 | 2681381.3081 | 1252282.7427 | 2681390.1889 | 1252277.4274 | 2681395.6991 | 1252273.5335 | 2681404.7571 | 1252265.2184 | 2681413.6876 | 1252256.29 | 2681445.7459 | 1252223.5839 | 2681458.1915 | 1252204.9299
65 | 2681314.581 | 1252331.1851 | 2681333.9485 | 1252348.4498
66 | 2681333.9485 | 1252348.4498 | 2681342.5832 | 1252356.147
67 | 2681243.371 | 1252151.9526 | 2681247.7248 | 1252150.3889 | 2681251.0165 | 1252149.2109 | 2681248.2902 | 1252141.6345 | 2681245.2652 | 1252132.7198 | 2681240.6874 | 1252131.912 | 2681235.7768 | 1252133.9017
68 | 2681243.371 | 1252151.9526 | 2681247.7248 | 1252150.3889 | 2681250.1062 | 1252160.5513 | 2681254.0904 | 1252168.8677
69 | 2681243.371 | 1252151.9526 | 2681249.6777 | 1252169.7745 | 2681246.6265 | 1252174.325 | 2681235.5753 | 1252177.7538
70 | 2681235.2466 | 1252123.5867 | 2681237.4968 | 1252128.4657 | 2681240.6874 | 1252131.912 | 2681235.7768 | 1252133.9017
71 | 2681235.7768 | 1252133.9017 | 2681231.5115 | 1252135.6223 | 2681230.0729 | 1252138.16 | 2681219.7827 | 1252141.9689
72 | 2681254.0904 | 1252168.8677 | 2681269.6626 | 1252187.4395
73 | 2681254.0904 | 1252168.8677 | 2681261.4089 | 1252166.4975
74 | 2681229.9344 | 1252181.4436 | 2681235.5753 | 1252177.7538 | 2681235.5753 | 1252177.7538
75 | 2681161.299 | 1252205.4011 | 2681166.8163 | 1252218.6087
76 | 2681161.299 | 1252205.4011 | 2681166.4466 | 1252203.1811 | 2681173.5174 | 1252202.1661 | 2681181.9488 | 1252197.1445
77 | 2681166.8163 | 1252218.6087 | 2681140.9867 | 1252231.0591
78 | 2681169.1109 | 1252224.0998 | 2681166.8163 | 1252218.6087
79 | 2681205.2562 | 1252189.9251 | 2681198.8184 | 1252195.4188 | 2681181.9488 | 1252197.1445
80 | 2681277.9812 | 1252202.5621 | 2681277.6679 | 1252201.9156 | 2681272.0347 | 1252193.8768 | 2681269.6626 | 1252187.4395
81 | 2681261.4089 | 1252166.4975 | 2681273.4764 | 1252162.5893
82 | 2681235.2466 | 1252123.5867 | 2681236.4276 | 1252122.2241 | 2681235.9817 | 1252119.516 | 2681242.3902 | 1252114.0252
83 | 2681202.9783 | 1252148.189 | 2681219.7827 | 1252141.9689
84 | 2681121.626 | 1252245.3432 | 2681129.8536 | 1252261.7127
85 | 2681121.626 | 1252245.3432 | 2681119.7569 | 1252241.2924 | 2681129.3734 | 1252236.657
86 | 2681138.0312 | 1252232.4838 | 2681129.3734 | 1252236.657
87 | 2681146.6081 | 1252307.1948 | 2681144.4643 | 1252308.2581
88 | 2681251.8317 | 1252341.3115 | 2681256.1419 | 1252335.0752 | 2681256.9474 | 1252331.3724 | 2681256.1329 | 1252328.5814 | 2681245.8117 | 1252318.9772 | 2681246.0063 | 1252316.8894 | 2681244.0773 | 1252315.9339
89 | 2681175.3538 | 1252292.9375 | 2681164.4153 | 1252298.3628
90 | 2681189.3483 | 1252272.6081 | 2681185.9927 | 1252264.564
91 | 2681243.6815 | 1252356.466 | 2681238.7086 | 1252365.8147 | 2681234.4643 | 1252370.4155 | 2681233.6423 | 1252371.4717
92 | 2681243.6815 | 1252356.466 | 2681251.4448 | 1252341.8715 | 2681251.8317 | 1252341.3115
93 | 2681239.0966 | 1252260.9989 | 2681245.822 | 1252257.7162
94 | 2681246.061 | 1252257.5996 | 2681245.822 | 1252257.7162
95 | 2681342.5832 | 1252356.147 | 2681485.6884 | 1252457.5794
96 | 2681146.6081 | 1252307.1948 | 2681155.3291 | 1252302.8694
97 | 2681164.4153 | 1252298.3628 | 2681155.3291 | 1252302.8694
98 | 2681177.7049 | 1252244.6961 | 2681185.9927 | 1252264.564
99 | 2681140.7788 | 1252170.8593 | 2681122.4911 | 1252177.2376 | 2681108.3907 | 1252183.4694
100 | 2681140.7788 | 1252170.8593 | 2681157.2776 | 1252165.1049 | 2681160.6085 | 1252163.872
101 | 2681160.6085 | 1252163.872 | 2681168.9617 | 1252160.7801
102 | 2681168.9617 | 1252160.7801 | 2681180.9489 | 1252156.343
103 | 2681346.7081 | 1252206.5887 | 2681341.7179 | 1252194.4705
104 | 2681346.7081 | 1252206.5887 | 2681340.5498 | 1252209.9446
105 | 2681340.5498 | 1252209.9446 | 2681323.3606 | 1252219.3119
106 | 2681215.9133 | 1252184.9675 | 2681229.0485 | 1252182.0231 | 2681229.9344 | 1252181.4436
107 | 2681138.0312 | 1252232.4838 | 2681140.9867 | 1252231.0591
108 | 2681169.1109 | 1252224.0998 | 2681171.7489 | 1252230.4184 | 2681177.7049 | 1252244.6961
109 | 2681205.2562 | 1252189.9251 | 2681209.3267 | 1252186.445
110 | 2681285.4568 | 1252216.222 | 2681285.4568 | 1252216.222 | 2681281.5139 | 1252209.8521 | 2681277.9812 | 1252202.5621
111 | 2681284.9534 | 1252158.8724 | 2681273.4764 | 1252162.5893
112 | 2681284.9534 | 1252158.8724 | 2681290.3308 | 1252156.2569
113 | 2681284.9534 | 1252158.8724 | 2681289.9543 | 1252170.0938 | 2681293.5403 | 1252168.9199 | 2681296.8872 | 1252175.8265 | 2681299.5552 | 1252180.5637
114 | 2681202.9783 | 1252148.189 | 2681180.9489 | 1252156.343
115 | 2681111.1114 | 1252136.011 | 2681122.7111 | 1252130.7978
116 | 2681140.011 | 1252123.0227 | 2681122.7111 | 1252130.7978
117 | 2681140.011 | 1252123.0227 | 2681140.9633 | 1252122.5947
118 | 2681140.9633 | 1252122.5947 | 2681161.3711 | 1252113.4228
119 | 2681164.7024 | 1252111.9256 | 2681161.3711 | 1252113.4228
120 | 2681164.7024 | 1252111.9256 | 2681172.6467 | 1252108.3552
121 | 2681180.8758 | 1252104.6568 | 2681172.6467 | 1252108.3552
122 | 2681194.4053 | 1252212.8713 | 2681209.3212 | 1252211.0632
123 | 2681212.4628 | 1252191.1136 | 2681214.0687 | 1252197.8407 | 2681217.3451 | 1252202.1888 | 2681209.3212 | 1252211.0632
124 | 2681215.9133 | 1252184.9675 | 2681212.4628 | 1252191.1136
125 | 2681215.9133 | 1252184.9675 | 2681209.3267 | 1252186.445
126 | 2681194.0698 | 1252098.727 | 2681200.5958 | 1252095.794
127 | 2681194.0698 | 1252098.727 | 2681180.8758 | 1252104.6568
128 | 2681323.3606 | 1252219.3119 | 2681322.5827 | 1252219.7357
129 | 2681246.061 | 1252257.5996 | 2681247.8963 | 1252256.7038 | 2681254.2713 | 1252253.5889 | 2681262.5777 | 1252249.5353
130 | 2681269.9499 | 1252245.9376 | 2681262.5777 | 1252249.5353
131 | 2681269.9499 | 1252245.9376 | 2681291.2596 | 1252235.5383
132 | 2681291.2596 | 1252235.5383 | 2681292.6329 | 1252234.8681
133 | 2681296.5785 | 1252232.9426 | 2681292.6329 | 1252234.8681
134 | 2681296.5785 | 1252232.9426 | 2681309.2706 | 1252226.6174
135 | 2681296.5785 | 1252232.9426 | 2681286.0089 | 1252224.9361 | 2681285.4568 | 1252216.222
136 | 2681310.0885 | 1252226.2098 | 2681309.2706 | 1252226.6174
137 | 2681321.7147 | 1252220.2088 | 2681317.2717 | 1252222.63 | 2681310.0885 | 1252226.2098
138 | 2681322.5827 | 1252219.7357 | 2681321.7147 | 1252220.2088

## bus_geodata
| x | y | coords
0 | 2681076.1583 | 1252043.597
1 | 2681071.3643 | 1252061.4851
2 | 2681074.4179 | 1252069.644
3 | 2681133.9576 | 1252044.885
4 | 2681118.4603 | 1252055.3167
5 | 2681148.2181 | 1252038.6089
6 | 2681193.2974 | 1252046.5211
7 | 2681181.9053 | 1252019.1891
8 | 2681203.4154 | 1252041.9736
9 | 2681237.4103 | 1252079.7504
10 | 2681214.8391 | 1252089.3927
11 | 2681242.6178 | 1252096.6902
12 | 2681229.9029 | 1252058.0538
13 | 2681152.6846 | 1252076.1869
14 | 2681160.3366 | 1252072.5631
15 | 2681134.9859 | 1252086.7165
16 | 2681089.2423 | 1252111.2557
17 | 2681070.3654 | 1252122.9839
18 | 2681102.5654 | 1252103.8882
19 | 2681228.7276 | 1252054.6571
20 | 2681212.9011 | 1252025.9744
21 | 2681079.6122 | 1252079.2445
22 | 2681090.0091 | 1252071.4177
23 | 2681036.1234 | 1252120.0245
24 | 2681043.7418 | 1252135.8071
25 | 2681025.2218 | 1252091.7907
26 | 2681121.6918 | 1252093.9869
27 | 2681171.0083 | 1252067.5092
28 | 2681202.0584 | 1252095.1367
29 | 2681243.913 | 1252110.4157
30 | 2681057.0751 | 1252160.2966
31 | 2681016.7643 | 1252064.285
32 | 2681020.277 | 1252049.1662
33 | 2681069.6584 | 1252154.6413
34 | 2681072.4189 | 1252200.5587
35 | 2681063.056 | 1252206.3682
36 | 2681084.3803 | 1252194.816
37 | 2681078.6202 | 1252150.6135
38 | 2681123.6983 | 1252378.0266
39 | 2681138.6152 | 1252395.1541
40 | 2681095.6193 | 1252335.0541
41 | 2681141.8942 | 1252398.2013
42 | 2681124.371 | 1252318.224
43 | 2681163.7932 | 1252404.4725
44 | 2681131.7782 | 1252407.8671
45 | 2681176.9934 | 1252356.5621
46 | 2681274.5418 | 1252398.3303
47 | 2681186.0182 | 1252344.6477
48 | 2681067.4729 | 1252213.4117
49 | 2681076.0269 | 1252218.7216
50 | 2681084.5646 | 1252212.2543
51 | 2681136.0754 | 1252312.4188
52 | 2681227.5578 | 1252307.7519
53 | 2681211.0505 | 1252299.5973
54 | 2681224.1212 | 1252329.4315
55 | 2681227.7577 | 1252307.8509
56 | 2681194.1827 | 1252283.5987
57 | 2681203.1677 | 1252315.1214
58 | 2681318.2017 | 1252321.0608
59 | 2681314.581 | 1252331.1851
60 | 2681458.1915 | 1252204.9299
61 | 2681333.9485 | 1252348.4498
62 | 2681243.371 | 1252151.9526
63 | 2681235.7768 | 1252133.9017
64 | 2681254.0904 | 1252168.8677
65 | 2681235.5753 | 1252177.7538
66 | 2681161.299 | 1252205.4011
67 | 2681166.8163 | 1252218.6087
68 | 2681181.9488 | 1252197.1445
69 | 2681269.6626 | 1252187.4395
70 | 2681261.4089 | 1252166.4975
71 | 2681235.2466 | 1252123.5867
72 | 2681219.7827 | 1252141.9689
73 | 2681242.3902 | 1252114.0252
74 | 2681121.626 | 1252245.3432
75 | 2681129.8536 | 1252261.7127
76 | 2681129.3734 | 1252236.657
77 | 2681144.4643 | 1252308.2581
78 | 2681215.7077 | 1252345.7293
79 | 2681244.0773 | 1252315.9339
80 | 2681175.3538 | 1252292.9375
81 | 2681189.3483 | 1252272.6081
82 | 2681233.6423 | 1252371.4717
83 | 2681243.6815 | 1252356.466
84 | 2681239.0966 | 1252260.9989
85 | 2681245.822 | 1252257.7162
86 | 2681342.5832 | 1252356.147
87 | 2681485.6884 | 1252457.5794
88 | 2681146.6081 | 1252307.1948
89 | 2681155.3291 | 1252302.8694
90 | 2681164.4153 | 1252298.3628
91 | 2681185.9927 | 1252264.564
92 | 2681251.8318 | 1252341.3115
93 | 2681108.3907 | 1252183.4694
94 | 2681140.7788 | 1252170.8593
95 | 2681160.6085 | 1252163.872
96 | 2681168.9617 | 1252160.7801
97 | 2681346.7081 | 1252206.5887
98 | 2681341.7179 | 1252194.4705
99 | 2681340.5498 | 1252209.9446
100 | 2681229.9344 | 1252181.4436
101 | 2681140.9867 | 1252231.0591
102 | 2681169.1109 | 1252224.0998
103 | 2681205.2562 | 1252189.9251
104 | 2681277.9812 | 1252202.5621
105 | 2681273.4764 | 1252162.5893
106 | 2681290.3308 | 1252156.2569
107 | 2681284.9534 | 1252158.8724
108 | 2681202.9783 | 1252148.189
109 | 2681111.1114 | 1252136.011
110 | 2681122.7111 | 1252130.7978
111 | 2681140.011 | 1252123.0227
112 | 2681140.9633 | 1252122.5947
113 | 2681161.3711 | 1252113.4228
114 | 2681164.7024 | 1252111.9256
115 | 2681172.6467 | 1252108.3552
116 | 2681177.7049 | 1252244.6961
117 | 2681194.4053 | 1252212.8713
118 | 2681209.3212 | 1252211.0632
119 | 2681212.4628 | 1252191.1136
120 | 2681138.0312 | 1252232.4838
121 | 2681215.9133 | 1252184.9675
122 | 2681209.3267 | 1252186.445
123 | 2681200.5958 | 1252095.794
124 | 2681180.8758 | 1252104.6568
125 | 2681194.0698 | 1252098.727
126 | 2681180.9489 | 1252156.343
127 | 2681323.3606 | 1252219.3119
128 | 2681246.061 | 1252257.5996
129 | 2681262.5777 | 1252249.5353
130 | 2681269.9499 | 1252245.9376
131 | 2681291.2596 | 1252235.5383
132 | 2681292.6329 | 1252234.8681
133 | 2681296.5785 | 1252232.9426
134 | 2681309.2706 | 1252226.6174
135 | 2681285.4568 | 1252216.222
136 | 2681310.0885 | 1252226.2098
137 | 2681321.7147 | 1252220.2088
138 | 2681322.5827 | 1252219.7357
139 | 2681299.5552 | 1252180.5637
140 | 2681161.299 | 1252205.4011

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97997 | -0.38495 | 0.0035906 | 0.00089988
1 | 0.98004 | -0.38366 | 0 | 0
2 | 0.98007 | -0.38309 | 0.0049976 | 0.0012525
3 | 0.98092 | -0.36645 | 0 | 0
4 | 0.98063 | -0.37218 | 0.0038629 | 0.00096813
5 | 0.98115 | -0.36197 | 0.0037296 | 0.00093473
6 | 0.98256 | -0.33441 | 0 | 0
7 | 0.98188 | -0.34761 | 0 | 0
8 | 0.98276 | -0.33048 | 0.0022164 | 0.00055548
9 | 0.98448 | -0.29689 | 0 | 0
10 | 0.98262 | -0.333 | 0 | 0
11 | 0.98625 | -0.26266 | 0.0030382 | 0.00076144
12 | 0.98393 | -0.30752 | 0.0038979 | 0.0009769
13 | 0.97126 | -0.55561 | 0 | 0
14 | 0.97122 | -0.55647 | 0.0016163 | 0.00040509
15 | 0.97137 | -0.55344 | 0.0038762 | 0.00097147
16 | 0.97191 | -0.54279 | 0 | 0
17 | 0.97222 | -0.53656 | 0.0084367 | 0.0021144
18 | 0.97169 | -0.54702 | 0.0055411 | 0.0013887
19 | 0.98386 | -0.30893 | 0 | 0
20 | 0.9832 | -0.32191 | 0 | 0
21 | 0.98016 | -0.38139 | 0 | 0
22 | 0.98026 | -0.37934 | 0.0034246 | 0.00085828
23 | 0.9727 | -0.52717 | 0 | 0
24 | 0.97287 | -0.52384 | 0 | 0
25 | 0.97241 | -0.53291 | 0.0059301 | 0.0014862
26 | 0.9715 | -0.55081 | 0 | 0
27 | 0.97117 | -0.55732 | 0.0038705 | 0.00097005
28 | 0.98155 | -0.35373 | 0.00098439 | 0.00024671
29 | 0.98767 | -0.23528 | 0.0055965 | 0.0014026
30 | 0.97374 | -0.50659 | 0 | 0
31 | 0.97229 | -0.53523 | 0 | 0
32 | 0.97222 | -0.53668 | 0.0043702 | 0.0010953
33 | 0.97418 | -0.49806 | 0.002436 | 0.00061051
34 | 0.98085 | -0.36839 | 0 | 0
35 | 0.98074 | -0.37041 | 0.0048783 | 0.0012226
36 | 0.98097 | -0.36594 | 0.0050212 | 0.0012584
37 | 0.97451 | -0.49155 | 0.0018407 | 0.00046132
38 | 0.98685 | -0.25323 | 0.0041544 | 0.0010412
39 | 0.98636 | -0.26275 | 0 | 0
40 | 0.98815 | -0.22786 | 0 | 0
41 | 0.98626 | -0.26462 | 0 | 0
42 | 0.989 | -0.21148 | 0 | 0
43 | 0.98586 | -0.27254 | 0.01487 | 0.0037268
44 | 0.98615 | -0.26676 | 0.0085259 | 0.0021368
45 | 0.98947 | -0.20249 | 0 | 0
46 | 0.98821 | -0.22701 | 0 | 0
47 | 0.98959 | -0.20001 | 0.0040855 | 0.0010239
48 | 0.9807 | -0.37121 | 0 | 0
49 | 0.98063 | -0.37256 | 0 | 0
50 | 0.98058 | -0.37359 | 0.0052895 | 0.0013257
51 | 0.98933 | -0.20507 | 0.0012209 | 0.00030599
52 | 0.98993 | -0.19345 | 0 | 0
53 | 0.99032 | -0.18587 | 0 | 0
54 | 0.98979 | -0.19621 | 0.0033668 | 0.00084379
55 | 0.98993 | -0.19352 | 0.0039455 | 0.00098885
56 | 0.99155 | -0.16216 | 0 | 0
57 | 0.99001 | -0.19185 | 0.0059133 | 0.001482
58 | 0.98743 | -0.24207 | 0.0039116 | 0.00098034
59 | 0.98554 | -0.27911 | 0 | 0
60 | 0.9865 | -0.26032 | 0 | 0
61 | 0.98541 | -0.28162 | 0.0023383 | 0.00058602
62 | 0.99116 | -0.16825 | 0 | 0
63 | 0.98897 | -0.21038 | 0 | 0
64 | 0.98934 | -0.20356 | 0 | 0
65 | 0.99428 | -0.1085 | 0.0087456 | 0.0021919
66 | 0.99876 | -0.023721 | 0 | 0
67 | 0.99757 | -0.046339 | 0 | 0
68 | 1 | 0 | -0.51627 | -0.13141
69 | 0.98798 | -0.22979 | 0.0054443 | 0.0013645
70 | 0.98919 | -0.20645 | 0.0032827 | 0.00082271
71 | 0.98839 | -0.22141 | 0 | 0
72 | 0.98761 | -0.23655 | 0.0060421 | 0.0015143
73 | 0.98791 | -0.23074 | 0.0045054 | 0.0011292
74 | 0.99466 | -0.1025 | 0 | 0
75 | 0.9944 | -0.10758 | 0.015745 | 0.0039462
76 | 0.99488 | -0.0983 | 0.026268 | 0.0065835
77 | 0.98958 | -0.20027 | 0.0026884 | 0.00067378
78 | 0.98974 | -0.19722 | 0.0031151 | 0.00078072
79 | 0.98972 | -0.19765 | 0.003071 | 0.00076966
80 | 0.99074 | -0.17782 | 0.0025441 | 0.00063762
81 | 0.99248 | -0.14418 | 0.0025103 | 0.00062914
82 | 0.98928 | -0.2062 | 0.0031501 | 0.00078949
83 | 0.98933 | -0.20518 | 0.0031078 | 0.00077888
84 | 0.9845 | -0.29749 | 0.0044512 | 0.0011156
85 | 0.98453 | -0.29689 | 0.0018618 | 0.0004666
86 | 0.98538 | -0.28225 | 0.0011502 | 0.00028826
87 | 0.98507 | -0.28824 | 0.0018972 | 0.00047548
88 | 0.98965 | -0.19893 | 0.0026901 | 0.00067419
89 | 0.98995 | -0.19302 | 0.0026371 | 0.00066092
90 | 0.99029 | -0.18638 | 0.0026701 | 0.00066918
91 | 0.99317 | -0.13077 | 0.0045085 | 0.0011299
92 | 0.98943 | -0.20326 | 0.003404 | 0.00085312
93 | 0.98134 | -0.35864 | 0.031209 | 0.0078216
94 | 0.98284 | -0.32947 | 0.0057803 | 0.0014487
95 | 0.98385 | -0.30969 | 0.0033152 | 0.00083087
96 | 0.98431 | -0.3008 | 0.0032578 | 0.00081649
97 | 0.98483 | -0.29122 | 0 | 0
98 | 0.98477 | -0.29234 | 0.0047196 | 0.0011828
99 | 0.98486 | -0.29063 | 0.0013579 | 0.00034031
100 | 0.99489 | -0.096995 | 0.011241 | 0.0028174
101 | 0.99547 | -0.086917 | 0.0065675 | 0.001646
102 | 0.99703 | -0.056775 | 0 | 0
103 | 0.99744 | -0.04851 | 0 | 0
104 | 0.9871 | -0.24696 | 0.0050464 | 0.0012647
105 | 0.98898 | -0.21049 | 0.0048611 | 0.0012183
106 | 0.9888 | -0.21392 | 0.0060306 | 0.0015114
107 | 0.98884 | -0.21328 | 0 | 0
108 | 0.9864 | -0.26003 | 0.0085702 | 0.0021479
109 | 0.97577 | -0.46679 | 0.0081385 | 0.0020397
110 | 0.97631 | -0.45607 | 0.003673 | 0.00092054
111 | 0.97719 | -0.43883 | 0.0079775 | 0.0019993
112 | 0.97725 | -0.43773 | 0.0036548 | 0.00091599
113 | 0.97853 | -0.41271 | 0.0048073 | 0.0012048
114 | 0.97875 | -0.40831 | 0.0031222 | 0.00078251
115 | 0.97931 | -0.39733 | 0.00098144 | 0.00024597
116 | 0.99498 | -0.096024 | 0.008579 | 0.0021501
117 | 0.99563 | -0.082999 | 0.01133 | 0.0028395
118 | 0.99579 | -0.080007 | 0.0044599 | 0.0011177
119 | 0.99614 | -0.073258 | 0 | 0
120 | 0.99525 | -0.091192 | 0.032047 | 0.0080317
121 | 0.99624 | -0.071304 | 0 | 0
122 | 0.9969 | -0.058761 | 0.0099632 | 0.002497
123 | 0.98143 | -0.35608 | 0.0042969 | 0.0010769
124 | 0.9799 | -0.38581 | 0.0052632 | 0.0013191
125 | 0.98092 | -0.366 | 0.0010342 | 0.0002592
126 | 0.985 | -0.2873 | 0.0059389 | 0.0014884
127 | 0.98497 | -0.28849 | 0.0027574 | 0.00069108
128 | 0.98454 | -0.29686 | 0.0036388 | 0.00091197
129 | 0.9847 | -0.29358 | 0.0039185 | 0.00098206
130 | 0.98481 | -0.29153 | 0.0075297 | 0.0018871
131 | 0.98528 | -0.28241 | 0.0035311 | 0.00088498
132 | 0.98531 | -0.28173 | 0.0036489 | 0.0009145
133 | 0.98543 | -0.27948 | 0 | 0
134 | 0.98519 | -0.28415 | 0.0014697 | 0.00036835
135 | 0.98638 | -0.26097 | 0.0032453 | 0.00081336
136 | 0.98517 | -0.28443 | 0.001153 | 0.00028897
137 | 0.98498 | -0.28813 | 0.0032559 | 0.00081601
138 | 0.98497 | -0.28835 | 0.0036457 | 0.00091371
139 | 0.98865 | -0.2169 | 0.0069526 | 0.0017425
140 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0035906 | -0.00089988 | 0.0035908 | 0.00089977 | 2.2027e-07 | -1.0802e-07 | 0.005452 | 0.0054519 | 0.005452 | 0.97997 | -0.38495 | 0.98004 | -0.38366 | 1.4978
1 | -0.0035908 | -0.00089977 | 0.0035909 | 0.00089973 | 9.7685e-08 | -4.7918e-08 | 0.0054519 | 0.0054519 | 0.0054519 | 0.98004 | -0.38366 | 0.98007 | -0.38309 | 1.4978
2 | -0.0085885 | -0.0021522 | 0.0085892 | 0.0021526 | 6.9601e-07 | 3.0788e-07 | 0.01304 | 0.01304 | 0.01304 | 0.98007 | -0.38309 | 0.98016 | -0.38139 | 3.5823
3 | 0.015886 | 0.0039841 | -0.015882 | -0.0039815 | 4.3417e-06 | 2.5271e-06 | 0.024099 | 0.024099 | 0.024099 | 0.98092 | -0.36645 | 0.98063 | -0.37218 | 6.6207
4 | -0.015886 | -0.0039841 | 0.015889 | 0.003986 | 3.3933e-06 | 1.975e-06 | 0.024099 | 0.024099 | 0.024099 | 0.98092 | -0.36645 | 0.98115 | -0.36197 | 6.6207
5 | 0.012019 | 0.0030134 | -0.012015 | -0.0030112 | 4.0963e-06 | 2.2075e-06 | 0.018238 | 0.018238 | 0.018238 | 0.98063 | -0.37218 | 0.98026 | -0.37934 | 5.0104
6 | -0.019619 | -0.0049208 | 0.019632 | 0.0049289 | 1.3441e-05 | 8.0907e-06 | 0.029756 | 0.029755 | 0.029756 | 0.98115 | -0.36197 | 0.98188 | -0.34761 | 8.1746
7 | 0.019645 | 0.0049363 | -0.019632 | -0.0049289 | 1.2369e-05 | 7.4448e-06 | 0.029755 | 0.029755 | 0.029755 | 0.98256 | -0.33441 | 0.98188 | -0.34761 | 8.1746
8 | -0.019645 | -0.0049363 | 0.019648 | 0.0049385 | 3.6831e-06 | 2.2166e-06 | 0.029755 | 0.029755 | 0.029755 | 0.98256 | -0.33441 | 0.98276 | -0.33048 | 8.1745
9 | -0.021865 | -0.005494 | 0.021874 | 0.0054995 | 8.9518e-06 | 5.4531e-06 | 0.033111 | 0.033111 | 0.033111 | 0.98276 | -0.33048 | 0.9832 | -0.32191 | 9.0965
10 | 0.082554 | 0.020958 | -0.082411 | -0.020866 | 0.00014317 | 9.1319e-05 | 0.12487 | 0.12487 | 0.12487 | 0.98448 | -0.29689 | 0.98262 | -0.333 | 34.3061
11 | -0.10835 | -0.027451 | 0.10853 | 0.027565 | 0.00017848 | 0.000114 | 0.16388 | 0.16388 | 0.16388 | 0.98448 | -0.29689 | 0.98625 | -0.26266 | 45.0218
12 | 0.0258 | 0.0064936 | -0.025787 | -0.0064855 | 1.3099e-05 | 8.0915e-06 | 0.039006 | 0.039006 | 0.039006 | 0.98448 | -0.29689 | 0.98393 | -0.30752 | 10.7158
13 | 0.082411 | 0.020866 | -0.082329 | -0.020814 | 8.1937e-05 | 5.2262e-05 | 0.12487 | 0.12487 | 0.12487 | 0.98262 | -0.333 | 0.98155 | -0.35373 | 34.3061
14 | -0.11157 | -0.028327 | 0.11172 | 0.028421 | 0.00014716 | 9.4009e-05 | 0.16846 | 0.16846 | 0.16846 | 0.98625 | -0.26266 | 0.98767 | -0.23528 | 46.2811
15 | 0.021889 | 0.0055086 | -0.021887 | -0.0055077 | 1.4777e-06 | 9.0007e-07 | 0.033111 | 0.033111 | 0.033111 | 0.98393 | -0.30752 | 0.98386 | -0.30893 | 9.0964
16 | 0.0054873 | 0.0013751 | -0.005487 | -0.0013751 | 2.2439e-07 | 3.8828e-08 | 0.0084067 | 0.0084067 | 0.0084067 | 0.97126 | -0.55561 | 0.97122 | -0.55647 | 2.3095
17 | -0.0054873 | -0.0013751 | 0.0054878 | 0.0013752 | 5.6777e-07 | 9.8201e-08 | 0.0084067 | 0.0084066 | 0.0084067 | 0.97126 | -0.55561 | 0.97137 | -0.55344 | 2.3095
18 | 0.0038707 | 0.00097 | -0.0038705 | -0.00097005 | 1.5573e-07 | -4.6451e-08 | 0.0059303 | 0.0059304 | 0.0059304 | 0.97122 | -0.55647 | 0.97117 | -0.55732 | 1.6292
19 | -0.009364 | -0.0023467 | 0.0093652 | 0.0023473 | 1.176e-06 | 5.6395e-07 | 0.014344 | 0.014344 | 0.014344 | 0.97137 | -0.55344 | 0.9715 | -0.55081 | 3.9408
20 | -0.014911 | -0.0037385 | 0.014915 | 0.0037411 | 4.4276e-06 | 2.5528e-06 | 0.02283 | 0.02283 | 0.02283 | 0.97191 | -0.54279 | 0.97222 | -0.53656 | 6.2719
21 | 0.014911 | 0.0037385 | -0.014908 | -0.0037368 | 3.0062e-06 | 1.7334e-06 | 0.02283 | 0.02283 | 0.02283 | 0.97191 | -0.54279 | 0.97169 | -0.54702 | 6.2719
22 | -0.023352 | -0.0058555 | 0.023366 | 0.0058642 | 1.4161e-05 | 8.6965e-06 | 0.035742 | 0.035742 | 0.035742 | 0.97222 | -0.53656 | 0.97287 | -0.52384 | 9.8193
23 | 0.0093669 | 0.0023481 | -0.0093652 | -0.0023473 | 1.6888e-06 | 8.0977e-07 | 0.014344 | 0.014344 | 0.014344 | 0.97169 | -0.54702 | 0.9715 | -0.55081 | 3.9408
24 | 0.021887 | 0.0055077 | -0.021874 | -0.0054995 | 1.3565e-05 | 8.2629e-06 | 0.033111 | 0.033111 | 0.033111 | 0.98386 | -0.30893 | 0.9832 | -0.32191 | 9.0964
25 | -0.0085892 | -0.0021526 | 0.00859 | 0.0021529 | 8.3788e-07 | 3.706e-07 | 0.01304 | 0.01304 | 0.01304 | 0.98016 | -0.38139 | 0.98026 | -0.37934 | 3.5823
26 | -0.010304 | -0.0025829 | 0.010306 | 0.0025837 | 1.6321e-06 | 8.2707e-07 | 0.015763 | 0.015763 | 0.015763 | 0.9727 | -0.52717 | 0.97287 | -0.52384 | 4.3305
27 | 0.010304 | 0.0025829 | -0.010301 | -0.0025814 | 2.8202e-06 | 1.4294e-06 | 0.015763 | 0.015763 | 0.015763 | 0.9727 | -0.52717 | 0.97241 | -0.53291 | 4.3305
28 | -0.033672 | -0.0084479 | 0.0337 | 0.0084653 | 2.7722e-05 | 1.7395e-05 | 0.051505 | 0.051505 | 0.051505 | 0.97287 | -0.52384 | 0.97374 | -0.50659 | 14.1497
29 | 0.004371 | 0.0010952 | -0.0043705 | -0.0010953 | 4.8283e-07 | -4.7968e-08 | 0.0066886 | 0.0066887 | 0.0066887 | 0.97241 | -0.53291 | 0.97229 | -0.53523 | 1.8376
30 | 0.081344 | 0.020567 | -0.081335 | -0.020562 | 9.1539e-06 | 5.8382e-06 | 0.12338 | 0.12338 | 0.12338 | 0.98155 | -0.35373 | 0.98143 | -0.35608 | 33.8961
31 | -0.11731 | -0.029823 | 0.11734 | 0.02984 | 2.5696e-05 | 1.6334e-05 | 0.17689 | 0.17689 | 0.17689 | 0.98767 | -0.23528 | 0.98791 | -0.23074 | 24.2987
32 | -0.0337 | -0.0084653 | 0.033713 | 0.0084739 | 1.3724e-05 | 8.6115e-06 | 0.051505 | 0.051505 | 0.051505 | 0.97374 | -0.50659 | 0.97418 | -0.49806 | 14.1497
33 | 0.0043705 | 0.0010953 | -0.0043702 | -0.0010953 | 3.0036e-07 | -2.979e-08 | 0.0066887 | 0.0066888 | 0.0066888 | 0.97229 | -0.53523 | 0.97222 | -0.53668 | 1.8376
34 | -0.036149 | -0.0090844 | 0.036161 | 0.0090915 | 1.1237e-05 | 7.0694e-06 | 0.055226 | 0.055226 | 0.055226 | 0.97418 | -0.49806 | 0.97451 | -0.49155 | 15.1719
35 | 0.01017 | 0.0025489 | -0.010169 | -0.0025484 | 9.815e-07 | 4.8939e-07 | 0.015428 | 0.015428 | 0.015428 | 0.98085 | -0.36839 | 0.98074 | -0.37041 | 4.2385
36 | -0.01017 | -0.0025489 | 0.010171 | 0.0025495 | 1.1843e-06 | 5.9048e-07 | 0.015428 | 0.015428 | 0.015428 | 0.98085 | -0.36839 | 0.98097 | -0.36594 | 4.2385
37 | 0.0052903 | 0.0013258 | -0.0052901 | -0.0013258 | 2.007e-07 | 2.3627e-08 | 0.0080266 | 0.0080267 | 0.0080267 | 0.98074 | -0.37041 | 0.9807 | -0.37121 | 2.2051
38 | -0.015192 | -0.0038079 | 0.015197 | 0.0038109 | 5.2889e-06 | 3.0495e-06 | 0.023045 | 0.023044 | 0.023045 | 0.98097 | -0.36594 | 0.98134 | -0.35864 | 6.3309
39 | -0.038001 | -0.0095528 | 0.038046 | 0.0095812 | 4.4993e-05 | 2.8351e-05 | 0.058036 | 0.058036 | 0.058036 | 0.97451 | -0.49155 | 0.97577 | -0.46679 | 15.944
40 | 0.023415 | 0.005875 | -0.023405 | -0.0058685 | 1.0619e-05 | 6.5064e-06 | 0.035309 | 0.035309 | 0.035309 | 0.98685 | -0.25323 | 0.98636 | -0.26275 | 9.7003
41 | -0.02757 | -0.0069162 | 0.027603 | 0.0069369 | 3.3392e-05 | 2.0712e-05 | 0.041573 | 0.041573 | 0.041573 | 0.98685 | -0.25323 | 0.98815 | -0.22786 | 11.4212
42 | 0.023405 | 0.0058685 | -0.023403 | -0.0058672 | 2.0894e-06 | 1.2802e-06 | 0.035309 | 0.035309 | 0.035309 | 0.98636 | -0.26275 | 0.98626 | -0.26462 | 9.7003
43 | -0.027603 | -0.0069369 | 0.027625 | 0.0069503 | 2.16e-05 | 1.3397e-05 | 0.041573 | 0.041573 | 0.041573 | 0.98815 | -0.22786 | 0.989 | -0.21148 | 11.4211
44 | 0.014876 | 0.00373 | -0.01487 | -0.0037268 | 5.6113e-06 | 3.2123e-06 | 0.022444 | 0.022445 | 0.022445 | 0.98626 | -0.26462 | 0.98586 | -0.27254 | 6.1661
45 | 0.0085267 | 0.0021372 | -0.0085259 | -0.0021368 | 8.6836e-07 | 3.7722e-07 | 0.012865 | 0.012865 | 0.012865 | 0.98626 | -0.26462 | 0.98615 | -0.26676 | 3.5343
46 | -0.027625 | -0.0069503 | 0.027633 | 0.0069555 | 8.4676e-06 | 5.2515e-06 | 0.041573 | 0.041573 | 0.041573 | 0.989 | -0.21148 | 0.98933 | -0.20507 | 11.4211
47 | 0.0093255 | 0.0023376 | -0.0093146 | -0.0023325 | 1.0886e-05 | 5.0737e-06 | 0.014024 | 0.014025 | 0.014025 | 0.98947 | -0.20249 | 0.98821 | -0.22701 | 3.853
48 | -0.0093255 | -0.0023376 | 0.0093266 | 0.0023381 | 1.1024e-06 | 5.1353e-07 | 0.014024 | 0.014024 | 0.014024 | 0.98947 | -0.20249 | 0.98959 | -0.20001 | 3.8529
49 | 0.0093146 | 0.0023325 | -0.009308 | -0.0023294 | 6.6748e-06 | 3.1135e-06 | 0.014025 | 0.014025 | 0.014025 | 0.98821 | -0.22701 | 0.98743 | -0.24207 | 3.8532
50 | -0.013412 | -0.003362 | 0.013417 | 0.0033649 | 5.214e-06 | 2.8976e-06 | 0.020167 | 0.020167 | 0.020167 | 0.98959 | -0.20001 | 0.99001 | -0.19185 | 5.5405
51 | 0.0052901 | 0.0013258 | -0.0052898 | -0.0013257 | 3.4007e-07 | 4.0056e-08 | 0.0080267 | 0.0080267 | 0.0080267 | 0.9807 | -0.37121 | 0.98063 | -0.37256 | 2.2051
52 | 0.0052898 | 0.0013257 | -0.0052895 | -0.0013257 | 2.5942e-07 | 3.0574e-08 | 0.0080267 | 0.0080268 | 0.0080268 | 0.98063 | -0.37256 | 0.98058 | -0.37359 | 2.2052
53 | -0.028854 | -0.0072615 | 0.028861 | 0.0072656 | 6.6169e-06 | 4.1146e-06 | 0.043409 | 0.043409 | 0.043409 | 0.98933 | -0.20507 | 0.98958 | -0.20027 | 11.9256
54 | -0.023167 | -0.0058072 | 0.023175 | 0.0058124 | 8.3743e-06 | 5.1227e-06 | 0.034824 | 0.034824 | 0.034824 | 0.98993 | -0.19345 | 0.99032 | -0.18587 | 9.567
55 | 0.0064829 | 0.0016246 | -0.006482 | -0.0016244 | 8.5008e-07 | 2.3719e-07 | 0.0097447 | 0.0097448 | 0.0097448 | 0.98993 | -0.19345 | 0.98979 | -0.19621 | 2.6771
56 | 0.016684 | 0.0041826 | -0.016684 | -0.0041826 | 5.2625e-08 | 3.0812e-08 | 0.025079 | 0.025079 | 0.025079 | 0.98993 | -0.19345 | 0.98993 | -0.19352 | 6.8899
57 | -0.042512 | -0.010663 | 0.04256 | 0.010693 | 4.8116e-05 | 3.0389e-05 | 0.063879 | 0.063879 | 0.063879 | 0.99032 | -0.18587 | 0.99155 | -0.16216 | 17.5492
58 | 0.019336 | 0.0048502 | -0.019331 | -0.0048469 | 5.5118e-06 | 3.3036e-06 | 0.029055 | 0.029055 | 0.029055 | 0.99032 | -0.18587 | 0.99001 | -0.19185 | 7.9822
59 | 0.0031153 | 0.00078058 | -0.0031151 | -0.00078072 | 1.5086e-07 | -1.3917e-07 | 0.0046833 | 0.0046834 | 0.0046834 | 0.98979 | -0.19621 | 0.98974 | -0.19722 | 1.2867
60 | 0.012739 | 0.0031938 | -0.012736 | -0.0031924 | 2.5041e-06 | 1.3685e-06 | 0.019149 | 0.019149 | 0.019149 | 0.98993 | -0.19352 | 0.98972 | -0.19765 | 5.2606
61 | 0.042162 | 0.010626 | -0.04213 | -0.010606 | 3.1574e-05 | 1.9936e-05 | 0.063293 | 0.063293 | 0.063293 | 0.99155 | -0.16216 | 0.99074 | -0.17782 | 17.3882
62 | -0.084721 | -0.021319 | 0.084794 | 0.021366 | 7.2827e-05 | 4.6454e-05 | 0.12717 | 0.12717 | 0.12717 | 0.99155 | -0.16216 | 0.99248 | -0.14418 | 34.9373
63 | 0.0053964 | 0.0013491 | -0.0053917 | -0.0013485 | 4.6812e-06 | 5.8318e-07 | 0.0081309 | 0.0081317 | 0.0081317 | 0.98743 | -0.24207 | 0.9865 | -0.26032 | 2.234
64 | -0.0053869 | -0.0013479 | 0.0053917 | 0.0013485 | 4.8157e-06 | 6.0523e-07 | 0.0081326 | 0.0081317 | 0.0081326 | 0.98554 | -0.27911 | 0.9865 | -0.26032 | 2.2342
65 | 0.0053869 | 0.0013479 | -0.0053862 | -0.0013478 | 6.4352e-07 | 8.1284e-08 | 0.0081326 | 0.0081327 | 0.0081327 | 0.98554 | -0.27911 | 0.98541 | -0.28162 | 2.2343
66 | 0.003048 | 0.00076176 | -0.0030479 | -0.00076185 | 9.1862e-08 | -8.8562e-08 | 0.0046019 | 0.0046019 | 0.0046019 | 0.98541 | -0.28162 | 0.98538 | -0.28225 | 1.2643
67 | 0.20213 | 0.051466 | -0.20172 | -0.051205 | 0.0004098 | 0.0002609 | 0.30374 | 0.30374 | 0.30374 | 0.99116 | -0.16825 | 0.98897 | -0.21038 | 27.815
68 | 0.082172 | 0.020734 | -0.082033 | -0.020646 | 0.00013871 | 8.8459e-05 | 0.12341 | 0.12341 | 0.12341 | 0.99116 | -0.16825 | 0.98934 | -0.20356 | 33.9046
69 | -0.2843 | -0.0722 | 0.28512 | 0.072724 | 0.00082003 | 0.00052342 | 0.42715 | 0.42715 | 0.42715 | 0.99116 | -0.16825 | 0.99428 | -0.1085 | 39.1165
70 | 0.12196 | 0.031044 | -0.1219 | -0.031003 | 6.481e-05 | 4.0887e-05 | 0.18368 | 0.18368 | 0.18368 | 0.98897 | -0.21038 | 0.98839 | -0.22141 | 16.8206
71 | 0.079753 | 0.020161 | -0.079653 | -0.020097 | 9.9939e-05 | 6.3724e-05 | 0.12006 | 0.12006 | 0.12006 | 0.98897 | -0.21038 | 0.98761 | -0.23655 | 32.9834
72 | 0.060897 | 0.015346 | -0.06082 | -0.015297 | 7.6295e-05 | 4.8518e-05 | 0.091621 | 0.091622 | 0.091622 | 0.98934 | -0.20356 | 0.98798 | -0.22979 | 25.1708
73 | 0.021136 | 0.0053001 | -0.021133 | -0.0052983 | 2.9156e-06 | 1.7672e-06 | 0.031791 | 0.031791 | 0.031791 | 0.98934 | -0.20356 | 0.98919 | -0.20645 | 8.7339
74 | -0.29386 | -0.074915 | 0.29403 | 0.07502 | 0.0001633 | 0.00010425 | 0.44024 | 0.44024 | 0.44024 | 0.99428 | -0.1085 | 0.99489 | -0.096995 | 40.315
75 | 0.18186 | 0.046017 | -0.18166 | -0.045891 | 0.00019717 | 0.00012582 | 0.2711 | 0.2711 | 0.2711 | 0.99876 | -0.023721 | 0.99757 | -0.046339 | 37.2391
76 | -0.18186 | -0.046017 | 0.18207 | 0.046149 | 0.00020728 | 0.00013177 | 0.2711 | 0.2711 | 0.2711 | 0.99876 | -0.023721 | 1 | 0 | 24.8261
77 | 0.080821 | 0.02033 | -0.080664 | -0.02023 | 0.00015634 | 9.9684e-05 | 0.12058 | 0.12058 | 0.12058 | 0.99757 | -0.046339 | 0.99547 | -0.086917 | 33.1266
78 | 0.10084 | 0.025562 | -0.10079 | -0.025529 | 5.0543e-05 | 3.227e-05 | 0.15052 | 0.15052 | 0.15052 | 0.99757 | -0.046339 | 0.99703 | -0.056775 | 41.3517
79 | 0.33255 | 0.085266 | -0.33177 | -0.084768 | 0.00078023 | 0.00049835 | 0.49552 | 0.49552 | 0.49552 | 1 | 0 | 0.99744 | -0.04851 | 45.3773
80 | 0.055376 | 0.013933 | -0.055331 | -0.013904 | 4.5396e-05 | 2.8831e-05 | 0.083422 | 0.083422 | 0.083422 | 0.98798 | -0.22979 | 0.9871 | -0.24696 | 22.9181
81 | 0.017851 | 0.0044756 | -0.017847 | -0.0044736 | 3.4301e-06 | 2.0324e-06 | 0.026853 | 0.026853 | 0.026853 | 0.98919 | -0.20645 | 0.98898 | -0.21049 | 7.3773
82 | 0.1219 | 0.031003 | -0.12185 | -0.030969 | 5.477e-05 | 3.4553e-05 | 0.18368 | 0.18368 | 0.18368 | 0.98839 | -0.22141 | 0.98791 | -0.23074 | 16.8206
83 | 0.073611 | 0.018583 | -0.073528 | -0.01853 | 8.2726e-05 | 5.2715e-05 | 0.11096 | 0.11096 | 0.11096 | 0.98761 | -0.23655 | 0.9864 | -0.26003 | 30.4825
84 | 0.015749 | 0.0039484 | -0.015745 | -0.0039462 | 3.814e-06 | 2.2032e-06 | 0.023561 | 0.023561 | 0.023561 | 0.99466 | -0.1025 | 0.9944 | -0.10758 | 6.4729
85 | -0.015749 | -0.0039484 | 0.015752 | 0.0039502 | 3.1511e-06 | 1.8202e-06 | 0.023561 | 0.023561 | 0.023561 | 0.99466 | -0.1025 | 0.99488 | -0.0983 | 6.4729
86 | -0.042021 | -0.010534 | 0.042035 | 0.010543 | 1.4237e-05 | 8.9868e-06 | 0.06285 | 0.06285 | 0.06285 | 0.99488 | -0.0983 | 0.99525 | -0.091192 | 17.2665
87 | -0.031549 | -0.0079394 | 0.031551 | 0.0079407 | 2.0205e-06 | 1.2624e-06 | 0.047452 | 0.047452 | 0.047452 | 0.98958 | -0.20027 | 0.98965 | -0.19893 | 13.0362
88 | 0.0096652 | 0.0024227 | -0.0096626 | -0.0024215 | 2.5835e-06 | 1.2343e-06 | 0.014531 | 0.014532 | 0.014532 | 0.98972 | -0.19765 | 0.98943 | -0.20326 | 3.9922
89 | 0.039586 | 0.0099686 | -0.03957 | -0.0099584 | 1.6195e-05 | 1.0207e-05 | 0.059472 | 0.059472 | 0.059472 | 0.99074 | -0.17782 | 0.99029 | -0.18638 | 16.3385
90 | -0.087304 | -0.021995 | 0.087361 | 0.02203 | 5.6034e-05 | 3.5749e-05 | 0.13094 | 0.13094 | 0.13094 | 0.99248 | -0.14418 | 0.99317 | -0.13077 | 35.9713
91 | -0.0031501 | -0.00078949 | 0.0031503 | 0.00078936 | 1.5311e-07 | -1.3553e-07 | 0.0047382 | 0.0047381 | 0.0047382 | 0.98928 | -0.2062 | 0.98933 | -0.20518 | 1.3017
92 | -0.006258 | -0.0015682 | 0.0062586 | 0.0015684 | 5.7181e-07 | 1.4492e-07 | 0.0094124 | 0.0094123 | 0.0094124 | 0.98933 | -0.20518 | 0.98943 | -0.20326 | 2.5858
93 | -0.0044512 | -0.0011156 | 0.0044513 | 0.0011156 | 1.2702e-07 | -1.3872e-08 | 0.0067277 | 0.0067276 | 0.0067277 | 0.9845 | -0.29749 | 0.98453 | -0.29689 | 1.8483
94 | -0.0063131 | -0.0015822 | 0.0063131 | 0.0015822 | 9.0792e-09 | 2.4291e-09 | 0.0095415 | 0.0095415 | 0.0095415 | 0.98453 | -0.29689 | 0.98454 | -0.29686 | 2.6213
95 | 0.0018977 | 0.00047359 | -0.0018972 | -0.00047548 | 5.4008e-07 | -1.8881e-06 | 0.002865 | 0.0028658 | 0.0028658 | 0.98538 | -0.28225 | 0.98507 | -0.28824 | 0.78731
96 | -0.034241 | -0.0086149 | 0.034251 | 0.0086209 | 9.6808e-06 | 6.0706e-06 | 0.051496 | 0.051496 | 0.051496 | 0.98965 | -0.19893 | 0.98995 | -0.19302 | 14.1473
97 | -0.036888 | -0.0092819 | 0.0369 | 0.0092892 | 1.1699e-05 | 7.3567e-06 | 0.05546 | 0.05546 | 0.05546 | 0.98995 | -0.19302 | 0.99029 | -0.18638 | 15.2363
98 | -0.091869 | -0.02316 | 0.092022 | 0.023258 | 0.00015305 | 9.7671e-05 | 0.13769 | 0.13769 | 0.13769 | 0.99317 | -0.13077 | 0.99498 | -0.096024 | 37.827
99 | -0.046406 | -0.011633 | 0.04647 | 0.011673 | 6.4586e-05 | 4.0895e-05 | 0.070366 | 0.070366 | 0.070366 | 0.98134 | -0.35864 | 0.98284 | -0.32947 | 19.3314
100 | -0.052251 | -0.013122 | 0.0523 | 0.013153 | 4.9354e-05 | 3.132e-05 | 0.079117 | 0.079117 | 0.079117 | 0.98284 | -0.32947 | 0.98385 | -0.30969 | 21.7356
101 | -0.055615 | -0.013984 | 0.055639 | 0.013999 | 2.3642e-05 | 1.5018e-05 | 0.084131 | 0.084131 | 0.084131 | 0.98385 | -0.30969 | 0.98431 | -0.3008 | 23.113
102 | -0.058897 | -0.014816 | 0.058935 | 0.01484 | 3.8016e-05 | 2.4167e-05 | 0.089056 | 0.089056 | 0.089056 | 0.98431 | -0.3008 | 0.985 | -0.2873 | 24.466
103 | 0.0047199 | 0.0011828 | -0.0047196 | -0.0011828 | 2.4994e-07 | -6.7821e-09 | 0.0071314 | 0.0071315 | 0.0071315 | 0.98483 | -0.29122 | 0.98477 | -0.29234 | 1.9592
104 | -0.0047199 | -0.0011828 | 0.00472 | 0.0011828 | 1.3376e-07 | -3.6385e-09 | 0.0071314 | 0.0071314 | 0.0071314 | 0.98483 | -0.29122 | 0.98486 | -0.29063 | 1.9592
105 | -0.0060779 | -0.0015231 | 0.0060785 | 0.0015233 | 6.1904e-07 | 1.4705e-07 | 0.009183 | 0.0091829 | 0.009183 | 0.98486 | -0.29063 | 0.98497 | -0.28849 | 2.5228
106 | -0.30527 | -0.077837 | 0.30565 | 0.078079 | 0.00037914 | 0.00024209 | 0.45705 | 0.45705 | 0.45705 | 0.99489 | -0.096995 | 0.99624 | -0.071304 | 41.8546
107 | 0.074097 | 0.018584 | -0.074082 | -0.018574 | 1.5095e-05 | 9.6181e-06 | 0.11076 | 0.11076 | 0.11076 | 0.99547 | -0.086917 | 0.99525 | -0.091192 | 30.4296
108 | 0.10079 | 0.025529 | -0.1006 | -0.025408 | 0.00018961 | 0.00012106 | 0.15052 | 0.15052 | 0.15052 | 0.99703 | -0.056775 | 0.99498 | -0.096024 | 41.3517
109 | 0.33177 | 0.084768 | -0.3316 | -0.084663 | 0.00016437 | 0.00010499 | 0.49552 | 0.49552 | 0.49552 | 0.99744 | -0.04851 | 0.9969 | -0.058761 | 45.3773
110 | 0.050284 | 0.012639 | -0.050251 | -0.012618 | 3.3608e-05 | 2.131e-05 | 0.075815 | 0.075815 | 0.075815 | 0.9871 | -0.24696 | 0.98638 | -0.26097 | 20.8282
111 | 0.012986 | 0.0032553 | -0.012985 | -0.0032543 | 1.7272e-06 | 9.5062e-07 | 0.019539 | 0.019539 | 0.019539 | 0.98898 | -0.21049 | 0.98884 | -0.21328 | 5.368
112 | -0.0060306 | -0.0015114 | 0.0060308 | 0.0015115 | 1.8469e-07 | 4.1494e-08 | 0.0090753 | 0.0090753 | 0.0090753 | 0.9888 | -0.21392 | 0.98884 | -0.21328 | 2.4932
113 | 0.0069538 | 0.0017429 | -0.0069526 | -0.0017425 | 1.1978e-06 | 3.9247e-07 | 0.010464 | 0.010464 | 0.010464 | 0.98884 | -0.21328 | 0.98865 | -0.2169 | 2.8748
114 | 0.064958 | 0.016382 | -0.064874 | -0.016328 | 8.4648e-05 | 5.3875e-05 | 0.098028 | 0.098028 | 0.098028 | 0.9864 | -0.26003 | 0.985 | -0.2873 | 26.9308
115 | -0.046185 | -0.011621 | 0.046208 | 0.011636 | 2.3667e-05 | 1.4988e-05 | 0.070447 | 0.070447 | 0.070447 | 0.97577 | -0.46679 | 0.97631 | -0.45607 | 19.3536
116 | -0.049881 | -0.012556 | 0.049923 | 0.012582 | 4.1131e-05 | 2.6086e-05 | 0.076045 | 0.076045 | 0.076045 | 0.97631 | -0.45607 | 0.97719 | -0.43883 | 20.8915
117 | -0.0579 | -0.014582 | 0.057903 | 0.014584 | 3.0452e-06 | 1.9358e-06 | 0.088193 | 0.088193 | 0.088193 | 0.97719 | -0.43883 | 0.97725 | -0.43773 | 24.2288
118 | -0.061558 | -0.0155 | 0.061632 | 0.015547 | 7.3755e-05 | 4.6923e-05 | 0.093758 | 0.093758 | 0.093758 | 0.97725 | -0.43773 | 0.97853 | -0.41271 | 25.7576
119 | -0.066439 | -0.016752 | 0.066453 | 0.01676 | 1.399e-05 | 8.9078e-06 | 0.10107 | 0.10107 | 0.10107 | 0.97853 | -0.41271 | 0.97875 | -0.40831 | 27.7659
120 | -0.069575 | -0.017543 | 0.069612 | 0.017566 | 3.657e-05 | 2.3296e-05 | 0.10581 | 0.10581 | 0.10581 | 0.97875 | -0.40831 | 0.97931 | -0.39733 | 29.07
121 | -0.070593 | -0.017812 | 0.070632 | 0.017837 | 3.8957e-05 | 2.4819e-05 | 0.10731 | 0.10731 | 0.10731 | 0.97931 | -0.39733 | 0.9799 | -0.38581 | 29.4797
122 | -0.01133 | -0.0028395 | 0.011331 | 0.0028403 | 1.6155e-06 | 8.3849e-07 | 0.016933 | 0.016933 | 0.016933 | 0.99563 | -0.082999 | 0.99579 | -0.080007 | 4.6519
123 | -0.015791 | -0.0039581 | 0.015796 | 0.003961 | 5.0792e-06 | 2.9341e-06 | 0.023597 | 0.023597 | 0.023597 | 0.99579 | -0.080007 | 0.99614 | -0.073258 | 6.4828
124 | -0.015796 | -0.003961 | 0.015798 | 0.0039619 | 1.4708e-06 | 8.4963e-07 | 0.023597 | 0.023597 | 0.023597 | 0.99614 | -0.073258 | 0.99624 | -0.071304 | 6.4827
125 | -0.32145 | -0.082041 | 0.32164 | 0.082166 | 0.00019493 | 0.00012449 | 0.48065 | 0.48065 | 0.48065 | 0.99624 | -0.071304 | 0.9969 | -0.058761 | 44.0155
126 | 0.077038 | 0.019485 | -0.077002 | -0.019461 | 3.6645e-05 | 2.3363e-05 | 0.11687 | 0.11687 | 0.11687 | 0.98143 | -0.35608 | 0.98092 | -0.366 | 32.1063
127 | -0.075895 | -0.019156 | 0.075968 | 0.019202 | 7.2111e-05 | 4.5969e-05 | 0.1153 | 0.1153 | 0.1153 | 0.9799 | -0.38581 | 0.98092 | -0.366 | 31.6754
128 | -0.0088359 | -0.0022144 | 0.008836 | 0.0022144 | 5.919e-08 | 2.6607e-08 | 0.013349 | 0.013349 | 0.013349 | 0.98497 | -0.28849 | 0.98497 | -0.28835 | 3.6672
129 | -0.0099519 | -0.0024941 | 0.0099534 | 0.0024949 | 1.5593e-06 | 7.642e-07 | 0.015041 | 0.015041 | 0.015041 | 0.98454 | -0.29686 | 0.9847 | -0.29358 | 4.1322
130 | -0.013872 | -0.0034769 | 0.013873 | 0.0034777 | 1.3517e-06 | 7.6075e-07 | 0.020962 | 0.020962 | 0.020962 | 0.9847 | -0.29358 | 0.98481 | -0.29153 | 5.7589
131 | -0.021403 | -0.0053648 | 0.021412 | 0.0053705 | 9.2995e-06 | 5.6498e-06 | 0.032339 | 0.032339 | 0.032339 | 0.98481 | -0.29153 | 0.98528 | -0.28241 | 8.8845
132 | -0.024943 | -0.0062555 | 0.024944 | 0.006256 | 8.1322e-07 | 5.01e-07 | 0.037672 | 0.037672 | 0.037672 | 0.98528 | -0.28241 | 0.98531 | -0.28173 | 10.3495
133 | -0.028593 | -0.0071705 | 0.028596 | 0.0071724 | 3.0702e-06 | 1.909e-06 | 0.043183 | 0.043183 | 0.043183 | 0.98531 | -0.28173 | 0.98543 | -0.27948 | 11.8634
134 | 0.018368 | 0.0046057 | -0.018363 | -0.0046032 | 4.091e-06 | 2.4376e-06 | 0.027736 | 0.027736 | 0.027736 | 0.98543 | -0.27948 | 0.98519 | -0.28415 | 7.6199
135 | -0.046964 | -0.011778 | 0.047005 | 0.011804 | 4.1477e-05 | 2.6265e-05 | 0.070919 | 0.070919 | 0.070919 | 0.98543 | -0.27948 | 0.98638 | -0.26097 | 19.4832
136 | 0.016894 | 0.0042349 | -0.016894 | -0.0042348 | 2.2311e-07 | 1.3116e-07 | 0.025516 | 0.025516 | 0.025516 | 0.98519 | -0.28415 | 0.98517 | -0.28443 | 7.01
137 | 0.015741 | 0.0039458 | -0.015738 | -0.0039442 | 2.7738e-06 | 1.6086e-06 | 0.023775 | 0.023775 | 0.023775 | 0.98517 | -0.28443 | 0.98498 | -0.28813 | 6.5316
138 | 0.012482 | 0.0031282 | -0.012482 | -0.0031281 | 1.3181e-07 | 7.1778e-08 | 0.018856 | 0.018856 | 0.018856 | 0.98498 | -0.28813 | 0.98497 | -0.28835 | 5.1803

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.52872 | 0.13454

## res_load
| p_mw | q_mvar
0 | 0.0035906 | 0.00089988
1 | 0.0049976 | 0.0012525
2 | 0.0038629 | 0.00096813
3 | 0.0037296 | 0.00093473
4 | 0.0022164 | 0.00055548
5 | 0.0030382 | 0.00076144
6 | 0.0038979 | 0.0009769
7 | 0.0016163 | 0.00040509
8 | 0.0038762 | 0.00097147
9 | 0.0084367 | 0.0021144
10 | 0.0055411 | 0.0013887
11 | 0.0034246 | 0.00085828
12 | 0.0059301 | 0.0014862
13 | 0.0038705 | 0.00097005
14 | 0.00098439 | 0.00024671
15 | 0.0055965 | 0.0014026
16 | 0.0043702 | 0.0010953
17 | 0.002436 | 0.00061051
18 | 0.0048783 | 0.0012226
19 | 0.0050212 | 0.0012584
20 | 0.0018407 | 0.00046132
21 | 0.0041544 | 0.0010412
22 | 0.01487 | 0.0037268
23 | 0.0085259 | 0.0021368
24 | 0.0040855 | 0.0010239
25 | 0.0052895 | 0.0013257
26 | 0.0012209 | 0.00030599
27 | 0.0033668 | 0.00084379
28 | 0.0039455 | 0.00098885
29 | 0.0059133 | 0.001482
30 | 0.0039116 | 0.00098034
31 | 0.0023383 | 0.00058602
32 | 0.0087456 | 0.0021919
33 | 0.012451 | 0.0031205
34 | 0.0054443 | 0.0013645
35 | 0.0032827 | 0.00082271
36 | 0.0060421 | 0.0015143
37 | 0.0045054 | 0.0011292
38 | 0.015745 | 0.0039462
39 | 0.026268 | 0.0065835
40 | 0.0026884 | 0.00067378
41 | 0.0031151 | 0.00078072
42 | 0.003071 | 0.00076966
43 | 0.0025441 | 0.00063762
44 | 0.0025103 | 0.00062914
45 | 0.0031501 | 0.00078949
46 | 0.0031078 | 0.00077888
47 | 0.0044512 | 0.0011156
48 | 0.0018618 | 0.0004666
49 | 0.0011502 | 0.00028826
50 | 0.0018972 | 0.00047548
51 | 0.0026901 | 0.00067419
52 | 0.0026371 | 0.00066092
53 | 0.0026701 | 0.00066918
54 | 0.0045085 | 0.0011299
55 | 0.003404 | 0.00085312
56 | 0.031209 | 0.0078216
57 | 0.0057803 | 0.0014487
58 | 0.0033152 | 0.00083087
59 | 0.0032578 | 0.00081649
60 | 0.0047196 | 0.0011828
61 | 0.0013579 | 0.00034031
62 | 0.011241 | 0.0028174
63 | 0.0065675 | 0.001646
64 | 0.0050464 | 0.0012647
65 | 0.0048611 | 0.0012183
66 | 0.0060306 | 0.0015114
67 | 0.0085702 | 0.0021479
68 | 0.0081385 | 0.0020397
69 | 0.003673 | 0.00092054
70 | 0.0079775 | 0.0019993
71 | 0.0036548 | 0.00091599
72 | 0.0048073 | 0.0012048
73 | 0.0031222 | 0.00078251
74 | 0.00098144 | 0.00024597
75 | 0.008579 | 0.0021501
76 | 0.01133 | 0.0028395
77 | 0.0044599 | 0.0011177
78 | 0.032047 | 0.0080317
79 | 0.0099632 | 0.002497
80 | 0.0042969 | 0.0010769
81 | 0.0052632 | 0.0013191
82 | 0.0010342 | 0.0002592
83 | 0.0059389 | 0.0014884
84 | 0.0027574 | 0.00069108
85 | 0.0036388 | 0.00091197
86 | 0.0039185 | 0.00098206
87 | 0.0075297 | 0.0018871
88 | 0.0035311 | 0.00088498
89 | 0.0036489 | 0.0009145
90 | 0.0014697 | 0.00036835
91 | 0.0032453 | 0.00081336
92 | 0.001153 | 0.00028897
93 | 0.0032559 | 0.00081601
94 | 0.0036457 | 0.00091371
95 | 0.0069526 | 0.0017425

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1