## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-11_0_7_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-11_0_7_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-11_0_7_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-11_0_7_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-11_0_7_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-11_0_7_node_48 | 0.4 | n |  | TRUE
6 | bus_LV_261-11_0_7_node_75 | 0.4 | n |  | TRUE
7 | bus_LV_261-11_0_7_node_74 | 0.4 | n |  | TRUE
8 | bus_LV_261-11_0_7_node_73 | 0.4 | n |  | TRUE
9 | bus_LV_261-11_0_7_node_46 | 0.4 | n |  | TRUE
10 | bus_LV_261-11_0_7_node_47 | 0.4 | n |  | TRUE
11 | bus_LV_261-11_0_7_node_45 | 0.4 | n |  | TRUE
12 | bus_LV_261-11_0_7_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_261-11_0_7_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_261-11_0_7_node_20 | 0.4 | n |  | TRUE
15 | bus_LV_261-11_0_7_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_261-11_0_7_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_261-11_0_7_node_79 | 0.4 | n |  | TRUE
18 | bus_LV_261-11_0_7_node_40 | 0.4 | n |  | TRUE
19 | bus_LV_261-11_0_7_node_37 | 0.4 | n |  | TRUE
20 | bus_LV_261-11_0_7_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_261-11_0_7_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_261-11_0_7_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_261-11_0_7_node_70 | 0.4 | n |  | TRUE
24 | bus_LV_261-11_0_7_node_60 | 0.4 | n |  | TRUE
25 | bus_LV_261-11_0_7_node_12 | 0.4 | n |  | TRUE
26 | bus_LV_261-11_0_7_node_77 | 0.4 | n |  | TRUE
27 | bus_LV_261-11_0_7_node_78 | 0.4 | n |  | TRUE
28 | bus_LV_261-11_0_7_node_76 | 0.4 | n |  | TRUE
29 | bus_LV_261-11_0_7_node_13 | 0.4 | n |  | TRUE
30 | bus_LV_261-11_0_7_node_88 | 0.4 | n |  | TRUE
31 | bus_LV_261-11_0_7_node_14 | 0.4 | n |  | TRUE
32 | bus_LV_261-11_0_7_node_87 | 0.4 | n |  | TRUE
33 | bus_LV_261-11_0_7_node_62 | 0.4 | n |  | TRUE
34 | bus_LV_261-11_0_7_node_61 | 0.4 | n |  | TRUE
35 | bus_LV_261-11_0_7_node_16 | 0.4 | n |  | TRUE
36 | bus_LV_261-11_0_7_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_261-11_0_7_node_71 | 0.4 | n |  | TRUE
38 | bus_LV_261-11_0_7_node_19 | 0.4 | n |  | TRUE
39 | bus_LV_261-11_0_7_node_69 | 0.4 | n |  | TRUE
40 | bus_LV_261-11_0_7_node_90 | 0.4 | n |  | TRUE
41 | bus_LV_261-11_0_7_node_59 | 0.4 | n |  | TRUE
42 | bus_LV_261-11_0_7_node_23 | 0.4 | n |  | TRUE
43 | bus_LV_261-11_0_7_node_89 | 0.4 | n |  | TRUE
44 | bus_LV_261-11_0_7_node_22 | 0.4 | n |  | TRUE
45 | bus_LV_261-11_0_7_node_26 | 0.4 | n |  | TRUE
46 | bus_LV_261-11_0_7_node_27 | 0.4 | n |  | TRUE
47 | bus_LV_261-11_0_7_node_24 | 0.4 | n |  | TRUE
48 | bus_LV_261-11_0_7_node_83 | 0.4 | n |  | TRUE
49 | bus_LV_261-11_0_7_node_25 | 0.4 | n |  | TRUE
50 | bus_LV_261-11_0_7_node_67 | 0.4 | n |  | TRUE
51 | bus_LV_261-11_0_7_node_66 | 0.4 | n |  | TRUE
52 | bus_LV_261-11_0_7_node_28 | 0.4 | n |  | TRUE
53 | bus_LV_261-11_0_7_node_84 | 0.4 | n |  | TRUE
54 | bus_LV_261-11_0_7_node_82 | 0.4 | n |  | TRUE
55 | bus_LV_261-11_0_7_node_36 | 0.4 | n |  | TRUE
56 | bus_LV_261-11_0_7_node_58 | 0.4 | n |  | TRUE
57 | bus_LV_261-11_0_7_node_80 | 0.4 | n |  | TRUE
58 | bus_LV_261-11_0_7_node_56 | 0.4 | n |  | TRUE
59 | bus_LV_261-11_0_7_node_86 | 0.4 | n |  | TRUE
60 | bus_LV_261-11_0_7_node_68 | 0.4 | n |  | TRUE
61 | bus_LV_261-11_0_7_node_91 | 0.4 | n |  | TRUE
62 | bus_LV_261-11_0_7_node_57 | 0.4 | n |  | TRUE
63 | bus_LV_261-11_0_7_node_65 | 0.4 | n |  | TRUE
64 | bus_LV_261-11_0_7_node_29 | 0.4 | n |  | TRUE
65 | bus_LV_261-11_0_7_node_30 | 0.4 | n |  | TRUE
66 | bus_LV_261-11_0_7_node_31 | 0.4 | n |  | TRUE
67 | bus_LV_261-11_0_7_node_32 | 0.4 | n |  | TRUE
68 | bus_LV_261-11_0_7_node_33 | 0.4 | n |  | TRUE
69 | bus_LV_261-11_0_7_node_34 | 0.4 | n |  | TRUE
70 | bus_LV_261-11_0_7_node_41 | 0.4 | n |  | TRUE
71 | bus_LV_261-11_0_7_node_35 | 0.4 | n |  | TRUE
72 | bus_LV_261-11_0_7_node_53 | 0.4 | n |  | TRUE
73 | bus_LV_261-11_0_7_node_38 | 0.4 | n |  | TRUE
74 | bus_LV_261-11_0_7_node_44 | 0.4 | n |  | TRUE
75 | bus_LV_261-11_0_7_node_85 | 0.4 | n |  | TRUE
76 | bus_LV_261-11_0_7_node_42 | 0.4 | n |  | TRUE
77 | bus_LV_261-11_0_7_node_52 | 0.4 | n |  | TRUE
78 | bus_LV_261-11_0_7_node_43 | 0.4 | n |  | TRUE
79 | bus_LV_261-11_0_7_node_51 | 0.4 | n |  | TRUE
80 | bus_LV_261-11_0_7_node_54 | 0.4 | n |  | TRUE
81 | bus_LV_261-11_0_7_node_55 | 0.4 | n |  | TRUE
82 | bus_LV_261-11_0_7_node_72 | 0.4 | n |  | TRUE
83 | bus_LV_261-11_0_7_node_81 | 0.4 | n |  | TRUE
84 | bus_MV_524_0_node_148 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-11_0_7_load_0 | 0 | 0.0051974 | 0.0013026 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-11_0_7_load_1 | 1 | 0.0014836 | 0.00037183 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-11_0_7_load_2 | 2 | 0.0047389 | 0.0011877 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-11_0_7_load_3 | 3 | 0.0066089 | 0.0016564 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-11_0_7_load_73 | 8 | 0.0023437 | 0.00058738 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-11_0_7_load_47 | 10 | 0.006516 | 0.0016331 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-11_0_7_load_45 | 11 | 0.0040925 | 0.0010257 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-11_0_7_load_6 | 12 | 0.011111 | 0.0027846 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-11_0_7_load_79 | 17 | 0.012256 | 0.0030718 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-11_0_7_load_40 | 18 | 0.014244 | 0.0035698 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-11_0_7_load_37 | 19 | 0.001129 | 0.00028297 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-11_0_7_load_70 | 23 | 0.033167 | 0.0083124 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-11_0_7_load_60 | 24 | 0.0033528 | 0.00084028 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-11_0_7_load_77 | 26 | 0.0044213 | 0.0011081 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-11_0_7_load_78 | 27 | 0.024831 | 0.0062232 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-11_0_7_load_76 | 28 | 0.045091 | 0.011301 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-11_0_7_load_88 | 30 | 0.020159 | 0.0050524 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-11_0_7_load_87 | 32 | 0.0065881 | 0.0016511 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-11_0_7_load_62 | 33 | 0.045891 | 0.011501 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-11_0_7_load_61 | 34 | 0.0052737 | 0.0013217 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-11_0_7_load_71 | 37 | 0.02518 | 0.0063108 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-11_0_7_load_90 | 40 | 0.026361 | 0.0066068 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-11_0_7_load_59 | 41 | 0.0032846 | 0.00082321 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-11_0_7_load_89 | 43 | 0.0092407 | 0.0023159 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-11_0_7_load_83 | 48 | 0.077207 | 0.01935 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-11_0_7_load_67 | 50 | 0.0016494 | 0.00041339 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-11_0_7_load_66 | 51 | 0.0040152 | 0.0010063 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-11_0_7_load_84 | 53 | 0.023116 | 0.0057935 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-11_0_7_load_82 | 54 | 0.012996 | 0.0032571 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-11_0_7_load_58 | 56 | 0.0031461 | 0.00078849 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-11_0_7_load_80 | 57 | 0.028067 | 0.0070343 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-11_0_7_load_86 | 59 | 0.0078854 | 0.0019763 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-11_0_7_load_68 | 60 | 0.0056421 | 0.001414 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-11_0_7_load_91 | 61 | 0.0056147 | 0.0014072 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-11_0_7_load_57 | 62 | 0.0032605 | 0.00081717 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-11_0_7_load_65 | 63 | 0.0048655 | 0.0012194 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-11_0_7_load_29 | 64 | 0.0024444 | 0.00061263 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-11_0_7_load_30 | 65 | 0.0037959 | 0.00095134 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-11_0_7_load_31 | 66 | 0.0047822 | 0.0011985 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-11_0_7_load_32 | 67 | 0.00314 | 0.00078696 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-11_0_7_load_34 | 69 | 0.0021679 | 0.00054333 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-11_0_7_load_35 | 71 | 0.0024059 | 0.00060296 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-11_0_7_load_53 | 72 | 0.0024171 | 0.00060578 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-11_0_7_load_85 | 75 | 0.014856 | 0.0037234 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-11_0_7_load_42 | 76 | 0.017268 | 0.0043279 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-11_0_7_load_52 | 77 | 0.0033059 | 0.00082853 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-11_0_7_load_51 | 79 | 0.015051 | 0.0037722 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-11_0_7_load_54 | 80 | 0.011199 | 0.0028067 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-11_0_7_load_72 | 82 | 0.0091188 | 0.0022854 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-11_0_7_load_81 | 83 | 0.009108 | 0.0022827 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 20 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-11_0_7_line_0 |  | 0 | 1 | 0.015499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-11_0_7_line_1 |  | 0 | 2 | 0.0026705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-11_0_7_line_2 |  | 1 | 3 | 0.029288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-11_0_7_line_3 |  | 2 | 4 | 0.021749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-11_0_7_line_4 |  | 4 | 5 | 0.055183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-11_0_7_line_5 |  | 5 | 9 | 0.00208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-11_0_7_line_6 |  | 6 | 7 | 0.031761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-11_0_7_line_7 |  | 6 | 8 | 0.014231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-11_0_7_line_8 |  | 7 | 16 | 0.00264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-11_0_7_line_9 |  | 8 | 82 | 0.025528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-11_0_7_line_10 |  | 9 | 10 | 0.011329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-11_0_7_line_11 |  | 9 | 11 | 0.029445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-11_0_7_line_12 |  | 10 | 79 | 0.025088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-11_0_7_line_13 |  | 11 | 78 | 0.014478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-11_0_7_line_14 |  | 12 | 13 | 0.029033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-11_0_7_line_15 |  | 13 | 14 | 0.056816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_261-11_0_7_line_16 |  | 13 | 15 | 0.066282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_261-11_0_7_line_17 |  | 14 | 41 | 0.073683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_261-11_0_7_line_18 |  | 15 | 18 | 0.010304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-11_0_7_line_19 |  | 15 | 19 | 0.033623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_261-11_0_7_line_20 |  | 16 | 17 | 0.024169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-11_0_7_line_21 |  | 17 | 20 | 0.012211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-11_0_7_line_22 |  | 19 | 55 | 0.012626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_261-11_0_7_line_23 |  | 20 | 21 | 0.028159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_261-11_0_7_line_24 |  | 20 | 22 | 0.018577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_261-11_0_7_line_25 |  | 21 | 26 | 0.0032136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_261-11_0_7_line_26 |  | 22 | 23 | 0.014706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-11_0_7_line_27 |  | 22 | 24 | 0.071316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_261-11_0_7_line_28 |  | 23 | 39 | 0.0041398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-11_0_7_line_29 |  | 24 | 56 | 0.017923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_261-11_0_7_line_30 |  | 25 | 26 | 0.019807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_261-11_0_7_line_31 |  | 25 | 27 | 0.0101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-11_0_7_line_32 |  | 25 | 28 | 0.017646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_261-11_0_7_line_33 |  | 27 | 57 | 0.018836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-11_0_7_line_34 |  | 28 | 47 | 0.018564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_261-11_0_7_line_35 |  | 29 | 30 | 0.009695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-11_0_7_line_36 |  | 29 | 31 | 0.033426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-11_0_7_line_37 |  | 29 | 32 | 0.013761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-11_0_7_line_38 |  | 31 | 33 | 0.051676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-11_0_7_line_39 |  | 31 | 34 | 0.0056935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-11_0_7_line_40 |  | 32 | 44 | 0.013101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-11_0_7_line_41 |  | 34 | 58 | 0.0036134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-11_0_7_line_42 |  | 35 | 36 | 0.043736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-11_0_7_line_43 |  | 35 | 37 | 0.018315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-11_0_7_line_44 |  | 36 | 42 | 0.062091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_261-11_0_7_line_45 |  | 36 | 43 | 0.024226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_261-11_0_7_line_46 |  | 38 | 39 | 0.008134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-11_0_7_line_47 |  | 38 | 40 | 0.015624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-11_0_7_line_48 |  | 39 | 60 | 0.011558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-11_0_7_line_49 |  | 40 | 61 | 0.016304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-11_0_7_line_50 |  | 41 | 62 | 0.018062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_261-11_0_7_line_51 |  | 42 | 47 | 0.009866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
52 | LV_261-11_0_7_line_52 |  | 42 | 48 | 0.013669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-11_0_7_line_53 |  | 43 | 45 | 0.048377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-11_0_7_line_54 |  | 44 | 45 | 0.045788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-11_0_7_line_55 |  | 44 | 46 | 0.0089926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-11_0_7_line_56 |  | 46 | 51 | 0.022762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-11_0_7_line_57 |  | 48 | 52 | 0.020649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-11_0_7_line_58 |  | 49 | 50 | 0.019331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-11_0_7_line_59 |  | 49 | 51 | 0.016264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-11_0_7_line_60 |  | 50 | 59 | 0.017279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-11_0_7_line_61 |  | 52 | 53 | 0.003929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-11_0_7_line_62 |  | 52 | 54 | 0.016231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-11_0_7_line_63 |  | 55 | 71 | 0.023957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
64 | LV_261-11_0_7_line_64 |  | 56 | 62 | 0.017657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_261-11_0_7_line_65 |  | 57 | 83 | 0.012564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-11_0_7_line_66 |  | 58 | 63 | 0.0036166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-11_0_7_line_67 |  | 58 | 81 | 0.021445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-11_0_7_line_68 |  | 64 | 65 | 0.0022551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-11_0_7_line_69 |  | 64 | 66 | 0.021907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-11_0_7_line_70 |  | 65 | 67 | 0.013706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-11_0_7_line_71 |  | 66 | 68 | 0.0050343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-11_0_7_line_72 |  | 67 | 69 | 0.015756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-11_0_7_line_73 |  | 68 | 70 | 0.011503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-11_0_7_line_74 |  | 69 | 71 | 0.016296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-11_0_7_line_75 |  | 70 | 72 | 0.033139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-11_0_7_line_76 |  | 70 | 73 | 0.003132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-11_0_7_line_77 |  | 72 | 77 | 0.0071929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-11_0_7_line_78 |  | 73 | 74 | 0.014111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-11_0_7_line_79 |  | 73 | 75 | 0.035644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-11_0_7_line_80 |  | 74 | 76 | 0.0044501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_261-11_0_7_line_81 |  | 76 | 78 | 0.014964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-11_0_7_line_82 |  | 80 | 81 | 0.0179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-11_0_7_trafo_10 | 0.63 MVA 20/0.4 kV | 84 | 20 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2683457.6506 | 1252596.5197 | 2683449.2203 | 1252594.5257 | 2683442.5083 | 1252593.2298
1 | 2683457.6506 | 1252596.5197 | 2683460.2494 | 1252597.1344
2 | 2683413.7513 | 1252587.6777 | 2683442.5083 | 1252593.2298
3 | 2683481.4142 | 1252602.1404 | 2683460.2494 | 1252597.1344
4 | 2683481.4142 | 1252602.1404 | 2683479.7602 | 1252610.7903 | 2683442.5222 | 1252610.3321 | 2683438.0989 | 1252612.527 | 2683433.7694 | 1252612.3548
5 | 2683433.6872 | 1252614.433 | 2683433.7694 | 1252612.3548
6 | 2683489.6765 | 1252551.4076 | 2683461.9599 | 1252547.3919 | 2683461.1373 | 1252543.6442
7 | 2683489.6765 | 1252551.4076 | 2683499.4391 | 1252552.7128 | 2683500.0968 | 1252548.3522
8 | 2683461.1373 | 1252543.6442 | 2683460.5623 | 1252541.0675
9 | 2683500.0968 | 1252548.3522 | 2683523.7014 | 1252551.2203 | 2683525.4407 | 1252551.4109
10 | 2683433.6872 | 1252614.433 | 2683433.5576 | 1252617.7448 | 2683441.5416 | 1252618.4458
11 | 2683433.6872 | 1252614.433 | 2683425.6257 | 1252614.5307 | 2683418.7565 | 1252616.2353 | 2683414.92 | 1252619.1056 | 2683411.6657 | 1252625.6425 | 2683410.6529 | 1252627.6087
12 | 2683441.5416 | 1252618.4458 | 2683466.5333 | 1252620.6401
13 | 2683404.0229 | 1252640.4794 | 2683410.6529 | 1252627.6087
14 | 2683270.4721 | 1252557.828 | 2683294.3844 | 1252561.3556 | 2683299.1922 | 1252562.082
15 | 2683268.7228 | 1252512.6361 | 2683267.5059 | 1252512.2298 | 2683266.9049 | 1252512.0323 | 2683264.1285 | 1252515.1846 | 2683268.0749 | 1252517.9199 | 2683266.7823 | 1252526.119 | 2683270.4809 | 1252526.6158 | 2683270.0996 | 1252530.113 | 2683268.8236 | 1252541.4258 | 2683267.5055 | 1252552.5045 | 2683267.8702 | 1252553.944 | 2683268.8655 | 1252554.5474 | 2683270.9078 | 1252554.754 | 2683270.4721 | 1252557.828
16 | 2683270.4721 | 1252557.828 | 2683269.9197 | 1252561.6898 | 2683266.5673 | 1252562.332 | 2683267.4885 | 1252565.5251 | 2683271.581 | 1252584.697 | 2683273.4711 | 1252595.7319 | 2683275.8553 | 1252620.4618
17 | 2683268.7228 | 1252512.6361 | 2683276.8896 | 1252514.1854 | 2683341.7423 | 1252522.4003
18 | 2683275.8553 | 1252620.4618 | 2683279.1346 | 1252620.1854 | 2683282.6847 | 1252619.9685 | 2683285.8567 | 1252621.4141
19 | 2683275.8553 | 1252620.4618 | 2683277.857 | 1252654.0256
20 | 2683460.5623 | 1252541.0675 | 2683473.9411 | 1252520.9395
21 | 2683476.0452 | 1252509.2061 | 2683476.4161 | 1252514.482 | 2683474.0867 | 1252520.7205 | 2683473.9411 | 1252520.9395
22 | 2683278.4511 | 1252666.6329 | 2683278.469 | 1252664.287 | 2683277.857 | 1252654.0256
23 | 2683476.0452 | 1252509.2061 | 2683483.5263 | 1252503.1847 | 2683485.9086 | 1252501.228 | 2683489.2255 | 1252503.1094 | 2683497.8865 | 1252495.3034
24 | 2683461.4423 | 1252513.4369 | 2683463.6062 | 1252516.8032 | 2683476.0452 | 1252509.2061
25 | 2683497.8865 | 1252495.3034 | 2683500.6663 | 1252493.691
26 | 2683461.4423 | 1252513.4369 | 2683459.1425 | 1252510.0798 | 2683453.3334 | 1252501.17
27 | 2683461.4423 | 1252513.4369 | 2683456.9899 | 1252516.621 | 2683446.6746 | 1252524.0035 | 2683438.3118 | 1252528.3335 | 2683428.4135 | 1252530.7626 | 2683409.4094 | 1252530.7951 | 2683394.9755 | 1252529.0066
28 | 2683451.0907 | 1252497.6904 | 2683453.0035 | 1252500.664 | 2683453.3334 | 1252501.17
29 | 2683394.9755 | 1252529.0066 | 2683377.1888 | 1252526.8026
30 | 2683517.8003 | 1252483.7531 | 2683500.6663 | 1252493.691
31 | 2683517.8003 | 1252483.7531 | 2683523.5543 | 1252492.0537
32 | 2683517.8003 | 1252483.7531 | 2683526.8813 | 1252477.7433 | 2683532.577 | 1252474.1081
33 | 2683534.2852 | 1252507.5336 | 2683523.5543 | 1252492.0537
34 | 2683548.1173 | 1252463.9545 | 2683539.5462 | 1252469.6602 | 2683532.577 | 1252474.1081
35 | 2683425.6859 | 1252447.4171 | 2683415.9813 | 1252446.8023
36 | 2683400.0484 | 1252471.5077 | 2683403.0611 | 1252470.3381 | 2683408.2534 | 1252464.4512 | 2683410.8739 | 1252457.3717 | 2683411.9837 | 1252446.6348 | 2683415.9813 | 1252446.8023
37 | 2683415.9813 | 1252446.8023 | 2683416.3209 | 1252440.38 | 2683415.3952 | 1252439.6553 | 2683414.6761 | 1252438.7334 | 2683414.3516 | 1252437.6614 | 2683414.1337 | 1252436.5241 | 2683414.2196 | 1252433.8182
38 | 2683400.0484 | 1252471.5077 | 2683402.7552 | 1252473.8364 | 2683408.3605 | 1252476.1393 | 2683443.3228 | 1252469.4376 | 2683449.5843 | 1252467.9039
39 | 2683400.0484 | 1252471.5077 | 2683396.535 | 1252472.8592 | 2683394.6194 | 1252473.0877
40 | 2683415.5824 | 1252421.0106 | 2683414.5945 | 1252422.5646 | 2683414.2286 | 1252433.5343 | 2683414.2196 | 1252433.8182
41 | 2683391.0314 | 1252473.5156 | 2683394.6194 | 1252473.0877
42 | 2683521.1974 | 1252409.3118 | 2683522.2075 | 1252406.7241 | 2683518.4326 | 1252397.1859 | 2683508.4722 | 1252368.1459
43 | 2683508.4722 | 1252368.1459 | 2683501.1332 | 1252370.4998 | 2683497.0763 | 1252370.7873 | 2683492.8684 | 1252370.539 | 2683490.5454 | 1252370.4284
44 | 2683521.1974 | 1252409.3118 | 2683521.7421 | 1252411.3654 | 2683522.4662 | 1252414.0665 | 2683523.2407 | 1252416.9463 | 2683523.7209 | 1252418.7544 | 2683528.8489 | 1252421.7178 | 2683532.6091 | 1252428.02 | 2683535.2713 | 1252432.4386 | 2683538.1769 | 1252436.1935 | 2683552.1936 | 1252454.2714 | 2683553.2239 | 1252455.598 | 2683556.5375 | 1252458.7805
45 | 2683521.1974 | 1252409.3118 | 2683519.0686 | 1252410.4159 | 2683510.7215 | 1252410.4094 | 2683497.2609 | 1252409.6729
46 | 2683446.8947 | 1252490.715 | 2683451.0907 | 1252497.6904
47 | 2683446.8947 | 1252490.715 | 2683433.6895 | 1252499.0661
48 | 2683451.0907 | 1252497.6904 | 2683441.0656 | 1252503.4413
49 | 2683426.8629 | 1252510.6479 | 2683425.4128 | 1252504.3005 | 2683433.6895 | 1252499.0661
50 | 2683359.6661 | 1252524.6314 | 2683345.4235 | 1252522.8666 | 2683341.7423 | 1252522.4003
51 | 2683556.5375 | 1252458.7805 | 2683551.1495 | 1252461.9402 | 2683548.1173 | 1252463.9545
52 | 2683556.5375 | 1252458.7805 | 2683564.5851 | 1252469.829
53 | 2683448.9465 | 1252407.2478 | 2683463.9572 | 1252407.8375 | 2683472.1169 | 1252408.2972 | 2683497.2609 | 1252409.6729
54 | 2683415.5824 | 1252421.0106 | 2683417.2278 | 1252419.3993 | 2683419.6018 | 1252418.5654 | 2683428.6396 | 1252418.8373 | 2683429.0461 | 1252412.4827 | 2683429.4251 | 1252406.4724 | 2683448.9465 | 1252407.2478
55 | 2683406.6089 | 1252420.4617 | 2683411.2526 | 1252420.8496 | 2683415.5824 | 1252421.0106
56 | 2683406.6089 | 1252420.4617 | 2683404.6927 | 1252417.1878 | 2683399.2554 | 1252414.7428 | 2683386.2612 | 1252414.1752
57 | 2683576.7423 | 1252486.5196 | 2683564.5851 | 1252469.829
58 | 2683370.0128 | 1252413.4637 | 2683369.4749 | 1252425.3984 | 2683370.374 | 1252426.4007 | 2683370.1909 | 1252432.436
59 | 2683370.0128 | 1252413.4637 | 2683375.2096 | 1252413.6925 | 2683386.2612 | 1252414.1752
60 | 2683370.1909 | 1252432.436 | 2683367.3253 | 1252435.4868 | 2683361.9138 | 1252435.4996 | 2683361.1468 | 1252434.766 | 2683354.532 | 1252434.4872
61 | 2683573.5402 | 1252488.8095 | 2683576.7423 | 1252486.5196
62 | 2683576.7423 | 1252486.5196 | 2683580.0738 | 1252491.1033 | 2683586.3714 | 1252499.5856
63 | 2683278.4511 | 1252666.6329 | 2683302.336 | 1252668.4934
64 | 2683359.6661 | 1252524.6314 | 2683377.1888 | 1252526.8026
65 | 2683541.0778 | 1252517.3065 | 2683537.442 | 1252515.0313 | 2683536.3658 | 1252510.5349 | 2683534.2852 | 1252507.5336
66 | 2683391.0314 | 1252473.5156 | 2683390.9314 | 1252469.9004
67 | 2683370.1009 | 1252469.9184 | 2683377.7044 | 1252472.3494 | 2683382.0745 | 1252473.4006 | 2683387.15 | 1252473.6722 | 2683391.0314 | 1252473.5156
68 | 2683350.204 | 1252672.2221 | 2683347.9556 | 1252672.0469
69 | 2683372.0451 | 1252673.9234 | 2683350.204 | 1252672.2221
70 | 2683347.9556 | 1252672.0469 | 2683334.2909 | 1252670.9825
71 | 2683377.0642 | 1252674.3143 | 2683372.0451 | 1252673.9234
72 | 2683318.5828 | 1252669.759 | 2683334.2909 | 1252670.9825
73 | 2683377.0642 | 1252674.3143 | 2683380.9441 | 1252673.724 | 2683384.7526 | 1252672.3099 | 2683387.5529 | 1252670.1366
74 | 2683302.336 | 1252668.4934 | 2683318.5828 | 1252669.759
75 | 2683387.5529 | 1252670.1366 | 2683389.4144 | 1252667.1049 | 2683399.1936 | 1252645.2484 | 2683401.5375 | 1252640.122
76 | 2683390.5194 | 1252671.168 | 2683387.5529 | 1252670.1366
77 | 2683404.7001 | 1252633.6616 | 2683401.5375 | 1252640.122 | 2683401.5375 | 1252640.122
78 | 2683390.5194 | 1252671.168 | 2683396.0756 | 1252658.192
79 | 2683390.5194 | 1252671.168 | 2683396.0245 | 1252673.0691 | 2683414.1868 | 1252676.5051 | 2683425.2783 | 1252678.8451
80 | 2683396.0756 | 1252658.192 | 2683397.8973 | 1252654.1318
81 | 2683404.0229 | 1252640.4794 | 2683397.8973 | 1252654.1318
82 | 2683370.1009 | 1252469.9184 | 2683364.5015 | 1252468.2717 | 2683352.5436 | 1252466.6801

## bus_geodata
| x | y | coords
0 | 2683457.6506 | 1252596.5197
1 | 2683442.5083 | 1252593.2298
2 | 2683460.2494 | 1252597.1344
3 | 2683413.7513 | 1252587.6777
4 | 2683481.4142 | 1252602.1404
5 | 2683433.7694 | 1252612.3548
6 | 2683489.6765 | 1252551.4076
7 | 2683461.1373 | 1252543.6442
8 | 2683500.0968 | 1252548.3522
9 | 2683433.6872 | 1252614.433
10 | 2683441.5416 | 1252618.4458
11 | 2683410.6529 | 1252627.6087
12 | 2683299.1922 | 1252562.082
13 | 2683270.4721 | 1252557.828
14 | 2683268.7228 | 1252512.6361
15 | 2683275.8553 | 1252620.4618
16 | 2683460.5623 | 1252541.0675
17 | 2683473.9411 | 1252520.9395
18 | 2683285.8567 | 1252621.4141
19 | 2683277.857 | 1252654.0256
20 | 2683476.0452 | 1252509.2061
21 | 2683497.8865 | 1252495.3034
22 | 2683461.4423 | 1252513.4369
23 | 2683453.3334 | 1252501.17
24 | 2683394.9755 | 1252529.0066
25 | 2683517.8003 | 1252483.7531
26 | 2683500.6663 | 1252493.691
27 | 2683523.5543 | 1252492.0537
28 | 2683532.577 | 1252474.1081
29 | 2683415.9813 | 1252446.8023
30 | 2683425.6859 | 1252447.4171
31 | 2683400.0484 | 1252471.5077
32 | 2683414.2196 | 1252433.8182
33 | 2683449.5843 | 1252467.9039
34 | 2683394.6194 | 1252473.0877
35 | 2683508.4722 | 1252368.1459
36 | 2683521.1974 | 1252409.3118
37 | 2683490.5454 | 1252370.4284
38 | 2683446.8947 | 1252490.715
39 | 2683451.0907 | 1252497.6904
40 | 2683433.6895 | 1252499.0661
41 | 2683341.7423 | 1252522.4003
42 | 2683556.5375 | 1252458.7805
43 | 2683497.2609 | 1252409.6729
44 | 2683415.5824 | 1252421.0106
45 | 2683448.9465 | 1252407.2478
46 | 2683406.6089 | 1252420.4617
47 | 2683548.1173 | 1252463.9545
48 | 2683564.5851 | 1252469.829
49 | 2683370.0128 | 1252413.4637
50 | 2683370.1909 | 1252432.436
51 | 2683386.2612 | 1252414.1752
52 | 2683576.7423 | 1252486.5196
53 | 2683573.5402 | 1252488.8095
54 | 2683586.3714 | 1252499.5856
55 | 2683278.4511 | 1252666.6329
56 | 2683377.1888 | 1252526.8026
57 | 2683534.2852 | 1252507.5336
58 | 2683391.0314 | 1252473.5156
59 | 2683354.532 | 1252434.4872
60 | 2683441.0656 | 1252503.4413
61 | 2683426.8629 | 1252510.6479
62 | 2683359.6661 | 1252524.6314
63 | 2683390.9314 | 1252469.9004
64 | 2683350.204 | 1252672.2221
65 | 2683347.9556 | 1252672.0469
66 | 2683372.0451 | 1252673.9234
67 | 2683334.2909 | 1252670.9825
68 | 2683377.0642 | 1252674.3143
69 | 2683318.5828 | 1252669.759
70 | 2683387.5529 | 1252670.1366
71 | 2683302.336 | 1252668.4934
72 | 2683401.5375 | 1252640.122
73 | 2683390.5194 | 1252671.168
74 | 2683396.0756 | 1252658.192
75 | 2683425.2783 | 1252678.8451
76 | 2683397.8973 | 1252654.1318
77 | 2683404.7001 | 1252633.6616
78 | 2683404.0229 | 1252640.4794
79 | 2683466.5333 | 1252620.6401
80 | 2683352.5436 | 1252466.6801
81 | 2683370.1009 | 1252469.9184
82 | 2683525.4407 | 1252551.4109
83 | 2683541.0778 | 1252517.3065
84 | 2683485.9086 | 1252501.228

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97123 | -0.55516 | 0.0051974 | 0.0013026
1 | 0.97111 | -0.55748 | 0.0014836 | 0.00037183
2 | 0.97126 | -0.55451 | 0.0047389 | 0.0011877
3 | 0.97093 | -0.56106 | 0.0066089 | 0.0016564
4 | 0.97163 | -0.54726 | 0 | 0
5 | 0.97256 | -0.52891 | 0 | 0
6 | 0.99913 | -0.016767 | 0 | 0
7 | 0.99946 | -0.010412 | 0 | 0
8 | 0.99898 | -0.019616 | 0.0023437 | 0.00058738
9 | 0.97259 | -0.52822 | 0 | 0
10 | 0.97236 | -0.53272 | 0.006516 | 0.0016331
11 | 0.97368 | -0.50676 | 0.0040925 | 0.0010257
12 | 0.98808 | -0.22667 | 0.011111 | 0.0027846
13 | 0.98838 | -0.22091 | 0 | 0
14 | 0.99061 | -0.17817 | 0 | 0
15 | 0.986 | -0.26662 | 0 | 0
16 | 0.99949 | -0.0098837 | 0 | 0
17 | 0.99974 | -0.0050502 | 0.012256 | 0.0030718
18 | 0.98587 | -0.26925 | 0.014244 | 0.0035698
19 | 0.98494 | -0.28702 | 0.001129 | 0.00028297
20 | 1 | 0 | -0.6108 | -0.15577
21 | 0.99683 | -0.060202 | 0 | 0
22 | 0.9988 | -0.022762 | 0 | 0
23 | 0.99785 | -0.040966 | 0.033167 | 0.0083124
24 | 0.99571 | -0.081026 | 0.0033528 | 0.00084028
25 | 0.99426 | -0.10919 | 0 | 0
26 | 0.99646 | -0.067097 | 0.0044213 | 0.0011081
27 | 0.99369 | -0.12024 | 0.024831 | 0.0062232
28 | 0.99263 | -0.14039 | 0.045091 | 0.011301
29 | 0.97462 | -0.48867 | 0 | 0
30 | 0.97444 | -0.49226 | 0.020159 | 0.0050524
31 | 0.97252 | -0.53 | 0 | 0
32 | 0.97574 | -0.46663 | 0.0065881 | 0.0016511
33 | 0.97031 | -0.5738 | 0.045891 | 0.011501
34 | 0.97241 | -0.53224 | 0.0052737 | 0.0013217
35 | 0.98665 | -0.25534 | 0 | 0
36 | 0.98766 | -0.23564 | 0 | 0
37 | 0.98622 | -0.2636 | 0.02518 | 0.0063108
38 | 0.99747 | -0.048248 | 0 | 0
39 | 0.99771 | -0.043693 | 0 | 0
40 | 0.99702 | -0.057004 | 0.026361 | 0.0066068
41 | 0.9935 | -0.12302 | 0.0032846 | 0.00082321
42 | 0.99039 | -0.18329 | 0 | 0
43 | 0.98634 | -0.26095 | 0.0092407 | 0.0023159
44 | 0.97689 | -0.44412 | 0 | 0
45 | 0.98148 | -0.35461 | 0 | 0
46 | 0.97678 | -0.44634 | 0 | 0
47 | 0.99117 | -0.16838 | 0 | 0
48 | 0.98897 | -0.21085 | 0.077207 | 0.01935
49 | 0.97635 | -0.45482 | 0 | 0
50 | 0.97618 | -0.45819 | 0.0016494 | 0.00041339
51 | 0.97649 | -0.45198 | 0.0040152 | 0.0010063
52 | 0.98829 | -0.22415 | 0 | 0
53 | 0.9882 | -0.22577 | 0.023116 | 0.0057935
54 | 0.98809 | -0.22791 | 0.012996 | 0.0032571
55 | 0.98455 | -0.29461 | 0 | 0
56 | 0.99496 | -0.095372 | 0.0031461 | 0.00078849
57 | 0.99305 | -0.13261 | 0.028067 | 0.0070343
58 | 0.97235 | -0.53331 | 0 | 0
59 | 0.97605 | -0.46068 | 0.0078854 | 0.0019763
60 | 0.99765 | -0.044835 | 0.0056421 | 0.001414
61 | 0.99694 | -0.05861 | 0.0056147 | 0.0014072
62 | 0.99423 | -0.1092 | 0.0032605 | 0.00081717
63 | 0.97234 | -0.53363 | 0.0048655 | 0.0012194
64 | 0.97917 | -0.39898 | 0.0024444 | 0.00061263
65 | 0.97936 | -0.39535 | 0.0037959 | 0.00095134
66 | 0.97741 | -0.43343 | 0.0047822 | 0.0011985
67 | 0.98054 | -0.37232 | 0.00314 | 0.00078696
68 | 0.97703 | -0.44092 | 0 | 0
69 | 0.98195 | -0.34502 | 0.0021679 | 0.00054333
70 | 0.97616 | -0.45806 | 0 | 0
71 | 0.98343 | -0.31623 | 0.0024059 | 0.00060296
72 | 0.97598 | -0.46153 | 0.0024171 | 0.00060578
73 | 0.97594 | -0.46241 | 0 | 0
74 | 0.97513 | -0.47816 | 0 | 0
75 | 0.97544 | -0.4721 | 0.014856 | 0.0037234
76 | 0.97488 | -0.48314 | 0.017268 | 0.0043279
77 | 0.97596 | -0.46197 | 0.0033059 | 0.00082853
78 | 0.97427 | -0.49513 | 0 | 0
79 | 0.97201 | -0.53969 | 0.015051 | 0.0037722
80 | 0.97194 | -0.54144 | 0.011199 | 0.0028067
81 | 0.97213 | -0.53774 | 0 | 0
82 | 0.99877 | -0.023683 | 0.0091188 | 0.0022854
83 | 0.99294 | -0.13463 | 0.009108 | 0.0022827
84 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0080946 | 0.0020289 | -0.0080937 | -0.0020285 | 8.9392e-07 | 3.8033e-07 | 0.012402 | 0.012402 | 0.012402 | 0.97123 | -0.55516 | 0.97111 | -0.55748 | 3.4071
1 | -0.013292 | -0.0033315 | 0.013292 | 0.0033318 | 4.1532e-07 | 2.3275e-07 | 0.020365 | 0.020365 | 0.020365 | 0.97123 | -0.55516 | 0.97126 | -0.55451 | 5.5947
2 | 0.0066101 | 0.0016567 | -0.0066089 | -0.0016564 | 1.1267e-06 | 3.5881e-07 | 0.010128 | 0.010129 | 0.010129 | 0.97111 | -0.55748 | 0.97093 | -0.56106 | 2.7826
3 | -0.018031 | -0.0045194 | 0.018038 | 0.0045231 | 6.2239e-06 | 3.714e-06 | 0.027625 | 0.027625 | 0.027625 | 0.97126 | -0.55451 | 0.97163 | -0.54726 | 7.5892
4 | -0.018038 | -0.0045231 | 0.018053 | 0.0045326 | 1.5792e-05 | 9.4226e-06 | 0.027625 | 0.027625 | 0.027625 | 0.97163 | -0.54726 | 0.97256 | -0.52891 | 7.5892
5 | -0.018053 | -0.0045326 | 0.018054 | 0.0045329 | 5.9523e-07 | 3.5513e-07 | 0.027625 | 0.027624 | 0.027625 | 0.97256 | -0.52891 | 0.97259 | -0.52822 | 7.5892
6 | -0.011466 | -0.0028744 | 0.011469 | 0.0028762 | 3.4731e-06 | 1.8067e-06 | 0.017076 | 0.017076 | 0.017076 | 0.99913 | -0.016767 | 0.99946 | -0.010412 | 4.6913
7 | 0.011466 | 0.0028744 | -0.011464 | -0.0028736 | 1.5562e-06 | 8.0961e-07 | 0.017076 | 0.017076 | 0.017076 | 0.99913 | -0.016767 | 0.99898 | -0.019616 | 4.6913
8 | -0.011469 | -0.0028762 | 0.01147 | 0.0028763 | 2.8868e-07 | 1.5016e-07 | 0.017076 | 0.017076 | 0.017076 | 0.99946 | -0.010412 | 0.99949 | -0.0098837 | 4.6913
9 | 0.0091205 | 0.0022862 | -0.0091188 | -0.0022854 | 1.7669e-06 | 7.9663e-07 | 0.013585 | 0.013586 | 0.013586 | 0.99898 | -0.019616 | 0.99877 | -0.023683 | 3.7323
10 | 0.021577 | 0.005411 | -0.021572 | -0.0054082 | 4.6301e-06 | 2.8227e-06 | 0.033013 | 0.033013 | 0.033013 | 0.97259 | -0.52822 | 0.97236 | -0.53272 | 9.0695
11 | -0.039631 | -0.0099439 | 0.039672 | 0.0099696 | 4.06e-05 | 2.5618e-05 | 0.060637 | 0.060637 | 0.060637 | 0.97259 | -0.52822 | 0.97368 | -0.50676 | 16.6586
12 | 0.015056 | 0.0037751 | -0.015051 | -0.0037722 | 4.9948e-06 | 2.8856e-06 | 0.023042 | 0.023042 | 0.023042 | 0.97236 | -0.53272 | 0.97201 | -0.53969 | 6.3301
13 | -0.043764 | -0.010995 | 0.043788 | 0.011011 | 2.4293e-05 | 1.5367e-05 | 0.066892 | 0.066891 | 0.066892 | 0.97368 | -0.50676 | 0.97427 | -0.49513 | 18.3768
14 | -0.011111 | -0.0027846 | 0.011114 | 0.0027862 | 3.0482e-06 | 1.5788e-06 | 0.016732 | 0.016732 | 0.016732 | 0.98808 | -0.22667 | 0.98838 | -0.22091 | 4.5968
15 | -0.12809 | -0.032612 | 0.12836 | 0.032779 | 0.00026461 | 0.00016716 | 0.19302 | 0.19302 | 0.19302 | 0.98838 | -0.22091 | 0.99061 | -0.17817 | 17.6762
16 | 0.11698 | 0.029826 | -0.11672 | -0.029663 | 0.0002575 | 0.00016226 | 0.17629 | 0.17629 | 0.17629 | 0.98838 | -0.22091 | 0.986 | -0.26662 | 16.1441
17 | -0.12836 | -0.032779 | 0.1287 | 0.032996 | 0.00034316 | 0.00021677 | 0.19302 | 0.19302 | 0.19302 | 0.99061 | -0.17817 | 0.9935 | -0.12302 | 17.6762
18 | 0.014245 | 0.0035708 | -0.014244 | -0.0035698 | 1.7859e-06 | 1.0116e-06 | 0.021499 | 0.021499 | 0.021499 | 0.986 | -0.26662 | 0.98587 | -0.26925 | 5.9062
19 | 0.10247 | 0.026092 | -0.10237 | -0.026029 | 0.00010071 | 6.3168e-05 | 0.15479 | 0.1548 | 0.1548 | 0.986 | -0.26662 | 0.98494 | -0.28702 | 14.1754
20 | -0.01147 | -0.0028763 | 0.011472 | 0.0028777 | 2.6428e-06 | 1.3746e-06 | 0.017076 | 0.017076 | 0.017076 | 0.99949 | -0.0098837 | 0.99974 | -0.0050502 | 4.6913
21 | -0.023729 | -0.0059495 | 0.023734 | 0.0059529 | 5.7121e-06 | 3.4956e-06 | 0.035319 | 0.035319 | 0.035319 | 0.99974 | -0.0050502 | 1 | 0 | 9.7029
22 | 0.10124 | 0.025746 | -0.10121 | -0.025723 | 3.6987e-05 | 2.319e-05 | 0.15309 | 0.15309 | 0.15309 | 0.98494 | -0.28702 | 0.98455 | -0.29461 | 14.0192
23 | 0.37189 | 0.09518 | -0.37081 | -0.094489 | 0.0010806 | 0.00069049 | 0.55408 | 0.55408 | 0.55408 | 1 | 0 | 0.99683 | -0.060202 | 50.7399
24 | 0.21353 | 0.054639 | -0.21329 | -0.05449 | 0.00023502 | 0.00014968 | 0.31813 | 0.31813 | 0.31813 | 1 | 0 | 0.9988 | -0.022762 | 29.133
25 | 0.37081 | 0.094489 | -0.37069 | -0.09441 | 0.00012332 | 7.8801e-05 | 0.55408 | 0.55408 | 0.55408 | 0.99683 | -0.060202 | 0.99646 | -0.067097 | 50.7399
26 | 0.070873 | 0.017795 | -0.070811 | -0.017756 | 6.1493e-05 | 3.9163e-05 | 0.1056 | 0.1056 | 0.1056 | 0.9988 | -0.022762 | 0.99785 | -0.040966 | 29.0105
27 | 0.14242 | 0.036694 | -0.14202 | -0.036439 | 0.00040268 | 0.00025493 | 0.21254 | 0.21254 | 0.21254 | 0.9988 | -0.022762 | 0.99571 | -0.081026 | 19.4631
28 | 0.037644 | 0.0094439 | -0.037639 | -0.0094408 | 4.8926e-06 | 3.0772e-06 | 0.056139 | 0.056139 | 0.056139 | 0.99785 | -0.040966 | 0.99771 | -0.043693 | 15.4228
29 | 0.13867 | 0.035599 | -0.13857 | -0.035538 | 9.6485e-05 | 6.1052e-05 | 0.20753 | 0.20753 | 0.20753 | 0.99571 | -0.081026 | 0.99496 | -0.095372 | 19.0043
30 | -0.36552 | -0.092828 | 0.36627 | 0.093302 | 0.00074211 | 0.00047418 | 0.54748 | 0.54748 | 0.54748 | 0.99426 | -0.10919 | 0.99646 | -0.067097 | 50.1353
31 | 0.062061 | 0.015575 | -0.062029 | -0.015554 | 3.2679e-05 | 2.0784e-05 | 0.092889 | 0.092889 | 0.092889 | 0.99426 | -0.10919 | 0.99369 | -0.12024 | 25.5189
32 | 0.30346 | 0.077253 | -0.30301 | -0.076962 | 0.00045583 | 0.00029105 | 0.45459 | 0.45459 | 0.45459 | 0.99426 | -0.10919 | 0.99263 | -0.14039 | 41.6291
33 | 0.037198 | 0.0093311 | -0.037176 | -0.0093174 | 2.1918e-05 | 1.3784e-05 | 0.055706 | 0.055706 | 0.055706 | 0.99369 | -0.12024 | 0.99305 | -0.13261 | 15.3038
34 | 0.25792 | 0.065661 | -0.25757 | -0.065439 | 0.00034754 | 0.0002217 | 0.387 | 0.387 | 0.387 | 0.99263 | -0.14039 | 0.99117 | -0.16838 | 35.4392
35 | 0.020163 | 0.0050545 | -0.020159 | -0.0050524 | 3.4454e-06 | 2.0843e-06 | 0.030784 | 0.030784 | 0.030784 | 0.97462 | -0.48867 | 0.97444 | -0.49226 | 8.4573
36 | 0.067466 | 0.016999 | -0.067333 | -0.016914 | 0.00013307 | 8.4752e-05 | 0.10304 | 0.10304 | 0.10304 | 0.97462 | -0.48867 | 0.97252 | -0.53 | 28.3069
37 | -0.087629 | -0.022053 | 0.087721 | 0.022112 | 9.2415e-05 | 5.8974e-05 | 0.13382 | 0.13382 | 0.13382 | 0.97462 | -0.48867 | 0.97574 | -0.46663 | 36.7641
38 | 0.045987 | 0.011562 | -0.045891 | -0.011501 | 9.5978e-05 | 6.0786e-05 | 0.070376 | 0.070376 | 0.070376 | 0.97252 | -0.53 | 0.97031 | -0.5738 | 19.3341
39 | 0.021346 | 0.005352 | -0.021343 | -0.0053506 | 2.2776e-06 | 1.387e-06 | 0.032661 | 0.032661 | 0.032661 | 0.97252 | -0.53 | 0.97241 | -0.53224 | 8.9728
40 | -0.094309 | -0.023764 | 0.094411 | 0.023828 | 0.00010169 | 6.4917e-05 | 0.14387 | 0.14387 | 0.14387 | 0.97574 | -0.46663 | 0.97689 | -0.44412 | 39.5242
41 | 0.01607 | 0.0040289 | -0.016069 | -0.0040284 | 8.1942e-07 | 4.7961e-07 | 0.024591 | 0.024591 | 0.024591 | 0.97241 | -0.53224 | 0.97235 | -0.53331 | 6.7558
42 | -0.02519 | -0.0063169 | 0.025214 | 0.0063315 | 2.3673e-05 | 1.4592e-05 | 0.037992 | 0.037992 | 0.037992 | 0.98665 | -0.25534 | 0.98766 | -0.23564 | 10.4374
43 | 0.02519 | 0.0063169 | -0.02518 | -0.0063108 | 9.9136e-06 | 6.1109e-06 | 0.037992 | 0.037992 | 0.037992 | 0.98665 | -0.25534 | 0.98622 | -0.2636 | 10.4374
44 | -0.14352 | -0.036579 | 0.14389 | 0.036809 | 0.00036364 | 0.00023034 | 0.21645 | 0.21645 | 0.21645 | 0.98766 | -0.23564 | 0.99039 | -0.18329 | 19.8218
45 | 0.11831 | 0.030247 | -0.11817 | -0.030155 | 0.00014467 | 9.1969e-05 | 0.17846 | 0.17846 | 0.17846 | 0.98766 | -0.23564 | 0.98634 | -0.26095 | 24.514
46 | -0.03199 | -0.0080224 | 0.031997 | 0.0080267 | 6.9471e-06 | 4.34e-06 | 0.047724 | 0.047724 | 0.047724 | 0.99747 | -0.048248 | 0.99771 | -0.043693 | 13.1109
47 | 0.03199 | 0.0080224 | -0.031977 | -0.008014 | 1.3344e-05 | 8.3366e-06 | 0.047724 | 0.047724 | 0.047724 | 0.99747 | -0.048248 | 0.99702 | -0.057004 | 13.1109
48 | 0.0056424 | 0.0014141 | -0.0056421 | -0.001414 | 3.0692e-07 | 4.5507e-08 | 0.0084152 | 0.0084153 | 0.0084153 | 0.99771 | -0.043693 | 0.99765 | -0.044835 | 2.3119
49 | 0.0056151 | 0.0014072 | -0.0056147 | -0.0014072 | 4.2939e-07 | 6.2205e-08 | 0.0083804 | 0.0083804 | 0.0083804 | 0.99702 | -0.057004 | 0.99694 | -0.05861 | 2.3023
50 | -0.13198 | -0.033819 | 0.13207 | 0.033875 | 8.8462e-05 | 5.5913e-05 | 0.19794 | 0.19794 | 0.19794 | 0.9935 | -0.12302 | 0.99423 | -0.1092 | 18.1266
51 | -0.25738 | -0.065322 | 0.25757 | 0.065439 | 0.0001847 | 0.00011783 | 0.387 | 0.387 | 0.387 | 0.99039 | -0.18329 | 0.99117 | -0.16838 | 35.4392
52 | 0.11349 | 0.028512 | -0.11335 | -0.028417 | 0.00014909 | 9.5239e-05 | 0.17054 | 0.17054 | 0.17054 | 0.99039 | -0.18329 | 0.98897 | -0.21085 | 46.8529
53 | 0.10893 | 0.02784 | -0.10843 | -0.027526 | 0.00049103 | 0.00031365 | 0.16452 | 0.16452 | 0.16452 | 0.98634 | -0.26095 | 0.98148 | -0.35461 | 45.1983
54 | -0.10797 | -0.027229 | 0.10843 | 0.027526 | 0.00046476 | 0.00029687 | 0.16452 | 0.16452 | 0.16452 | 0.97689 | -0.44412 | 0.98148 | -0.35461 | 45.1983
55 | 0.013559 | 0.0034006 | -0.013557 | -0.0033997 | 1.4386e-06 | 8.081e-07 | 0.020654 | 0.020654 | 0.020654 | 0.97689 | -0.44412 | 0.97678 | -0.44634 | 5.6742
56 | 0.013557 | 0.0033997 | -0.013554 | -0.0033977 | 3.6412e-06 | 2.0456e-06 | 0.020654 | 0.020654 | 0.020654 | 0.97678 | -0.44634 | 0.97649 | -0.45198 | 5.6742
57 | 0.036139 | 0.0090673 | -0.036116 | -0.0090529 | 2.2897e-05 | 1.439e-05 | 0.054379 | 0.054379 | 0.054379 | 0.98897 | -0.21085 | 0.98829 | -0.22415 | 14.9393
58 | 0.0095373 | 0.0023908 | -0.0095358 | -0.00239 | 1.5317e-06 | 7.3855e-07 | 0.014536 | 0.014536 | 0.014536 | 0.97635 | -0.45482 | 0.97618 | -0.45819 | 3.9933
59 | -0.0095373 | -0.0023908 | 0.0095386 | 0.0023914 | 1.2886e-06 | 6.2128e-07 | 0.014536 | 0.014536 | 0.014536 | 0.97635 | -0.45482 | 0.97649 | -0.45198 | 3.9933
60 | 0.0078863 | 0.0019766 | -0.0078854 | -0.0019763 | 9.3642e-07 | 3.8332e-07 | 0.012021 | 0.012022 | 0.012022 | 0.97618 | -0.45819 | 0.97605 | -0.46068 | 3.3026
61 | 0.023118 | 0.0057946 | -0.023116 | -0.0057935 | 1.7851e-06 | 1.0921e-06 | 0.034808 | 0.034808 | 0.034808 | 0.98829 | -0.22415 | 0.9882 | -0.22577 | 9.5626
62 | 0.012998 | 0.0032584 | -0.012996 | -0.0032571 | 2.3314e-06 | 1.2841e-06 | 0.019571 | 0.019571 | 0.019571 | 0.98829 | -0.22415 | 0.98809 | -0.22791 | 5.3767
63 | 0.10121 | 0.025723 | -0.1011 | -0.025656 | 0.00010528 | 6.6768e-05 | 0.15309 | 0.15309 | 0.15309 | 0.98455 | -0.29461 | 0.98343 | -0.31623 | 21.0288
64 | 0.13542 | 0.034749 | -0.13533 | -0.034692 | 9.0792e-05 | 5.7419e-05 | 0.20282 | 0.20282 | 0.20282 | 0.99496 | -0.095372 | 0.99423 | -0.1092 | 18.5734
65 | 0.0091089 | 0.0022831 | -0.009108 | -0.0022827 | 8.7777e-07 | 3.9924e-07 | 0.013649 | 0.013649 | 0.013649 | 0.99305 | -0.13261 | 0.99294 | -0.13463 | 3.7498
66 | 0.0048656 | 0.0012194 | -0.0048655 | -0.0012194 | 7.5192e-08 | 3.2631e-09 | 0.0074459 | 0.0074459 | 0.0074459 | 0.97235 | -0.53331 | 0.97234 | -0.53363 | 2.0456
67 | 0.011203 | 0.002809 | -0.011201 | -0.0028078 | 2.364e-06 | 1.247e-06 | 0.017145 | 0.017145 | 0.017145 | 0.97235 | -0.53331 | 0.97213 | -0.53774 | 4.7102
68 | -0.089211 | -0.022529 | 0.089227 | 0.022538 | 1.5557e-05 | 9.9282e-06 | 0.13563 | 0.13563 | 0.13563 | 0.97917 | -0.39898 | 0.97936 | -0.39535 | 37.2616
69 | 0.086767 | 0.021916 | -0.086624 | -0.021825 | 0.00014296 | 9.1222e-05 | 0.13192 | 0.13192 | 0.13192 | 0.97917 | -0.39898 | 0.97741 | -0.43343 | 36.2411
70 | -0.093023 | -0.02349 | 0.093126 | 0.023555 | 0.00010276 | 6.5596e-05 | 0.1414 | 0.1414 | 0.1414 | 0.97936 | -0.39535 | 0.98054 | -0.37232 | 38.8461
71 | 0.081842 | 0.020626 | -0.081812 | -0.020607 | 2.9327e-05 | 1.8706e-05 | 0.12464 | 0.12464 | 0.12464 | 0.97741 | -0.43343 | 0.97703 | -0.44092 | 34.241
72 | -0.096266 | -0.024342 | 0.096392 | 0.024423 | 0.00012623 | 8.0587e-05 | 0.14616 | 0.14616 | 0.14616 | 0.98054 | -0.37232 | 0.98195 | -0.34502 | 40.1551
73 | 0.081812 | 0.020607 | -0.081745 | -0.020565 | 6.701e-05 | 4.2742e-05 | 0.12464 | 0.12464 | 0.12464 | 0.97703 | -0.44092 | 0.97616 | -0.45806 | 34.241
74 | -0.09856 | -0.024966 | 0.098696 | 0.025053 | 0.00013649 | 8.7147e-05 | 0.14945 | 0.14945 | 0.14945 | 0.98195 | -0.34502 | 0.98343 | -0.31623 | 41.0576
75 | 0.005724 | 0.0014344 | -0.005723 | -0.0014343 | 9.4611e-07 | 1.9131e-07 | 0.0087253 | 0.0087255 | 0.0087255 | 0.97616 | -0.45806 | 0.97598 | -0.46153 | 2.3971
76 | 0.076021 | 0.01913 | -0.076006 | -0.01912 | 1.578e-05 | 1.006e-05 | 0.11591 | 0.11591 | 0.11591 | 0.97616 | -0.45806 | 0.97594 | -0.46241 | 31.8439
77 | 0.0033059 | 0.00082848 | -0.0033059 | -0.00082853 | 6.8526e-08 | -4.6028e-08 | 0.0050403 | 0.0050404 | 0.0050404 | 0.97598 | -0.46153 | 0.97596 | -0.46197 | 1.3847
78 | 0.061142 | 0.015393 | -0.061096 | -0.015364 | 4.6013e-05 | 2.9272e-05 | 0.093249 | 0.093249 | 0.093249 | 0.97594 | -0.46241 | 0.97513 | -0.47816 | 25.6179
79 | 0.014863 | 0.0037273 | -0.014856 | -0.0037234 | 6.8652e-06 | 3.9486e-06 | 0.022663 | 0.022663 | 0.022663 | 0.97594 | -0.46241 | 0.97544 | -0.4721 | 6.2261
80 | 0.061096 | 0.015364 | -0.061082 | -0.015354 | 1.4511e-05 | 9.2315e-06 | 0.093249 | 0.093249 | 0.093249 | 0.97513 | -0.47816 | 0.97488 | -0.48314 | 25.6179
81 | 0.043813 | 0.011026 | -0.043788 | -0.011011 | 2.5108e-05 | 1.5883e-05 | 0.066891 | 0.066891 | 0.066891 | 0.97488 | -0.48314 | 0.97427 | -0.49513 | 18.3768
82 | -0.011199 | -0.0028067 | 0.011201 | 0.0028078 | 1.9732e-06 | 1.041e-06 | 0.017145 | 0.017145 | 0.017145 | 0.97194 | -0.54144 | 0.97213 | -0.53774 | 4.7103

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.6108 | 0.15577

## res_load
| p_mw | q_mvar
0 | 0.0051974 | 0.0013026
1 | 0.0014836 | 0.00037183
2 | 0.0047389 | 0.0011877
3 | 0.0066089 | 0.0016564
4 | 0.0023437 | 0.00058738
5 | 0.006516 | 0.0016331
6 | 0.0040925 | 0.0010257
7 | 0.011111 | 0.0027846
8 | 0.012256 | 0.0030718
9 | 0.014244 | 0.0035698
10 | 0.001129 | 0.00028297
11 | 0.033167 | 0.0083124
12 | 0.0033528 | 0.00084028
13 | 0.0044213 | 0.0011081
14 | 0.024831 | 0.0062232
15 | 0.045091 | 0.011301
16 | 0.020159 | 0.0050524
17 | 0.0065881 | 0.0016511
18 | 0.045891 | 0.011501
19 | 0.0052737 | 0.0013217
20 | 0.02518 | 0.0063108
21 | 0.026361 | 0.0066068
22 | 0.0032846 | 0.00082321
23 | 0.0092407 | 0.0023159
24 | 0.077207 | 0.01935
25 | 0.0016494 | 0.00041339
26 | 0.0040152 | 0.0010063
27 | 0.023116 | 0.0057935
28 | 0.012996 | 0.0032571
29 | 0.0031461 | 0.00078849
30 | 0.028067 | 0.0070343
31 | 0.0078854 | 0.0019763
32 | 0.0056421 | 0.001414
33 | 0.0056147 | 0.0014072
34 | 0.0032605 | 0.00081717
35 | 0.0048655 | 0.0012194
36 | 0.0024444 | 0.00061263
37 | 0.0037959 | 0.00095134
38 | 0.0047822 | 0.0011985
39 | 0.00314 | 0.00078696
40 | 0.0021679 | 0.00054333
41 | 0.0024059 | 0.00060296
42 | 0.0024171 | 0.00060578
43 | 0.014856 | 0.0037234
44 | 0.017268 | 0.0043279
45 | 0.0033059 | 0.00082853
46 | 0.015051 | 0.0037722
47 | 0.011199 | 0.0028067
48 | 0.0091188 | 0.0022854
49 | 0.009108 | 0.0022827

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1