## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-124_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-124_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-124_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-124_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_261-124_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_261-124_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_261-124_0_4_node_84 | 0.4 | n |  | TRUE
7 | bus_LV_261-124_0_4_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_261-124_0_4_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_261-124_0_4_node_10 | 0.4 | n |  | TRUE
10 | bus_LV_261-124_0_4_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_261-124_0_4_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_261-124_0_4_node_13 | 0.4 | n |  | TRUE
13 | bus_LV_261-124_0_4_node_20 | 0.4 | n |  | TRUE
14 | bus_LV_261-124_0_4_node_18 | 0.4 | n |  | TRUE
15 | bus_LV_261-124_0_4_node_58 | 0.4 | n |  | TRUE
16 | bus_LV_261-124_0_4_node_55 | 0.4 | n |  | TRUE
17 | bus_LV_261-124_0_4_node_25 | 0.4 | n |  | TRUE
18 | bus_LV_261-124_0_4_node_45 | 0.4 | n |  | TRUE
19 | bus_LV_261-124_0_4_node_44 | 0.4 | n |  | TRUE
20 | bus_LV_261-124_0_4_node_53 | 0.4 | n |  | TRUE
21 | bus_LV_261-124_0_4_node_54 | 0.4 | n |  | TRUE
22 | bus_LV_261-124_0_4_node_63 | 0.4 | n |  | TRUE
23 | bus_LV_261-124_0_4_node_56 | 0.4 | n |  | TRUE
24 | bus_LV_261-124_0_4_node_57 | 0.4 | n |  | TRUE
25 | bus_LV_261-124_0_4_node_85 | 0.4 | n |  | TRUE
26 | bus_LV_261-124_0_4_node_72 | 0.4 | n |  | TRUE
27 | bus_LV_261-124_0_4_node_59 | 0.4 | n |  | TRUE
28 | bus_LV_261-124_0_4_node_60 | 0.4 | n |  | TRUE
29 | bus_LV_261-124_0_4_node_61 | 0.4 | n |  | TRUE
30 | bus_LV_261-124_0_4_node_62 | 0.4 | n |  | TRUE
31 | bus_LV_261-124_0_4_node_81 | 0.4 | n |  | TRUE
32 | bus_LV_261-124_0_4_node_65 | 0.4 | n |  | TRUE
33 | bus_LV_261-124_0_4_node_66 | 0.4 | n |  | TRUE
34 | bus_LV_261-124_0_4_node_69 | 0.4 | n |  | TRUE
35 | bus_LV_261-124_0_4_node_70 | 0.4 | n |  | TRUE
36 | bus_LV_261-124_0_4_node_83 | 0.4 | n |  | TRUE
37 | bus_LV_261-124_0_4_node_82 | 0.4 | n |  | TRUE
38 | bus_MV_389_1_node_132 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-124_0_4_load_0 | 0 | 0.012694 | 0.0031813 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-124_0_4_load_4 | 3 | 0.0037827 | 0.00094804 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-124_0_4_load_5 | 4 | 0.0080766 | 0.0020242 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-124_0_4_load_6 | 5 | 0.0064346 | 0.0016127 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-124_0_4_load_84 | 6 | 0.0026181 | 0.00065616 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-124_0_4_load_9 | 7 | 0.019835 | 0.0049711 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-124_0_4_load_8 | 8 | 0.012081 | 0.0030277 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-124_0_4_load_10 | 9 | 0.033465 | 0.0083872 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-124_0_4_load_13 | 12 | 0.0081766 | 0.0020492 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-124_0_4_load_58 | 15 | 0.0016226 | 0.00040665 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-124_0_4_load_55 | 16 | 0.0021335 | 0.0005347 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-124_0_4_load_45 | 18 | 0.010907 | 0.0027336 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-124_0_4_load_44 | 19 | 0.0035346 | 0.00088585 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-124_0_4_load_53 | 20 | 0.0030527 | 0.00076507 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-124_0_4_load_54 | 21 | 0.035756 | 0.0089613 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-124_0_4_load_56 | 23 | 0.0006449 | 0.00016163 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-124_0_4_load_85 | 25 | 0.015159 | 0.0037992 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-124_0_4_load_59 | 27 | 0.0075193 | 0.0018845 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-124_0_4_load_60 | 28 | 0.0032539 | 0.0008155 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-124_0_4_load_62 | 30 | 0.00018352 | 4.5994e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-124_0_4_load_81 | 31 | 0.0011156 | 0.00027959 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-124_0_4_load_69 | 34 | 0.0038104 | 0.00095497 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-124_0_4_load_70 | 35 | 0.00030979 | 7.7641e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-124_0_4_load_82 | 37 | 0.0078636 | 0.0019708 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 22 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-124_0_4_line_0 |  | 0 | 1 | 0.011085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-124_0_4_line_1 |  | 0 | 2 | 0.025973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-124_0_4_line_2 |  | 1 | 3 | 0.076276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-124_0_4_line_3 |  | 2 | 4 | 0.013828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-124_0_4_line_4 |  | 2 | 5 | 0.0031411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-124_0_4_line_5 |  | 3 | 6 | 0.039409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-124_0_4_line_6 |  | 5 | 7 | 0.018502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-124_0_4_line_7 |  | 6 | 33 | 0.16263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_261-124_0_4_line_8 |  | 7 | 8 | 0.0057724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-124_0_4_line_9 |  | 9 | 10 | 0.034484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-124_0_4_line_10 |  | 9 | 11 | 0.044577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-124_0_4_line_11 |  | 10 | 12 | 0.049279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-124_0_4_line_12 |  | 11 | 13 | 0.10234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-124_0_4_line_13 |  | 13 | 17 | 0.009469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-124_0_4_line_14 |  | 13 | 18 | 0.019489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-124_0_4_line_15 |  | 13 | 19 | 0.04813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-124_0_4_line_16 |  | 14 | 15 | 0.019115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-124_0_4_line_17 |  | 14 | 16 | 0.0085499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-124_0_4_line_18 |  | 15 | 17 | 0.047698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-124_0_4_line_19 |  | 16 | 23 | 0.047425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-124_0_4_line_20 |  | 18 | 20 | 0.0078524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-124_0_4_line_21 |  | 20 | 21 | 0.0047396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-124_0_4_line_22 |  | 21 | 22 | 0.03265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-124_0_4_line_23 |  | 22 | 31 | 0.069623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_261-124_0_4_line_24 |  | 22 | 29 | 0.039127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-124_0_4_line_25 |  | 23 | 24 | 0.037522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-124_0_4_line_26 |  | 24 | 25 | 0.010834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-124_0_4_line_27 |  | 24 | 26 | 0.044319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-124_0_4_line_28 |  | 26 | 36 | 0.04122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-124_0_4_line_29 |  | 26 | 35 | 0.01674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-124_0_4_line_30 |  | 27 | 28 | 0.056921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-124_0_4_line_31 |  | 27 | 29 | 0.012793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-124_0_4_line_32 |  | 28 | 30 | 0.030041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-124_0_4_line_33 |  | 31 | 32 | 0.01329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_261-124_0_4_line_34 |  | 32 | 33 | 0.43412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_261-124_0_4_line_35 |  | 34 | 35 | 0.0074201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-124_0_4_line_36 |  | 36 | 37 | 0.015332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-124_0_4_trafo_63 | 0.63 MVA 20/0.4 kV | 38 | 22 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2679260.5522 | 1250372.9549 | 2679270.9935 | 1250369.2314
1 | 2679295.4551 | 1250360.5014 | 2679278.5536 | 1250366.5354 | 2679270.9935 | 1250369.2314
2 | 2679260.5522 | 1250372.9549 | 2679243.7189 | 1250376.1545 | 2679227.8161 | 1250375.8194 | 2679215.2198 | 1250374.3834 | 2679202.64 | 1250371.7133 | 2679186.3939 | 1250364.6966
3 | 2679295.4551 | 1250360.5014 | 2679299.4474 | 1250373.7402
4 | 2679295.4551 | 1250360.5014 | 2679298.5834 | 1250360.2181
5 | 2679150.0435 | 1250369.1196 | 2679165.7271 | 1250360.5898 | 2679171.9492 | 1250359.9391 | 2679177.959 | 1250361.0535 | 2679186.3939 | 1250364.6966
6 | 2679298.5834 | 1250360.2181 | 2679317.0102 | 1250358.549
7 | 2679037.4049 | 1250482.2225 | 2679062.4714 | 1250440.2148 | 2679071.8103 | 1250427.7746 | 2679090.959 | 1250409.4611 | 2679116.3167 | 1250389.7961 | 2679145.3534 | 1250371.6704 | 2679150.0435 | 1250369.1196
8 | 2679322.759 | 1250358.0282 | 2679317.0102 | 1250358.549
9 | 2679336.6956 | 1250129.6502 | 2679303.0985 | 1250137.4195
10 | 2679279.6932 | 1250160.0989 | 2679278.2314 | 1250154.2417 | 2679276.0626 | 1250143.6716 | 2679303.0985 | 1250137.4195
11 | 2679336.6956 | 1250129.6502 | 2679348.1858 | 1250111.1237 | 2679375.0089 | 1250105.158
12 | 2679279.6932 | 1250160.0989 | 2679280.9476 | 1250164.53 | 2679284.8019 | 1250163.6809 | 2679285.3478 | 1250165.7676 | 2679249.35 | 1250174.7595 | 2679244.1704 | 1250175.9133 | 2679245.5041 | 1250179.5004 | 2679286.505 | 1250171.2537 | 2679287.7133 | 1250174.6168
13 | 2679287.7133 | 1250174.6168 | 2679296.9392 | 1250172.3719
14 | 2679287.7133 | 1250174.6168 | 2679294.2879 | 1250192.9633
15 | 2679287.7133 | 1250174.6168 | 2679256.5921 | 1250181.9727 | 2679240.908 | 1250185.8287
16 | 2679361.8685 | 1250156.6181 | 2679356.1573 | 1250157.9982 | 2679343.2915 | 1250161.121
17 | 2679361.8685 | 1250156.6181 | 2679362.914 | 1250161.9805 | 2679363.0565 | 1250162.6162 | 2679363.2283 | 1250163.8861 | 2679363.4244 | 1250165.0229
18 | 2679296.9392 | 1250172.3719 | 2679343.2915 | 1250161.121
19 | 2679363.4244 | 1250165.0229 | 2679364.7569 | 1250163.0615 | 2679408.0142 | 1250150.4642
20 | 2679296.9369 | 1250200.3554 | 2679294.2879 | 1250192.9633
21 | 2679298.5358 | 1250204.8171 | 2679296.9369 | 1250200.3554
22 | 2679308.3414 | 1250235.96 | 2679298.5358 | 1250204.8171
23 | 2679308.3414 | 1250235.96 | 2679290.0587 | 1250238.5507 | 2679264.6218 | 1250239.7781 | 2679256.1355 | 1250239.2309 | 2679240.747 | 1250238.2467 | 2679239.0074 | 1250237.9363
24 | 2679347.5356 | 1250237.4412 | 2679319.464 | 1250236.9652 | 2679308.3414 | 1250235.96
25 | 2679444.0392 | 1250139.9731 | 2679408.0142 | 1250150.4642
26 | 2679447.2754 | 1250150.313 | 2679444.9038 | 1250142.4977 | 2679444.0392 | 1250139.9731
27 | 2679444.0392 | 1250139.9731 | 2679462.9755 | 1250138.7816 | 2679464.2352 | 1250139.9994 | 2679467.4013 | 1250139.7972 | 2679468.4574 | 1250138.1769 | 2679475.5304 | 1250137.7158 | 2679484.6136 | 1250137.1149 | 2679484.7338 | 1250139.4071
28 | 2679488.0656 | 1250179.1921 | 2679487.9574 | 1250177.6896 | 2679487.1078 | 1250160.5434 | 2679485.8231 | 1250160.6373 | 2679485.4281 | 1250152.9375 | 2679484.7338 | 1250139.4071
29 | 2679484.7338 | 1250139.4071 | 2679485.8291 | 1250139.3662 | 2679487.0693 | 1250139.216 | 2679488.3519 | 1250139.2889 | 2679490.1146 | 1250140.1465 | 2679501.2412 | 1250139.4292
30 | 2679360.1436 | 1250239.6089 | 2679416.2414 | 1250249.254
31 | 2679347.5356 | 1250237.4412 | 2679360.1436 | 1250239.6089
32 | 2679416.2414 | 1250249.254 | 2679445.4508 | 1250254.2761 | 2679445.8456 | 1250254.3578
33 | 2679225.9242 | 1250235.6022 | 2679239.0074 | 1250237.9363
34 | 2679037.4049 | 1250482.2225 | 2679027.8317 | 1250476.5907 | 2678961.0167 | 1250433.0795 | 2679025.8424 | 1250359.7338 | 2679061.9862 | 1250331.7619 | 2679122.9567 | 1250294.5592 | 2679183.4616 | 1250269.0817 | 2679218.7914 | 1250260.8699 | 2679222.6048 | 1250251.2137 | 2679223.5713 | 1250246.69 | 2679225.2958 | 1250238.5515 | 2679225.9242 | 1250235.6022
35 | 2679508.6459 | 1250138.9519 | 2679501.2412 | 1250139.4292
36 | 2679488.0656 | 1250179.1921 | 2679488.976 | 1250194.4974

## bus_geodata
| x | y | coords
0 | 2679270.9935 | 1250369.2314
1 | 2679260.5522 | 1250372.9549
2 | 2679295.4551 | 1250360.5014
3 | 2679186.3939 | 1250364.6966
4 | 2679299.4474 | 1250373.7402
5 | 2679298.5834 | 1250360.2181
6 | 2679150.0435 | 1250369.1196
7 | 2679317.0102 | 1250358.549
8 | 2679322.759 | 1250358.0282
9 | 2679303.0985 | 1250137.4195
10 | 2679336.6956 | 1250129.6502
11 | 2679279.6932 | 1250160.0989
12 | 2679375.0089 | 1250105.158
13 | 2679287.7133 | 1250174.6168
14 | 2679361.8685 | 1250156.6181
15 | 2679343.2915 | 1250161.121
16 | 2679363.4244 | 1250165.0229
17 | 2679296.9392 | 1250172.3719
18 | 2679294.2879 | 1250192.9633
19 | 2679240.908 | 1250185.8287
20 | 2679296.9369 | 1250200.3554
21 | 2679298.5358 | 1250204.8171
22 | 2679308.3414 | 1250235.96
23 | 2679408.0142 | 1250150.4642
24 | 2679444.0392 | 1250139.9731
25 | 2679447.2754 | 1250150.313
26 | 2679484.7338 | 1250139.4071
27 | 2679360.1436 | 1250239.6089
28 | 2679416.2414 | 1250249.254
29 | 2679347.5356 | 1250237.4412
30 | 2679445.8456 | 1250254.3578
31 | 2679239.0074 | 1250237.9363
32 | 2679225.9242 | 1250235.6022
33 | 2679037.4049 | 1250482.2225
34 | 2679508.6459 | 1250138.9519
35 | 2679501.2412 | 1250139.4292
36 | 2679488.0656 | 1250179.1921
37 | 2679488.976 | 1250194.4974
38 | 2679347.5356 | 1250237.4412

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.972 | -0.53721 | 0.012694 | 0.0031813
1 | 0.97262 | -0.52513 | 0 | 0
2 | 0.97088 | -0.55948 | 0 | 0
3 | 0.97683 | -0.44239 | 0.0037827 | 0.00094804
4 | 0.97077 | -0.56155 | 0.0080766 | 0.0020242
5 | 0.97076 | -0.56171 | 0.0064346 | 0.0016127
6 | 0.97914 | -0.39722 | 0.0026181 | 0.00065616
7 | 0.97021 | -0.57264 | 0.019835 | 0.0049711
8 | 0.97015 | -0.57393 | 0.012081 | 0.0030277
9 | 0.98821 | -0.22684 | 0.033465 | 0.0083872
10 | 0.98795 | -0.23187 | 0 | 0
11 | 0.98992 | -0.19376 | 0 | 0
12 | 0.98758 | -0.23907 | 0.0081766 | 0.0020492
13 | 0.99383 | -0.11825 | 0 | 0
14 | 0.99165 | -0.16027 | 0 | 0
15 | 0.99217 | -0.15013 | 0.0016226 | 0.00040665
16 | 0.99141 | -0.1648 | 0.0021335 | 0.0005347
17 | 0.99355 | -0.12352 | 0 | 0
18 | 0.9952 | -0.091892 | 0.010907 | 0.0027336
19 | 0.99367 | -0.12125 | 0.0035346 | 0.00088585
20 | 0.99583 | -0.079788 | 0.0030527 | 0.00076507
21 | 0.99622 | -0.072236 | 0.035756 | 0.0089613
22 | 1 | 0 | -0.20843 | -0.052865
23 | 0.99021 | -0.18821 | 0.0006449 | 0.00016163
24 | 0.98927 | -0.20633 | 0 | 0
25 | 0.98912 | -0.20925 | 0.015159 | 0.0037992
26 | 0.98879 | -0.2158 | 0 | 0
27 | 0.99948 | -0.0099236 | 0.0075193 | 0.0018845
28 | 0.99931 | -0.01334 | 0.0032539 | 0.0008155
29 | 0.99961 | -0.0074777 | 0 | 0
30 | 0.9993 | -0.013436 | 0.00018352 | 4.5994e-05
31 | 0.99783 | -0.040549 | 0.0011156 | 0.00027959
32 | 0.99742 | -0.048179 | 0 | 0
33 | 0.98412 | -0.30083 | 0 | 0
34 | 0.9887 | -0.21753 | 0.0038104 | 0.00095497
35 | 0.98872 | -0.21703 | 0.00030979 | 7.7641e-05
36 | 0.98849 | -0.22158 | 0 | 0
37 | 0.98838 | -0.22373 | 0.0078636 | 0.0019708
38 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.059192 | -0.014862 | 0.059226 | 0.014884 | 3.4141e-05 | 2.1713e-05 | 0.090625 | 0.090625 | 0.090625 | 0.972 | -0.53721 | 0.97262 | -0.52513 | 24.8971
1 | 0.046498 | 0.011681 | -0.046449 | -0.011649 | 4.9366e-05 | 3.1272e-05 | 0.071193 | 0.071193 | 0.071193 | 0.972 | -0.53721 | 0.97088 | -0.55948 | 19.5586
2 | -0.059226 | -0.014884 | 0.059461 | 0.015033 | 0.00023492 | 0.0001494 | 0.090625 | 0.090625 | 0.090625 | 0.97262 | -0.52513 | 0.97683 | -0.44239 | 24.8971
3 | 0.0080774 | 0.0020245 | -0.0080766 | -0.0020242 | 7.9471e-07 | 3.3764e-07 | 0.01238 | 0.01238 | 0.01238 | 0.97088 | -0.55948 | 0.97077 | -0.56155 | 3.4011
4 | 0.038372 | 0.0096249 | -0.038368 | -0.0096223 | 4.0744e-06 | 2.5688e-06 | 0.058813 | 0.058813 | 0.058813 | 0.97088 | -0.55948 | 0.97076 | -0.56171 | 16.1575
5 | -0.063244 | -0.015981 | 0.063381 | 0.016068 | 0.0001373 | 8.7377e-05 | 0.096387 | 0.096387 | 0.096387 | 0.97683 | -0.44239 | 0.97914 | -0.39722 | 26.48
6 | 0.031933 | 0.0080096 | -0.031916 | -0.0079992 | 1.6625e-05 | 1.0411e-05 | 0.04895 | 0.04895 | 0.04895 | 0.97076 | -0.56171 | 0.97021 | -0.57264 | 13.4479
7 | -0.065999 | -0.016725 | 0.066306 | 0.016917 | 0.00030716 | 0.00019247 | 0.10037 | 0.10036 | 0.10037 | 0.97914 | -0.39722 | 0.98412 | -0.30083 | 13.7865
8 | 0.012081 | 0.0030281 | -0.012081 | -0.0030277 | 7.432e-07 | 4.0437e-07 | 0.018529 | 0.018529 | 0.018529 | 0.97021 | -0.57264 | 0.97015 | -0.57393 | 5.0905
9 | 0.0081813 | 0.0020512 | -0.0081794 | -0.0020504 | 1.9626e-06 | 8.1438e-07 | 0.012319 | 0.01232 | 0.01232 | 0.98821 | -0.22684 | 0.98795 | -0.23187 | 3.3845
10 | -0.041647 | -0.010438 | 0.041712 | 0.01048 | 6.5738e-05 | 4.15e-05 | 0.06271 | 0.06271 | 0.06271 | 0.98821 | -0.22684 | 0.98992 | -0.19376 | 17.2281
11 | 0.0081794 | 0.0020504 | -0.0081766 | -0.0020492 | 2.8047e-06 | 1.1642e-06 | 0.01232 | 0.01232 | 0.01232 | 0.98795 | -0.23187 | 0.98758 | -0.23907 | 3.3846
12 | -0.041712 | -0.01048 | 0.041863 | 0.010575 | 0.00015092 | 9.527e-05 | 0.06271 | 0.06271 | 0.06271 | 0.98992 | -0.19376 | 0.99383 | -0.11825 | 17.228
13 | 0.031678 | 0.0079879 | -0.03167 | -0.0079829 | 7.9941e-06 | 4.9936e-06 | 0.047448 | 0.047448 | 0.047448 | 0.99383 | -0.11825 | 0.99355 | -0.12352 | 13.0352
14 | -0.077077 | -0.019449 | 0.077174 | 0.019511 | 9.7411e-05 | 6.209e-05 | 0.11545 | 0.11545 | 0.11545 | 0.99383 | -0.11825 | 0.9952 | -0.091892 | 31.7171
15 | 0.0035351 | 0.00088555 | -0.0035346 | -0.00088585 | 5.0564e-07 | -2.9995e-07 | 0.0052928 | 0.005293 | 0.005293 | 0.99383 | -0.11825 | 0.99367 | -0.12125 | 1.4541
16 | -0.029993 | -0.007542 | 0.030008 | 0.0075511 | 1.4525e-05 | 9.0493e-06 | 0.045015 | 0.045015 | 0.045015 | 0.99165 | -0.16027 | 0.99217 | -0.15013 | 12.3667
17 | 0.029993 | 0.007542 | -0.029987 | -0.007538 | 6.4969e-06 | 4.0477e-06 | 0.045015 | 0.045015 | 0.045015 | 0.99165 | -0.16027 | 0.99141 | -0.1648 | 12.3667
18 | -0.03163 | -0.0079577 | 0.03167 | 0.0079829 | 4.0269e-05 | 2.5155e-05 | 0.047448 | 0.047448 | 0.047448 | 0.99217 | -0.15013 | 0.99355 | -0.12352 | 13.0352
19 | 0.027853 | 0.0070033 | -0.027822 | -0.006984 | 3.1093e-05 | 1.9289e-05 | 0.041813 | 0.041813 | 0.041813 | 0.99141 | -0.1648 | 0.99021 | -0.18821 | 11.4871
20 | -0.088081 | -0.022244 | 0.088132 | 0.022277 | 5.112e-05 | 3.2615e-05 | 0.13176 | 0.13176 | 0.13176 | 0.9952 | -0.091892 | 0.99583 | -0.079788 | 36.1973
21 | -0.091185 | -0.023042 | 0.091218 | 0.023063 | 3.3028e-05 | 2.1077e-05 | 0.13632 | 0.13632 | 0.13632 | 0.99583 | -0.079788 | 0.99622 | -0.072236 | 37.4505
22 | -0.12697 | -0.032024 | 0.12741 | 0.032306 | 0.00044073 | 0.00028164 | 0.18973 | 0.18973 | 0.18973 | 0.99622 | -0.072236 | 1 | 0 | 52.1227
23 | 0.068403 | 0.017811 | -0.068267 | -0.017726 | 0.00013588 | 8.514e-05 | 0.10202 | 0.10202 | 0.10202 | 1 | 0 | 0.99783 | -0.040549 | 14.0142
24 | 0.010962 | 0.0027479 | -0.010959 | -0.0027459 | 3.9044e-06 | 1.9857e-06 | 0.016312 | 0.016313 | 0.016313 | 1 | 0 | 0.99961 | -0.0074777 | 4.4815
25 | 0.027177 | 0.0068224 | -0.027154 | -0.0068078 | 2.3473e-05 | 1.4541e-05 | 0.040844 | 0.040844 | 0.040844 | 0.99021 | -0.18821 | 0.98927 | -0.20633 | 11.2209
26 | 0.015161 | 0.0038004 | -0.015159 | -0.0037992 | 2.1129e-06 | 1.2132e-06 | 0.022805 | 0.022805 | 0.022805 | 0.98927 | -0.20633 | 0.98912 | -0.20925 | 6.2651
27 | 0.011992 | 0.0030074 | -0.011987 | -0.0030045 | 5.4082e-06 | 2.8925e-06 | 0.018039 | 0.018039 | 0.018039 | 0.98927 | -0.20633 | 0.98879 | -0.2158 | 4.9559
28 | 0.0078666 | 0.001972 | -0.0078644 | -0.0019711 | 2.1664e-06 | 8.5794e-07 | 0.011838 | 0.011839 | 0.011839 | 0.98879 | -0.2158 | 0.98849 | -0.22158 | 3.2524
29 | 0.0041205 | 0.0010325 | -0.0041203 | -0.0010326 | 2.4137e-07 | -6.0224e-08 | 0.0062009 | 0.0062009 | 0.0062009 | 0.98879 | -0.2158 | 0.98872 | -0.21703 | 1.7036
30 | 0.003438 | 0.00086072 | -0.0034374 | -0.0008611 | 5.5916e-07 | -3.8799e-07 | 0.0051181 | 0.0051183 | 0.0051183 | 0.99948 | -0.0099236 | 0.99931 | -0.01334 | 1.4061
31 | -0.010957 | -0.0027452 | 0.010959 | 0.0027459 | 1.2766e-06 | 6.4933e-07 | 0.016313 | 0.016313 | 0.016313 | 0.99948 | -0.0099236 | 0.99961 | -0.0074777 | 4.4815
32 | 0.00018352 | 4.5601e-05 | -0.00018352 | -4.5994e-05 | 8.4082e-10 | -3.9303e-07 | 0.00027313 | 0.00027327 | 0.00027327 | 0.99931 | -0.01334 | 0.9993 | -0.013436 | 0.075073
33 | 0.067151 | 0.017446 | -0.067126 | -0.017431 | 2.5098e-05 | 1.5716e-05 | 0.10036 | 0.10036 | 0.10036 | 0.99783 | -0.040549 | 0.99742 | -0.048179 | 13.7858
34 | 0.067126 | 0.017431 | -0.066306 | -0.016917 | 0.00081988 | 0.00051354 | 0.10036 | 0.10036 | 0.10036 | 0.99742 | -0.048179 | 0.98412 | -0.30083 | 13.7863
35 | -0.0038104 | -0.00095497 | 0.0038105 | 0.00095493 | 9.1509e-08 | -3.6595e-08 | 0.0057347 | 0.0057347 | 0.0057347 | 0.9887 | -0.21753 | 0.98872 | -0.21703 | 1.5755
36 | 0.0078644 | 0.0019711 | -0.0078636 | -0.0019708 | 8.0584e-07 | 3.1921e-07 | 0.011839 | 0.011839 | 0.011839 | 0.98849 | -0.22158 | 0.98838 | -0.22373 | 3.2524

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.20843 | 0.052865

## res_load
| p_mw | q_mvar
0 | 0.012694 | 0.0031813
1 | 0.0037827 | 0.00094804
2 | 0.0080766 | 0.0020242
3 | 0.0064346 | 0.0016127
4 | 0.0026181 | 0.00065616
5 | 0.019835 | 0.0049711
6 | 0.012081 | 0.0030277
7 | 0.033465 | 0.0083872
8 | 0.0081766 | 0.0020492
9 | 0.0016226 | 0.00040665
10 | 0.0021335 | 0.0005347
11 | 0.010907 | 0.0027336
12 | 0.0035346 | 0.00088585
13 | 0.0030527 | 0.00076507
14 | 0.035756 | 0.0089613
15 | 0.0006449 | 0.00016163
16 | 0.015159 | 0.0037992
17 | 0.0075193 | 0.0018845
18 | 0.0032539 | 0.0008155
19 | 0.00018352 | 4.5994e-05
20 | 0.0011156 | 0.00027959
21 | 0.0038104 | 0.00095497
22 | 0.00030979 | 7.7641e-05
23 | 0.0078636 | 0.0019708

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1