## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-125_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-125_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-125_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-125_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_261-125_0_4_node_8 | 0.4 | n |  | TRUE
5 | bus_LV_261-125_0_4_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_261-125_0_4_node_55 | 0.4 | n |  | TRUE
7 | bus_LV_261-125_0_4_node_137 | 0.4 | n |  | TRUE
8 | bus_LV_261-125_0_4_node_33 | 0.4 | n |  | TRUE
9 | bus_LV_261-125_0_4_node_37 | 0.4 | n |  | TRUE
10 | bus_LV_261-125_0_4_node_136 | 0.4 | n |  | TRUE
11 | bus_LV_261-125_0_4_node_53 | 0.4 | n |  | TRUE
12 | bus_LV_261-125_0_4_node_138 | 0.4 | n |  | TRUE
13 | bus_LV_261-125_0_4_node_36 | 0.4 | n |  | TRUE
14 | bus_LV_261-125_0_4_node_38 | 0.4 | n |  | TRUE
15 | bus_LV_261-125_0_4_node_56 | 0.4 | n |  | TRUE
16 | bus_LV_261-125_0_4_node_54 | 0.4 | n |  | TRUE
17 | bus_LV_261-125_0_4_node_34 | 0.4 | n |  | TRUE
18 | bus_LV_261-125_0_4_node_35 | 0.4 | n |  | TRUE
19 | bus_LV_261-125_0_4_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_261-125_0_4_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_261-125_0_4_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_261-125_0_4_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_261-125_0_4_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_261-125_0_4_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_261-125_0_4_node_117 | 0.4 | n |  | TRUE
26 | bus_LV_261-125_0_4_node_78 | 0.4 | n |  | TRUE
27 | bus_LV_261-125_0_4_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_261-125_0_4_node_65 | 0.4 | n |  | TRUE
29 | bus_LV_261-125_0_4_node_66 | 0.4 | n |  | TRUE
30 | bus_LV_261-125_0_4_node_63 | 0.4 | n |  | TRUE
31 | bus_LV_261-125_0_4_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_261-125_0_4_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_261-125_0_4_node_97 | 0.4 | n |  | TRUE
34 | bus_LV_261-125_0_4_node_86 | 0.4 | n |  | TRUE
35 | bus_LV_261-125_0_4_node_119 | 0.4 | n |  | TRUE
36 | bus_LV_261-125_0_4_node_120 | 0.4 | n |  | TRUE
37 | bus_LV_261-125_0_4_node_22 | 0.4 | n |  | TRUE
38 | bus_LV_261-125_0_4_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_261-125_0_4_node_42 | 0.4 | n |  | TRUE
40 | bus_LV_261-125_0_4_node_74 | 0.4 | n |  | TRUE
41 | bus_LV_261-125_0_4_node_23 | 0.4 | n |  | TRUE
42 | bus_LV_261-125_0_4_node_58 | 0.4 | n |  | TRUE
43 | bus_LV_261-125_0_4_node_24 | 0.4 | n |  | TRUE
44 | bus_LV_261-125_0_4_node_57 | 0.4 | n |  | TRUE
45 | bus_LV_261-125_0_4_node_43 | 0.4 | n |  | TRUE
46 | bus_LV_261-125_0_4_node_32 | 0.4 | n |  | TRUE
47 | bus_LV_261-125_0_4_node_45 | 0.4 | n |  | TRUE
48 | bus_LV_261-125_0_4_node_118 | 0.4 | n |  | TRUE
49 | bus_LV_261-125_0_4_node_76 | 0.4 | n |  | TRUE
50 | bus_LV_261-125_0_4_node_30 | 0.4 | n |  | TRUE
51 | bus_LV_261-125_0_4_node_61 | 0.4 | n |  | TRUE
52 | bus_LV_261-125_0_4_node_72 | 0.4 | n |  | TRUE
53 | bus_LV_261-125_0_4_node_64 | 0.4 | n |  | TRUE
54 | bus_LV_261-125_0_4_node_62 | 0.4 | n |  | TRUE
55 | bus_LV_261-125_0_4_node_67 | 0.4 | n |  | TRUE
56 | bus_LV_261-125_0_4_node_107 | 0.4 | n |  | TRUE
57 | bus_LV_261-125_0_4_node_82 | 0.4 | n |  | TRUE
58 | bus_LV_261-125_0_4_node_83 | 0.4 | n |  | TRUE
59 | bus_LV_261-125_0_4_node_81 | 0.4 | n |  | TRUE
60 | bus_LV_261-125_0_4_node_95 | 0.4 | n |  | TRUE
61 | bus_LV_261-125_0_4_node_85 | 0.4 | n |  | TRUE
62 | bus_LV_261-125_0_4_node_92 | 0.4 | n |  | TRUE
63 | bus_LV_261-125_0_4_node_96 | 0.4 | n |  | TRUE
64 | bus_LV_261-125_0_4_node_116 | 0.4 | n |  | TRUE
65 | bus_LV_261-125_0_4_node_113 | 0.4 | n |  | TRUE
66 | bus_LV_261-125_0_4_node_112 | 0.4 | n |  | TRUE
67 | bus_LV_261-125_0_4_node_26 | 0.4 | n |  | TRUE
68 | bus_LV_261-125_0_4_node_27 | 0.4 | n |  | TRUE
69 | bus_LV_261-125_0_4_node_121 | 0.4 | n |  | TRUE
70 | bus_LV_261-125_0_4_node_44 | 0.4 | n |  | TRUE
71 | bus_LV_261-125_0_4_node_40 | 0.4 | n |  | TRUE
72 | bus_LV_261-125_0_4_node_144 | 0.4 | n |  | TRUE
73 | bus_LV_261-125_0_4_node_52 | 0.4 | n |  | TRUE
74 | bus_LV_261-125_0_4_node_41 | 0.4 | n |  | TRUE
75 | bus_LV_261-125_0_4_node_31 | 0.4 | n |  | TRUE
76 | bus_LV_261-125_0_4_node_46 | 0.4 | n |  | TRUE
77 | bus_LV_261-125_0_4_node_28 | 0.4 | n |  | TRUE
78 | bus_LV_261-125_0_4_node_80 | 0.4 | n |  | TRUE
79 | bus_LV_261-125_0_4_node_60 | 0.4 | n |  | TRUE
80 | bus_LV_261-125_0_4_node_73 | 0.4 | n |  | TRUE
81 | bus_LV_261-125_0_4_node_39 | 0.4 | n |  | TRUE
82 | bus_LV_261-125_0_4_node_141 | 0.4 | n |  | TRUE
83 | bus_LV_261-125_0_4_node_142 | 0.4 | n |  | TRUE
84 | bus_LV_261-125_0_4_node_143 | 0.4 | n |  | TRUE
85 | bus_LV_261-125_0_4_node_139 | 0.4 | n |  | TRUE
86 | bus_LV_261-125_0_4_node_140 | 0.4 | n |  | TRUE
87 | bus_LV_261-125_0_4_node_70 | 0.4 | n |  | TRUE
88 | bus_LV_261-125_0_4_node_71 | 0.4 | n |  | TRUE
89 | bus_LV_261-125_0_4_node_47 | 0.4 | n |  | TRUE
90 | bus_LV_261-125_0_4_node_48 | 0.4 | n |  | TRUE
91 | bus_LV_261-125_0_4_node_49 | 0.4 | n |  | TRUE
92 | bus_LV_261-125_0_4_node_50 | 0.4 | n |  | TRUE
93 | bus_LV_261-125_0_4_node_51 | 0.4 | n |  | TRUE
94 | bus_LV_261-125_0_4_node_59 | 0.4 | n |  | TRUE
95 | bus_LV_261-125_0_4_node_68 | 0.4 | n |  | TRUE
96 | bus_LV_261-125_0_4_node_69 | 0.4 | n |  | TRUE
97 | bus_LV_261-125_0_4_node_108 | 0.4 | n |  | TRUE
98 | bus_LV_261-125_0_4_node_75 | 0.4 | n |  | TRUE
99 | bus_LV_261-125_0_4_node_106 | 0.4 | n |  | TRUE
100 | bus_LV_261-125_0_4_node_88 | 0.4 | n |  | TRUE
101 | bus_LV_261-125_0_4_node_87 | 0.4 | n |  | TRUE
102 | bus_LV_261-125_0_4_node_105 | 0.4 | n |  | TRUE
103 | bus_LV_261-125_0_4_node_77 | 0.4 | n |  | TRUE
104 | bus_LV_261-125_0_4_node_94 | 0.4 | n |  | TRUE
105 | bus_LV_261-125_0_4_node_115 | 0.4 | n |  | TRUE
106 | bus_LV_261-125_0_4_node_114 | 0.4 | n |  | TRUE
107 | bus_LV_261-125_0_4_node_130 | 0.4 | n |  | TRUE
108 | bus_LV_261-125_0_4_node_126 | 0.4 | n |  | TRUE
109 | bus_LV_261-125_0_4_node_89 | 0.4 | n |  | TRUE
110 | bus_LV_261-125_0_4_node_90 | 0.4 | n |  | TRUE
111 | bus_LV_261-125_0_4_node_91 | 0.4 | n |  | TRUE
112 | bus_LV_261-125_0_4_node_93 | 0.4 | n |  | TRUE
113 | bus_LV_261-125_0_4_node_98 | 0.4 | n |  | TRUE
114 | bus_LV_261-125_0_4_node_99 | 0.4 | n |  | TRUE
115 | bus_LV_261-125_0_4_node_111 | 0.4 | n |  | TRUE
116 | bus_LV_261-125_0_4_node_100 | 0.4 | n |  | TRUE
117 | bus_LV_261-125_0_4_node_101 | 0.4 | n |  | TRUE
118 | bus_LV_261-125_0_4_node_102 | 0.4 | n |  | TRUE
119 | bus_LV_261-125_0_4_node_103 | 0.4 | n |  | TRUE
120 | bus_LV_261-125_0_4_node_104 | 0.4 | n |  | TRUE
121 | bus_LV_261-125_0_4_node_109 | 0.4 | n |  | TRUE
122 | bus_LV_261-125_0_4_node_110 | 0.4 | n |  | TRUE
123 | bus_LV_261-125_0_4_node_122 | 0.4 | n |  | TRUE
124 | bus_LV_261-125_0_4_node_123 | 0.4 | n |  | TRUE
125 | bus_LV_261-125_0_4_node_131 | 0.4 | n |  | TRUE
126 | bus_LV_261-125_0_4_node_124 | 0.4 | n |  | TRUE
127 | bus_LV_261-125_0_4_node_125 | 0.4 | n |  | TRUE
128 | bus_LV_261-125_0_4_node_127 | 0.4 | n |  | TRUE
129 | bus_LV_261-125_0_4_node_128 | 0.4 | n |  | TRUE
130 | bus_LV_261-125_0_4_node_132 | 0.4 | n |  | TRUE
131 | bus_LV_261-125_0_4_node_129 | 0.4 | n |  | TRUE
132 | bus_LV_261-125_0_4_node_133 | 0.4 | n |  | TRUE
133 | bus_LV_261-125_0_4_node_134 | 0.4 | n |  | TRUE
134 | bus_MV_518_0_node_8 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-125_0_4_load_0 | 0 | 0.0070318 | 0.0017623 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-125_0_4_load_55 | 6 | 0.0071127 | 0.0017826 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-125_0_4_load_137 | 7 | 0.0049622 | 0.0012436 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-125_0_4_load_37 | 9 | 0.0024846 | 0.0006227 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-125_0_4_load_136 | 10 | 0.0029536 | 0.00074024 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-125_0_4_load_53 | 11 | 0.0071196 | 0.0017843 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-125_0_4_load_36 | 13 | 0.0024703 | 0.00061912 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-125_0_4_load_38 | 14 | 0.0024461 | 0.00061304 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-125_0_4_load_56 | 15 | 0.0070595 | 0.0017693 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-125_0_4_load_54 | 16 | 0.007031 | 0.0017621 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-125_0_4_load_34 | 17 | 0.0024382 | 0.00061106 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-125_0_4_load_35 | 18 | 0.0021777 | 0.00054578 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-125_0_4_load_9 | 19 | 0.0074581 | 0.0018692 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-125_0_4_load_10 | 20 | 0.0023456 | 0.00058785 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-125_0_4_load_12 | 22 | 0.0017392 | 0.00043589 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-125_0_4_load_14 | 24 | 0.0021145 | 0.00052993 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-125_0_4_load_117 | 25 | 0.0017254 | 0.00043242 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-125_0_4_load_78 | 26 | 0.0044884 | 0.0011249 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-125_0_4_load_65 | 28 | 0.0067234 | 0.001685 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-125_0_4_load_66 | 29 | 0.0017781 | 0.00044564 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-125_0_4_load_63 | 30 | 0.0069431 | 0.0017401 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-125_0_4_load_97 | 33 | 0.001976 | 0.00049522 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-125_0_4_load_119 | 35 | 0.0017128 | 0.00042928 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-125_0_4_load_120 | 36 | 0.0017766 | 0.00044525 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-125_0_4_load_74 | 40 | 0.0027833 | 0.00069756 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-125_0_4_load_58 | 42 | 0.0058681 | 0.0014707 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-125_0_4_load_57 | 44 | 0.0026895 | 0.00067405 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-125_0_4_load_43 | 45 | 0.003179 | 0.00079674 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-125_0_4_load_45 | 47 | 0.00079668 | 0.00019967 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-125_0_4_load_118 | 48 | 0.0017169 | 0.0004303 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-125_0_4_load_76 | 49 | 0.013428 | 0.0033653 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-125_0_4_load_61 | 51 | 0.0014016 | 0.00035128 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-125_0_4_load_64 | 53 | 0.0027417 | 0.00068713 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-125_0_4_load_62 | 54 | 0.0054494 | 0.0013657 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-125_0_4_load_107 | 56 | 0.0020769 | 0.00052051 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-125_0_4_load_81 | 59 | 0.011868 | 0.0029743 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-125_0_4_load_95 | 60 | 0.0031921 | 0.00080002 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-125_0_4_load_92 | 62 | 0.0031953 | 0.00080083 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-125_0_4_load_96 | 63 | 0.0031281 | 0.00078397 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-125_0_4_load_116 | 64 | 0.0053686 | 0.0013455 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-125_0_4_load_113 | 65 | 0.0050668 | 0.0012699 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-125_0_4_load_112 | 66 | 0.0020998 | 0.00052627 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-125_0_4_load_26 | 67 | 0.00247 | 0.00061903 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-125_0_4_load_27 | 68 | 0.0039772 | 0.00099677 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-125_0_4_load_121 | 69 | 0.0017314 | 0.00043393 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-125_0_4_load_44 | 70 | 0.0055063 | 0.00138 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-125_0_4_load_40 | 71 | 0.0047372 | 0.0011872 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-125_0_4_load_144 | 72 | 0.0068334 | 0.0017126 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-125_0_4_load_52 | 73 | 0.0015505 | 0.0003886 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-125_0_4_load_41 | 74 | 0.0014515 | 0.00036379 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-125_0_4_load_31 | 75 | 0.0022967 | 0.0005756 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-125_0_4_load_46 | 76 | 0.00075867 | 0.00019014 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-125_0_4_load_28 | 77 | 0.0018563 | 0.00046524 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-125_0_4_load_80 | 78 | 0.005503 | 0.0013792 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-125_0_4_load_60 | 79 | 0.0011561 | 0.00028974 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-125_0_4_load_142 | 83 | 0.0074814 | 0.001875 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-125_0_4_load_143 | 84 | 0.0067359 | 0.0016882 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-125_0_4_load_139 | 85 | 0.0073654 | 0.0018459 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-125_0_4_load_140 | 86 | 0.00096436 | 0.00024169 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-125_0_4_load_71 | 88 | 0.0031809 | 0.00079721 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-125_0_4_load_47 | 89 | 0.0025674 | 0.00064346 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-125_0_4_load_48 | 90 | 0.0038205 | 0.00095751 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-125_0_4_load_49 | 91 | 0.0030741 | 0.00077043 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-125_0_4_load_50 | 92 | 0.002259 | 0.00056615 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-125_0_4_load_51 | 93 | 0.0029378 | 0.00073628 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-125_0_4_load_59 | 94 | 0.0014023 | 0.00035146 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-125_0_4_load_69 | 96 | 0.0079831 | 0.0020008 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-125_0_4_load_108 | 97 | 0.0022233 | 0.0005572 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-125_0_4_load_75 | 98 | 0.0070917 | 0.0017774 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-125_0_4_load_106 | 99 | 0.002249 | 0.00056364 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-125_0_4_load_88 | 100 | 0.0060802 | 0.0015238 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-125_0_4_load_87 | 101 | 0.0047633 | 0.0011938 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-125_0_4_load_105 | 102 | 0.0021527 | 0.00053953 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-125_0_4_load_77 | 103 | 0.0044635 | 0.0011187 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-125_0_4_load_94 | 104 | 0.0030965 | 0.00077605 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-125_0_4_load_115 | 105 | 0.0047712 | 0.0011958 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-125_0_4_load_114 | 106 | 0.0050399 | 0.0012631 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-125_0_4_load_89 | 109 | 0.0086952 | 0.0021792 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-125_0_4_load_90 | 110 | 0.0020228 | 0.00050697 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-125_0_4_load_91 | 111 | 0.0075743 | 0.0018983 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-125_0_4_load_93 | 112 | 0.0020046 | 0.0005024 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-125_0_4_load_98 | 113 | 0.0021139 | 0.00052979 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_261-125_0_4_load_99 | 114 | 0.0039264 | 0.00098406 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_261-125_0_4_load_111 | 115 | 0.0018834 | 0.00047203 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_261-125_0_4_load_100 | 116 | 0.002153 | 0.00053959 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_261-125_0_4_load_101 | 117 | 0.0050292 | 0.0012604 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_261-125_0_4_load_102 | 118 | 0.0021434 | 0.00053719 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_261-125_0_4_load_103 | 119 | 0.0022613 | 0.00056673 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_261-125_0_4_load_104 | 120 | 0.0044914 | 0.0011257 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_261-125_0_4_load_109 | 121 | 0.0022961 | 0.00057547 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_261-125_0_4_load_110 | 122 | 0.0020027 | 0.00050193 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_261-125_0_4_load_123 | 124 | 0.0040242 | 0.0010086 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_261-125_0_4_load_131 | 125 | 0.0041753 | 0.0010464 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_261-125_0_4_load_124 | 126 | 0.0040404 | 0.0010126 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_261-125_0_4_load_125 | 127 | 0.0045873 | 0.0011497 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_261-125_0_4_load_127 | 128 | 0.0044729 | 0.001121 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_261-125_0_4_load_128 | 129 | 0.0030095 | 0.00075425 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_261-125_0_4_load_132 | 130 | 0.010614 | 0.0026601 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_261-125_0_4_load_129 | 131 | 0.0043291 | 0.001085 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_261-125_0_4_load_134 | 133 | 0.009981 | 0.0025015 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 116 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-125_0_4_line_0 |  | 0 | 1 | 0.020569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-125_0_4_line_1 |  | 0 | 2 | 0.027162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-125_0_4_line_2 |  | 1 | 3 | 0.15565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-125_0_4_line_3 |  | 2 | 4 | 0.02057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-125_0_4_line_4 |  | 3 | 8 | 0.006005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-125_0_4_line_5 |  | 3 | 9 | 0.020608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-125_0_4_line_6 |  | 4 | 10 | 0.02908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-125_0_4_line_7 |  | 5 | 6 | 0.012202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-125_0_4_line_8 |  | 5 | 7 | 0.01888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-125_0_4_line_9 |  | 6 | 11 | 0.014366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-125_0_4_line_10 |  | 7 | 12 | 0.0074592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-125_0_4_line_11 |  | 8 | 13 | 0.013084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-125_0_4_line_12 |  | 9 | 14 | 0.016122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-125_0_4_line_13 |  | 11 | 16 | 0.014284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-125_0_4_line_14 |  | 12 | 86 | 0.015988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-125_0_4_line_15 |  | 13 | 18 | 0.016863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-125_0_4_line_16 |  | 14 | 81 | 0.022688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-125_0_4_line_17 |  | 15 | 16 | 0.014221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-125_0_4_line_18 |  | 17 | 18 | 0.015246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-125_0_4_line_19 |  | 19 | 20 | 0.015633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-125_0_4_line_20 |  | 19 | 21 | 0.023511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-125_0_4_line_21 |  | 20 | 22 | 0.020949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-125_0_4_line_22 |  | 21 | 23 | 0.01806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-125_0_4_line_23 |  | 21 | 24 | 0.018891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-125_0_4_line_24 |  | 22 | 25 | 0.0072938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-125_0_4_line_25 |  | 23 | 26 | 0.018255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-125_0_4_line_26 |  | 25 | 48 | 0.017945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-125_0_4_line_27 |  | 26 | 49 | 0.011243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-125_0_4_line_28 |  | 27 | 28 | 0.019053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_261-125_0_4_line_29 |  | 27 | 29 | 0.012253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_261-125_0_4_line_30 |  | 27 | 30 | 0.038621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-125_0_4_line_31 |  | 28 | 55 | 0.013987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_261-125_0_4_line_32 |  | 29 | 56 | 0.0079256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_261-125_0_4_line_33 |  | 30 | 54 | 0.029896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-125_0_4_line_34 |  | 31 | 32 | 0.018817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-125_0_4_line_35 |  | 31 | 33 | 0.008237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-125_0_4_line_36 |  | 32 | 34 | 0.022214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-125_0_4_line_37 |  | 32 | 35 | 0.034035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-125_0_4_line_38 |  | 32 | 36 | 0.017781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-125_0_4_line_39 |  | 33 | 66 | 0.0093596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_261-125_0_4_line_40 |  | 33 | 61 | 0.009716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-125_0_4_line_41 |  | 34 | 64 | 0.023218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-125_0_4_line_42 |  | 34 | 65 | 0.015699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-125_0_4_line_43 |  | 35 | 48 | 0.0072255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-125_0_4_line_44 |  | 36 | 69 | 0.00090907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-125_0_4_line_45 |  | 37 | 38 | 0.016455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_261-125_0_4_line_46 |  | 37 | 39 | 0.001758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_261-125_0_4_line_47 |  | 37 | 40 | 0.053581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-125_0_4_line_48 |  | 38 | 46 | 0.002498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-125_0_4_line_49 |  | 38 | 47 | 0.016608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_261-125_0_4_line_50 |  | 39 | 70 | 0.04775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_261-125_0_4_line_51 |  | 39 | 71 | 0.027421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-125_0_4_line_52 |  | 41 | 42 | 0.023109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
53 | LV_261-125_0_4_line_53 |  | 41 | 43 | 0.083697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-125_0_4_line_54 |  | 41 | 44 | 0.016931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
55 | LV_261-125_0_4_line_55 |  | 42 | 72 | 0.032108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-125_0_4_line_56 |  | 43 | 45 | 0.055383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-125_0_4_line_57 |  | 44 | 73 | 0.022063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_261-125_0_4_line_58 |  | 45 | 74 | 0.011137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-125_0_4_line_59 |  | 46 | 75 | 0.016323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-125_0_4_line_60 |  | 47 | 76 | 0.0081693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_261-125_0_4_line_61 |  | 49 | 103 | 0.031724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-125_0_4_line_62 |  | 50 | 51 | 0.039015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-125_0_4_line_63 |  | 50 | 52 | 0.031507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-125_0_4_line_64 |  | 51 | 79 | 0.0027787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-125_0_4_line_65 |  | 52 | 59 | 0.017869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-125_0_4_line_66 |  | 52 | 80 | 0.05432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-125_0_4_line_67 |  | 52 | 78 | 0.012516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-125_0_4_line_68 |  | 53 | 54 | 0.0074911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-125_0_4_line_69 |  | 55 | 95 | 0.007041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_261-125_0_4_line_70 |  | 55 | 96 | 0.026854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-125_0_4_line_71 |  | 56 | 97 | 0.020938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_261-125_0_4_line_72 |  | 57 | 58 | 0.048227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-125_0_4_line_73 |  | 57 | 59 | 0.013852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-125_0_4_line_74 |  | 58 | 60 | 0.044505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-125_0_4_line_75 |  | 60 | 104 | 0.008879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-125_0_4_line_76 |  | 61 | 62 | 0.013116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-125_0_4_line_77 |  | 61 | 63 | 0.022079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-125_0_4_line_78 |  | 63 | 104 | 0.01918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-125_0_4_line_79 |  | 64 | 107 | 0.0089813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-125_0_4_line_80 |  | 65 | 106 | 0.017362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_261-125_0_4_line_81 |  | 66 | 115 | 0.020854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
82 | LV_261-125_0_4_line_82 |  | 67 | 68 | 0.021427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_261-125_0_4_line_83 |  | 68 | 77 | 0.00065731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_261-125_0_4_line_84 |  | 70 | 87 | 0.0064031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_261-125_0_4_line_85 |  | 72 | 84 | 0.015853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_261-125_0_4_line_86 |  | 73 | 93 | 0.020196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_261-125_0_4_line_87 |  | 75 | 77 | 0.028069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_261-125_0_4_line_88 |  | 76 | 89 | 0.017677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
89 | LV_261-125_0_4_line_89 |  | 79 | 94 | 0.0034887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_261-125_0_4_line_90 |  | 80 | 100 | 0.007198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_261-125_0_4_line_91 |  | 80 | 101 | 0.03155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_261-125_0_4_line_92 |  | 81 | 82 | 0.035916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_261-125_0_4_line_93 |  | 81 | 83 | 0.0080966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_261-125_0_4_line_94 |  | 82 | 84 | 0.02037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_261-125_0_4_line_95 |  | 82 | 85 | 0.015841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_261-125_0_4_line_96 |  | 83 | 86 | 0.027592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_261-125_0_4_line_97 |  | 87 | 88 | 0.028747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
98 | LV_261-125_0_4_line_98 |  | 88 | 95 | 0.010946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
99 | LV_261-125_0_4_line_99 |  | 89 | 90 | 0.02406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
100 | LV_261-125_0_4_line_100 |  | 90 | 91 | 0.016687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
101 | LV_261-125_0_4_line_101 |  | 91 | 92 | 0.02201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
102 | LV_261-125_0_4_line_102 |  | 92 | 93 | 0.018876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
103 | LV_261-125_0_4_line_103 |  | 95 | 98 | 0.013212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
104 | LV_261-125_0_4_line_104 |  | 97 | 121 | 0.0081329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
105 | LV_261-125_0_4_line_105 |  | 98 | 99 | 0.0010459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
106 | LV_261-125_0_4_line_106 |  | 99 | 102 | 0.018663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
107 | LV_261-125_0_4_line_107 |  | 102 | 120 | 0.005147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
108 | LV_261-125_0_4_line_108 |  | 105 | 106 | 0.017218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_261-125_0_4_line_109 |  | 107 | 108 | 0.010779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-125_0_4_line_110 |  | 108 | 125 | 0.023877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_261-125_0_4_line_111 |  | 108 | 123 | 0.010608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_261-125_0_4_line_112 |  | 109 | 110 | 0.010392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_261-125_0_4_line_113 |  | 109 | 111 | 0.011218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_261-125_0_4_line_114 |  | 111 | 112 | 0.017706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_261-125_0_4_line_115 |  | 112 | 113 | 0.0079716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_261-125_0_4_line_116 |  | 113 | 114 | 0.002249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_261-125_0_4_line_117 |  | 114 | 116 | 0.016448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_261-125_0_4_line_118 |  | 115 | 122 | 0.0080669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
119 | LV_261-125_0_4_line_119 |  | 116 | 117 | 0.0069247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
120 | LV_261-125_0_4_line_120 |  | 117 | 118 | 0.0010669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
121 | LV_261-125_0_4_line_121 |  | 118 | 119 | 0.018616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
122 | LV_261-125_0_4_line_122 |  | 119 | 120 | 0.002781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
123 | LV_261-125_0_4_line_123 |  | 121 | 122 | 0.020798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
124 | LV_261-125_0_4_line_124 |  | 123 | 124 | 0.016206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_261-125_0_4_line_125 |  | 124 | 126 | 0.012912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_261-125_0_4_line_126 |  | 125 | 130 | 0.028416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_261-125_0_4_line_127 |  | 126 | 127 | 0.012361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_261-125_0_4_line_128 |  | 127 | 128 | 0.014275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_261-125_0_4_line_129 |  | 128 | 129 | 0.011041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_261-125_0_4_line_130 |  | 129 | 131 | 0.0028726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_261-125_0_4_line_131 |  | 130 | 132 | 0.013366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_261-125_0_4_line_132 |  | 132 | 133 | 0.043252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-125_0_4_trafo_100 | 0.63 MVA 20/0.4 kV | 134 | 116 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2679109.2186 | 1250631.2789 | 2679104.8248 | 1250623.37 | 2679099.4083 | 1250613.2007
1 | 2679088.3339 | 1250588.5466 | 2679090.6403 | 1250596.739 | 2679099.4083 | 1250613.2007
2 | 2679109.2186 | 1250631.2789 | 2679129.3707 | 1250620.3288 | 2679147.2783 | 1250604.4784 | 2679159.4395 | 1250598.8922 | 2679136.5155 | 1250620.1017 | 2679138.9426 | 1250622.0801 | 2679133.5885 | 1250631.8046 | 2679136.6642 | 1250636.0933 | 2679134.0122 | 1250638.5152 | 2679137.3731 | 1250642.3629 | 2679163.7996 | 1250642.0822 | 2679167.7373 | 1250650.7857
3 | 2679082.7018 | 1250568.768 | 2679084.5597 | 1250576.0648 | 2679088.3339 | 1250588.5466
4 | 2679170.0184 | 1250656.3425 | 2679167.7373 | 1250650.7857
5 | 2679167.7373 | 1250650.7857 | 2679186.2009 | 1250641.6317
6 | 2679082.7018 | 1250568.768 | 2679108.9005 | 1250556.1466
7 | 2679237.1072 | 1250580.3163 | 2679248.4979 | 1250575.9407
8 | 2679237.1072 | 1250580.3163 | 2679221.9932 | 1250591.6313
9 | 2679261.9087 | 1250570.789 | 2679248.4979 | 1250575.9407
10 | 2679216.0219 | 1250596.1016 | 2679221.9932 | 1250591.6313
11 | 2679170.0184 | 1250656.3425 | 2679159.4921 | 1250664.1127
12 | 2679186.2009 | 1250641.6317 | 2679200.6452 | 1250634.4704
13 | 2679261.9087 | 1250570.789 | 2679275.2426 | 1250565.6669
14 | 2679216.0219 | 1250596.1016 | 2679203.2955 | 1250605.7785
15 | 2679159.4921 | 1250664.1127 | 2679157.0872 | 1250665.8879 | 2679144.7998 | 1250672.3294
16 | 2679221.8128 | 1250626.5459 | 2679209.209 | 1250630.2246 | 2679200.6452 | 1250634.4704
17 | 2679288.5182 | 1250560.5672 | 2679275.2426 | 1250565.6669
18 | 2679131.2971 | 1250679.4081 | 2679144.7998 | 1250672.3294
19 | 2679224.0675 | 1250825.4407 | 2679239.4775 | 1250822.8125
20 | 2679200.8913 | 1250829.3934 | 2679224.0675 | 1250825.4407
21 | 2679260.1157 | 1250819.2191 | 2679248.953 | 1250821.1964 | 2679239.4775 | 1250822.8125
22 | 2679204.5578 | 1250847.0776 | 2679201.1787 | 1250831.054 | 2679200.8913 | 1250829.3934
23 | 2679200.8913 | 1250829.3934 | 2679195.6554 | 1250830.2908 | 2679188.8759 | 1250831.4455 | 2679182.365 | 1250833.0313
24 | 2679260.1157 | 1250819.2191 | 2679267.2977 | 1250817.9469
25 | 2679204.5578 | 1250847.0776 | 2679209.1157 | 1250852.2868 | 2679209.9369 | 1250855.2333 | 2679207.5381 | 1250859.6156 | 2679207.6162 | 1250862.8079 | 2679207.6637 | 1250862.879
26 | 2679284.9671 | 1250814.817 | 2679267.2977 | 1250817.9469
27 | 2679216.2719 | 1250868.6834 | 2679215.4361 | 1250866.8264 | 2679209.1852 | 1250865.1528 | 2679207.6637 | 1250862.879
28 | 2679227.6262 | 1250809.9475 | 2679221.8095 | 1250794.4361 | 2679220.8223 | 1250792.1534
29 | 2679227.6262 | 1250809.9475 | 2679235.8062 | 1250808.5002 | 2679239.6938 | 1250807.826
30 | 2679227.6262 | 1250809.9475 | 2679201.5049 | 1250814.5573 | 2679193.561 | 1250815.8522 | 2679189.5666 | 1250816.5011
31 | 2679215.2703 | 1250779.3153 | 2679220.8223 | 1250792.1534
32 | 2679239.6938 | 1250807.826 | 2679247.5028 | 1250806.4718
33 | 2679160.0886 | 1250821.4813 | 2679176.2964 | 1250818.6569 | 2679189.5666 | 1250816.5011
34 | 2679325.543 | 1250807.3663 | 2679328.2609 | 1250806.7911 | 2679337.6835 | 1250804.4377 | 2679336.6944 | 1250800.5105 | 2679336.1427 | 1250798.3014
35 | 2679336.1427 | 1250798.3014 | 2679335.9423 | 1250797.4759 | 2679334.1283 | 1250790.313
36 | 2679333.2635 | 1250825.5719 | 2679328.2609 | 1250806.7911 | 2679325.543 | 1250807.3663
37 | 2679325.543 | 1250807.3663 | 2679315.7236 | 1250809.4697 | 2679292.0844 | 1250813.5706
38 | 2679325.543 | 1250807.3663 | 2679330.1624 | 1250824.5367
39 | 2679334.1283 | 1250790.313 | 2679325.0533 | 1250792.6033
40 | 2679334.1283 | 1250790.313 | 2679343.5741 | 1250787.9266
41 | 2679333.2635 | 1250825.5719 | 2679339.2441 | 1250848.0069
42 | 2679333.2635 | 1250825.5719 | 2679348.2799 | 1250820.9934
43 | 2679284.9671 | 1250814.817 | 2679288.1732 | 1250814.2491 | 2679292.0844 | 1250813.5706
44 | 2679330.1624 | 1250824.5367 | 2679330.3986 | 1250825.4146
45 | 2679179.6001 | 1250688.4163 | 2679184.4868 | 1250695.5868 | 2679188.8624 | 1250702.0167
46 | 2679190.3546 | 1250701.0804 | 2679188.8624 | 1250702.0167
47 | 2679188.8624 | 1250702.0167 | 2679174.6945 | 1250710.9006 | 2679160.7564 | 1250720.099 | 2679149.0414 | 1250729.0269 | 2679144.8615 | 1250732.4918
48 | 2679179.6001 | 1250688.4163 | 2679177.4244 | 1250689.6548
49 | 2679179.6001 | 1250688.4163 | 2679193.8306 | 1250679.8542
50 | 2679190.3546 | 1250701.0804 | 2679191.919 | 1250703.2139 | 2679193.6052 | 1250701.8799 | 2679195.1424 | 1250703.7908 | 2679181.9801 | 1250714.2449 | 2679182.9192 | 1250715.714 | 2679186.4856 | 1250714.3496 | 2679193.2915 | 1250731.155
51 | 2679190.3546 | 1250701.0804 | 2679198.8999 | 1250695.4682 | 2679213.5625 | 1250686.4814
52 | 2679342.6697 | 1250605.2133 | 2679341.3566 | 1250602.9274 | 2679339.4663 | 1250601.4565 | 2679327.1915 | 1250597.4671 | 2679322.0202 | 1250597.4645
53 | 2679342.6697 | 1250605.2133 | 2679346.7121 | 1250612.2837 | 2679375.1726 | 1250596.5643 | 2679393.3139 | 1250586.422 | 2679406.3036 | 1250578.757 | 2679409.5775 | 1250585.1389
54 | 2679342.6697 | 1250605.2133 | 2679327.9148 | 1250613.5174
55 | 2679291.1486 | 1250606.2811 | 2679314.2468 | 1250599.5287 | 2679322.0202 | 1250597.4645
56 | 2679409.5775 | 1250585.1389 | 2679361.2196 | 1250612.1358
57 | 2679308.651 | 1250624.2704 | 2679310.2879 | 1250623.4378 | 2679327.9148 | 1250613.5174
58 | 2679361.2196 | 1250612.1358 | 2679359.0258 | 1250613.3604 | 2679351.4973 | 1250617.5683
59 | 2679177.4244 | 1250689.6548 | 2679164.6967 | 1250697.535 | 2679163.6078 | 1250698.3388
60 | 2679200.8306 | 1250675.6425 | 2679193.8306 | 1250679.8542
61 | 2679216.2719 | 1250868.6834 | 2679209.7807 | 1250875.9465 | 2679211.7267 | 1250877.1956 | 2679219.2324 | 1250877.0514 | 2679220.1842 | 1250879.2657 | 2679212.7247 | 1250885.5484
62 | 2679402.6295 | 1250652.9068 | 2679365.2152 | 1250663.9675
63 | 2679402.6295 | 1250652.9068 | 2679406.0381 | 1250670.6433 | 2679408.8589 | 1250683.7908
64 | 2679362.5506 | 1250664.7552 | 2679365.2152 | 1250663.9675
65 | 2679408.8589 | 1250683.7908 | 2679407.7434 | 1250685.9108 | 2679407.5627 | 1250687.5651 | 2679411.497 | 1250700.8016
66 | 2679408.8589 | 1250683.7908 | 2679382.802 | 1250686.9219 | 2679386.3518 | 1250700.3237 | 2679385.9906 | 1250710.3707 | 2679383.1193 | 1250713.3789
67 | 2679408.8589 | 1250683.7908 | 2679412.3998 | 1250682.0814 | 2679420.7168 | 1250679.9552
68 | 2679160.0886 | 1250821.4813 | 2679152.7088 | 1250822.7673
69 | 2679215.2703 | 1250779.3153 | 2679212.4729 | 1250772.851
70 | 2679215.2703 | 1250779.3153 | 2679200.0314 | 1250783.0478 | 2679188.7952 | 1250782.7085
71 | 2679268.1332 | 1250802.8941 | 2679247.5028 | 1250806.4718
72 | 2679415.4435 | 1250714.0791 | 2679415.7972 | 1250715.2847 | 2679417.1925 | 1250717.0714 | 2679417.8236 | 1250718.9924 | 2679420.4531 | 1250718.2493 | 2679432.7014 | 1250756.2748
73 | 2679415.4435 | 1250714.0791 | 2679411.497 | 1250700.8016
74 | 2679432.7014 | 1250756.2748 | 2679422.9366 | 1250760.4915 | 2679392.7166 | 1250771.795 | 2679391.2041 | 1250772.3296
75 | 2679382.8326 | 1250775.2885 | 2679391.2041 | 1250772.3296
76 | 2679343.5741 | 1250787.9266 | 2679340.4785 | 1250775.1815
77 | 2679343.5741 | 1250787.9266 | 2679348.278 | 1250786.7443 | 2679364.6925 | 1250781.5114
78 | 2679382.8326 | 1250775.2885 | 2679370.1357 | 1250779.7762 | 2679364.6925 | 1250781.5114
79 | 2679341.8696 | 1250856.5655 | 2679341.3021 | 1250855.5349 | 2679340.8252 | 1250853.9385 | 2679339.2441 | 1250848.0069
80 | 2679348.2799 | 1250820.9934 | 2679364.8867 | 1250815.93
81 | 2679325.0533 | 1250792.6033 | 2679321.6603 | 1250793.4596 | 2679304.5723 | 1250796.4912
82 | 2679124.8449 | 1250730.1038 | 2679132.2056 | 1250723.4536 | 2679140.9683 | 1250715.9945
83 | 2679140.9683 | 1250715.9945 | 2679141.4688 | 1250715.5685
84 | 2679197.1849 | 1250736.2197 | 2679193.4355 | 1250731.5106 | 2679193.2915 | 1250731.155
85 | 2679291.1486 | 1250606.2811 | 2679275.9325 | 1250610.7293
86 | 2679290.6022 | 1250633.3254 | 2679292.524 | 1250632.4735 | 2679308.651 | 1250624.2704
87 | 2679163.6078 | 1250698.3388 | 2679149.3104 | 1250708.8935 | 2679141.4688 | 1250715.5685
88 | 2679200.8306 | 1250675.6425 | 2679205.1638 | 1250673.0354 | 2679216.3237 | 1250667.1432
89 | 2679359.205 | 1250665.7443 | 2679362.5506 | 1250664.7552
90 | 2679383.1193 | 1250713.3789 | 2679376.0844 | 1250714.997
91 | 2679383.1193 | 1250713.3789 | 2679387.9214 | 1250733.6026 | 2679377.467 | 1250736.164
92 | 2679221.8128 | 1250626.5459 | 2679256.3807 | 1250616.445
93 | 2679221.8128 | 1250626.5459 | 2679218.0662 | 1250619.3683
94 | 2679256.3807 | 1250616.445 | 2679275.9325 | 1250610.7293
95 | 2679256.3807 | 1250616.445 | 2679248.9657 | 1250602.4466
96 | 2679218.0662 | 1250619.3683 | 2679207.1169 | 1250619.5666 | 2679200.7604 | 1250607.7062 | 2679203.2955 | 1250605.7785
97 | 2679197.1849 | 1250736.2197 | 2679198.765 | 1250739.9992 | 2679208.2577 | 1250762.7488
98 | 2679212.4729 | 1250772.851 | 2679208.2577 | 1250762.7488
99 | 2679238.0028 | 1250656.7341 | 2679224.9849 | 1250662.5703 | 2679216.3237 | 1250667.1432
100 | 2679238.0028 | 1250656.7341 | 2679253.23 | 1250649.9075
101 | 2679253.23 | 1250649.9075 | 2679256.3898 | 1250648.4909 | 2679273.3455 | 1250640.9748
102 | 2679273.3455 | 1250640.9748 | 2679290.6022 | 1250633.3254
103 | 2679212.4729 | 1250772.851 | 2679225.2752 | 1250769.5852
104 | 2679268.1332 | 1250802.8941 | 2679276.1465 | 1250801.5045
105 | 2679225.2752 | 1250769.5852 | 2679226.2886 | 1250769.3267
106 | 2679226.2886 | 1250769.3267 | 2679244.3721 | 1250764.7138
107 | 2679249.3594 | 1250763.4416 | 2679244.3721 | 1250764.7138
108 | 2679381.3565 | 1250810.9083 | 2679364.8867 | 1250815.93
109 | 2679341.8696 | 1250856.5655 | 2679342.4666 | 1250857.6409 | 2679343.9479 | 1250859.2064 | 2679345.5787 | 1250860.3179 | 2679346.8047 | 1250860.6568 | 2679348.6728 | 1250860.9598 | 2679350.9522 | 1250860.9903
110 | 2679350.9522 | 1250860.9903 | 2679353.6356 | 1250881.0188 | 2679353.9987 | 1250884.6699
111 | 2679340.9176 | 1250864.5141 | 2679350.9522 | 1250860.9903
112 | 2679331.8444 | 1250743.8371 | 2679331.8444 | 1250743.8371 | 2679333.8009 | 1250747.6884 | 2679335.2341 | 1250753.5893
113 | 2679331.8444 | 1250743.8371 | 2679327.1141 | 1250743.607 | 2679320.8332 | 1250745.2092
114 | 2679320.8332 | 1250745.2092 | 2679303.6768 | 1250749.5856
115 | 2679295.9526 | 1250751.556 | 2679303.6768 | 1250749.5856
116 | 2679293.7734 | 1250752.1119 | 2679295.9526 | 1250751.556
117 | 2679293.7734 | 1250752.1119 | 2679277.836 | 1250756.1774
118 | 2679296.6294 | 1250797.9004 | 2679304.5723 | 1250796.4912
119 | 2679271.1261 | 1250757.889 | 2679277.836 | 1250756.1774
120 | 2679271.1261 | 1250757.889 | 2679270.0924 | 1250758.1527
121 | 2679270.0924 | 1250758.1527 | 2679252.0541 | 1250762.7541
122 | 2679249.3594 | 1250763.4416 | 2679252.0541 | 1250762.7541
123 | 2679296.6294 | 1250797.9004 | 2679283.6051 | 1250800.211 | 2679276.1465 | 1250801.5045
124 | 2679340.9176 | 1250864.5141 | 2679334.3398 | 1250868.0843 | 2679325.6592 | 1250868.9348
125 | 2679325.6592 | 1250868.9348 | 2679312.809 | 1250870.1938
126 | 2679353.9987 | 1250884.6699 | 2679355.2323 | 1250897.0742 | 2679357.3015 | 1250912.8901
127 | 2679300.5065 | 1250871.3991 | 2679312.809 | 1250870.1938
128 | 2679300.5065 | 1250871.3991 | 2679297.9962 | 1250871.645 | 2679286.4089 | 1250873.6115
129 | 2679286.4089 | 1250873.6115 | 2679275.5234 | 1250875.4589
130 | 2679272.6913 | 1250875.9395 | 2679275.5234 | 1250875.4589
131 | 2679359.3654 | 1250926.0843 | 2679358.574 | 1250922.6156 | 2679357.3015 | 1250912.8901
132 | 2679359.3654 | 1250926.0843 | 2679318.8252 | 1250941.1588

## bus_geodata
| x | y | coords
0 | 2679099.4083 | 1250613.2007
1 | 2679109.2186 | 1250631.2789
2 | 2679088.3339 | 1250588.5466
3 | 2679167.7373 | 1250650.7857
4 | 2679082.7018 | 1250568.768
5 | 2679237.1072 | 1250580.3163
6 | 2679248.4979 | 1250575.9407
7 | 2679221.9932 | 1250591.6313
8 | 2679170.0184 | 1250656.3425
9 | 2679186.2009 | 1250641.6317
10 | 2679108.9005 | 1250556.1466
11 | 2679261.9087 | 1250570.789
12 | 2679216.0219 | 1250596.1016
13 | 2679159.4921 | 1250664.1127
14 | 2679200.6452 | 1250634.4704
15 | 2679288.5182 | 1250560.5672
16 | 2679275.2426 | 1250565.6669
17 | 2679131.2971 | 1250679.4081
18 | 2679144.7998 | 1250672.3294
19 | 2679224.0675 | 1250825.4407
20 | 2679239.4775 | 1250822.8125
21 | 2679200.8913 | 1250829.3934
22 | 2679260.1157 | 1250819.2191
23 | 2679204.5578 | 1250847.0776
24 | 2679182.365 | 1250833.0313
25 | 2679267.2977 | 1250817.9469
26 | 2679207.6637 | 1250862.879
27 | 2679227.6262 | 1250809.9475
28 | 2679220.8223 | 1250792.1534
29 | 2679239.6938 | 1250807.826
30 | 2679189.5666 | 1250816.5011
31 | 2679336.1427 | 1250798.3014
32 | 2679325.543 | 1250807.3663
33 | 2679334.1283 | 1250790.313
34 | 2679333.2635 | 1250825.5719
35 | 2679292.0844 | 1250813.5706
36 | 2679330.1624 | 1250824.5367
37 | 2679188.8624 | 1250702.0167
38 | 2679179.6001 | 1250688.4163
39 | 2679190.3546 | 1250701.0804
40 | 2679144.8615 | 1250732.4918
41 | 2679342.6697 | 1250605.2133
42 | 2679322.0202 | 1250597.4645
43 | 2679409.5775 | 1250585.1389
44 | 2679327.9148 | 1250613.5174
45 | 2679361.2196 | 1250612.1358
46 | 2679177.4244 | 1250689.6548
47 | 2679193.8306 | 1250679.8542
48 | 2679284.9671 | 1250814.817
49 | 2679216.2719 | 1250868.6834
50 | 2679402.6295 | 1250652.9068
51 | 2679365.2152 | 1250663.9675
52 | 2679408.8589 | 1250683.7908
53 | 2679152.7088 | 1250822.7673
54 | 2679160.0886 | 1250821.4813
55 | 2679215.2703 | 1250779.3153
56 | 2679247.5028 | 1250806.4718
57 | 2679415.4435 | 1250714.0791
58 | 2679432.7014 | 1250756.2748
59 | 2679411.497 | 1250700.8016
60 | 2679391.2041 | 1250772.3296
61 | 2679343.5741 | 1250787.9266
62 | 2679340.4785 | 1250775.1815
63 | 2679364.6925 | 1250781.5114
64 | 2679339.2441 | 1250848.0069
65 | 2679348.2799 | 1250820.9934
66 | 2679325.0533 | 1250792.6033
67 | 2679124.8449 | 1250730.1038
68 | 2679140.9683 | 1250715.9945
69 | 2679330.3986 | 1250825.4146
70 | 2679193.2915 | 1250731.155
71 | 2679213.5625 | 1250686.4814
72 | 2679291.1486 | 1250606.2811
73 | 2679308.651 | 1250624.2704
74 | 2679351.4973 | 1250617.5683
75 | 2679163.6078 | 1250698.3388
76 | 2679200.8306 | 1250675.6425
77 | 2679141.4688 | 1250715.5685
78 | 2679420.7167 | 1250679.9552
79 | 2679362.5506 | 1250664.7552
80 | 2679383.1193 | 1250713.3789
81 | 2679221.8128 | 1250626.5459
82 | 2679256.3807 | 1250616.445
83 | 2679218.0662 | 1250619.3683
84 | 2679275.9325 | 1250610.7293
85 | 2679248.9658 | 1250602.4466
86 | 2679203.2955 | 1250605.7785
87 | 2679197.1849 | 1250736.2197
88 | 2679208.2577 | 1250762.7488
89 | 2679216.3237 | 1250667.1432
90 | 2679238.0028 | 1250656.7341
91 | 2679253.23 | 1250649.9075
92 | 2679273.3455 | 1250640.9748
93 | 2679290.6022 | 1250633.3254
94 | 2679359.205 | 1250665.7443
95 | 2679212.4729 | 1250772.851
96 | 2679188.7952 | 1250782.7085
97 | 2679268.1332 | 1250802.8941
98 | 2679225.2752 | 1250769.5852
99 | 2679226.2886 | 1250769.3267
100 | 2679376.0844 | 1250714.997
101 | 2679377.467 | 1250736.164
102 | 2679244.3721 | 1250764.7138
103 | 2679212.7247 | 1250885.5484
104 | 2679382.8326 | 1250775.2885
105 | 2679381.3565 | 1250810.9083
106 | 2679364.8867 | 1250815.93
107 | 2679341.8696 | 1250856.5655
108 | 2679350.9522 | 1250860.9903
109 | 2679331.8444 | 1250743.8371
110 | 2679335.2341 | 1250753.5893
111 | 2679320.8332 | 1250745.2092
112 | 2679303.6768 | 1250749.5856
113 | 2679295.9526 | 1250751.556
114 | 2679293.7734 | 1250752.1119
115 | 2679304.5723 | 1250796.4912
116 | 2679277.836 | 1250756.1774
117 | 2679271.1261 | 1250757.889
118 | 2679270.0924 | 1250758.1527
119 | 2679252.0541 | 1250762.7541
120 | 2679249.3594 | 1250763.4416
121 | 2679276.1465 | 1250801.5045
122 | 2679296.6294 | 1250797.9004
123 | 2679340.9176 | 1250864.5141
124 | 2679325.6592 | 1250868.9348
125 | 2679353.9987 | 1250884.6699
126 | 2679312.809 | 1250870.1938
127 | 2679300.5065 | 1250871.3991
128 | 2679286.4089 | 1250873.6115
129 | 2679275.5234 | 1250875.4589
130 | 2679357.3015 | 1250912.8901
131 | 2679272.6913 | 1250875.9395
132 | 2679359.3654 | 1250926.0843
133 | 2679318.8252 | 1250941.1588
134 | 2679212.4729 | 1250772.851

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97092 | -0.56122 | 0.0070318 | 0.0017623
1 | 0.97112 | -0.55742 | 0 | 0
2 | 0.97085 | -0.5627 | 0 | 0
3 | 0.97257 | -0.52872 | 0 | 0
4 | 0.97079 | -0.56383 | 0 | 0
5 | 0.97123 | -0.55513 | 0 | 0
6 | 0.97091 | -0.56152 | 0.0071127 | 0.0017826
7 | 0.97173 | -0.54526 | 0.0049622 | 0.0012436
8 | 0.97253 | -0.52951 | 0 | 0
9 | 0.9729 | -0.52224 | 0.0024846 | 0.0006227
10 | 0.97071 | -0.56542 | 0.0029536 | 0.00074024
11 | 0.97062 | -0.56716 | 0.0071196 | 0.0017843
12 | 0.97196 | -0.54068 | 0 | 0
13 | 0.97244 | -0.53122 | 0.0024703 | 0.00061912
14 | 0.97319 | -0.51643 | 0.0024461 | 0.00061304
15 | 0.97034 | -0.57274 | 0.0070595 | 0.0017693
16 | 0.97043 | -0.57088 | 0.007031 | 0.0017621
17 | 0.97233 | -0.53334 | 0.0024382 | 0.00061106
18 | 0.97237 | -0.53265 | 0.0021777 | 0.00054578
19 | 0.97779 | -0.42704 | 0.0074581 | 0.0018692
20 | 0.97826 | -0.41793 | 0.0023456 | 0.00058785
21 | 0.97726 | -0.43754 | 0 | 0
22 | 0.97892 | -0.40485 | 0.0017392 | 0.00043589
23 | 0.97688 | -0.44492 | 0 | 0
24 | 0.97722 | -0.43827 | 0.0021145 | 0.00052993
25 | 0.97917 | -0.40007 | 0.0017254 | 0.00043242
26 | 0.9765 | -0.45239 | 0.0044884 | 0.0011249
27 | 0.99009 | -0.18841 | 0 | 0
28 | 0.99121 | -0.16693 | 0.0067234 | 0.001685
29 | 0.98942 | -0.20115 | 0.0017781 | 0.00044564
30 | 0.98955 | -0.19881 | 0.0069431 | 0.0017401
31 | 0.98336 | -0.31836 | 0 | 0
32 | 0.98136 | -0.35717 | 0 | 0
33 | 0.98423 | -0.30142 | 0.001976 | 0.00049522
34 | 0.97993 | -0.38515 | 0 | 0
35 | 0.98006 | -0.38258 | 0.0017128 | 0.00042928
36 | 0.9813 | -0.3583 | 0.0017766 | 0.00044525
37 | 0.98846 | -0.21952 | 0 | 0
38 | 0.98782 | -0.23188 | 0 | 0
39 | 0.98853 | -0.21817 | 0 | 0
40 | 0.98832 | -0.22218 | 0.0027833 | 0.00069756
41 | 0.98181 | -0.34793 | 0 | 0
42 | 0.98083 | -0.36687 | 0.0058681 | 0.0014707
43 | 0.98145 | -0.35494 | 0 | 0
44 | 0.98231 | -0.33822 | 0.0026895 | 0.00067405
45 | 0.98121 | -0.35959 | 0.003179 | 0.00079674
46 | 0.98779 | -0.23235 | 0 | 0
47 | 0.98722 | -0.24332 | 0.00079668 | 0.00019967
48 | 0.9798 | -0.38776 | 0.0017169 | 0.0004303
49 | 0.97632 | -0.45606 | 0.013428 | 0.0033653
50 | 0.97837 | -0.41588 | 0 | 0
51 | 0.97823 | -0.4187 | 0.0014016 | 0.00035128
52 | 0.97849 | -0.41361 | 0 | 0
53 | 0.98931 | -0.20354 | 0.0027417 | 0.00068713
54 | 0.98933 | -0.20317 | 0.0054494 | 0.0013657
55 | 0.99206 | -0.15063 | 0 | 0
56 | 0.989 | -0.20932 | 0.0020769 | 0.00052051
57 | 0.97924 | -0.3989 | 0 | 0
58 | 0.98067 | -0.37073 | 0 | 0
59 | 0.97882 | -0.40701 | 0.011868 | 0.0029743
60 | 0.982 | -0.34481 | 0.0031921 | 0.00080002
61 | 0.98383 | -0.30926 | 0 | 0
62 | 0.98379 | -0.31001 | 0.0031953 | 0.00080083
63 | 0.98298 | -0.32581 | 0.0031281 | 0.00078397
64 | 0.97875 | -0.40819 | 0.0053686 | 0.0013455
65 | 0.97971 | -0.38939 | 0.0050668 | 0.0012699
66 | 0.98493 | -0.28788 | 0.0020998 | 0.00052627
67 | 0.98737 | -0.24063 | 0.00247 | 0.00061903
68 | 0.98741 | -0.23969 | 0.0039772 | 0.00099677
69 | 0.9813 | -0.35833 | 0.0017314 | 0.00043393
70 | 0.99051 | -0.18026 | 0.0055063 | 0.00138
71 | 0.98841 | -0.22049 | 0.0047372 | 0.0011872
72 | 0.9783 | -0.41626 | 0.0068334 | 0.0017126
73 | 0.98298 | -0.32523 | 0.0015505 | 0.0003886
74 | 0.9812 | -0.35988 | 0.0014515 | 0.00036379
75 | 0.98763 | -0.23544 | 0.0022967 | 0.0005756
76 | 0.98693 | -0.24892 | 0.00075867 | 0.00019014
77 | 0.98742 | -0.23961 | 0.0018563 | 0.00046524
78 | 0.97842 | -0.41486 | 0.005503 | 0.0013792
79 | 0.97822 | -0.41883 | 0.0011561 | 0.00028974
80 | 0.97794 | -0.42434 | 0 | 0
81 | 0.97366 | -0.50724 | 0 | 0
82 | 0.97579 | -0.46524 | 0 | 0
83 | 0.97334 | -0.51346 | 0.0074814 | 0.001875
84 | 0.97714 | -0.43876 | 0.0067359 | 0.0016882
85 | 0.97568 | -0.46738 | 0.0073654 | 0.0018459
86 | 0.97246 | -0.53086 | 0.00096436 | 0.00024169
87 | 0.99078 | -0.17498 | 0 | 0
88 | 0.99202 | -0.15131 | 0.0031809 | 0.00079721
89 | 0.9863 | -0.26096 | 0.0025674 | 0.00064346
90 | 0.98547 | -0.277 | 0.0038205 | 0.00095751
91 | 0.98491 | -0.28776 | 0.0030741 | 0.00077043
92 | 0.9842 | -0.30156 | 0.002259 | 0.00056615
93 | 0.9836 | -0.31316 | 0.0029378 | 0.00073628
94 | 0.97822 | -0.41892 | 0.0014023 | 0.00035146
95 | 0.9925 | -0.1421 | 0 | 0
96 | 0.99186 | -0.15443 | 0.0079831 | 0.0020008
97 | 0.98789 | -0.23067 | 0.0022233 | 0.0005572
98 | 0.99392 | -0.11505 | 0.0070917 | 0.0017774
99 | 0.99404 | -0.11287 | 0.002249 | 0.00056364
100 | 0.9779 | -0.42514 | 0.0060802 | 0.0015238
101 | 0.9778 | -0.42708 | 0.0047633 | 0.0011938
102 | 0.99609 | -0.073773 | 0.0021527 | 0.00053953
103 | 0.97619 | -0.45865 | 0.0044635 | 0.0011187
104 | 0.98229 | -0.33913 | 0.0030965 | 0.00077605
105 | 0.97948 | -0.39398 | 0.0047712 | 0.0011958
106 | 0.97956 | -0.39248 | 0.0050399 | 0.0012631
107 | 0.97834 | -0.41624 | 0 | 0
108 | 0.97785 | -0.42591 | 0 | 0
109 | 0.99901 | -0.019009 | 0.0086952 | 0.0021792
110 | 0.99899 | -0.019377 | 0.0020228 | 0.00050697
111 | 0.99912 | -0.01691 | 0.0075743 | 0.0018983
112 | 0.99941 | -0.011256 | 0.0020046 | 0.0005024
113 | 0.99956 | -0.008433 | 0.0021139 | 0.00052979
114 | 0.99961 | -0.0075538 | 0.0039264 | 0.00098406
115 | 0.98598 | -0.26753 | 0.0018834 | 0.00047203
116 | 1 | 0 | -0.40772 | -0.10435
117 | 0.9992 | -0.015022 | 0.0050292 | 0.0012604
118 | 0.99908 | -0.017308 | 0.0021434 | 0.00053719
119 | 0.99698 | -0.057041 | 0.0022613 | 0.00056673
120 | 0.99667 | -0.062955 | 0.0044914 | 0.0011257
121 | 0.98746 | -0.23887 | 0.0022961 | 0.00057547
122 | 0.98639 | -0.25958 | 0.0020027 | 0.00050193
123 | 0.97761 | -0.43064 | 0 | 0
124 | 0.97724 | -0.43788 | 0.0040242 | 0.0010086
125 | 0.9773 | -0.4367 | 0.0041753 | 0.0010464
126 | 0.977 | -0.44269 | 0.0040404 | 0.0010126
127 | 0.97681 | -0.4464 | 0.0045873 | 0.0011497
128 | 0.97665 | -0.44948 | 0.0044729 | 0.001121
129 | 0.97658 | -0.45096 | 0.0030095 | 0.00075425
130 | 0.97676 | -0.44739 | 0.010614 | 0.0026601
131 | 0.97657 | -0.45119 | 0.0043291 | 0.001085
132 | 0.97663 | -0.44982 | 0 | 0
133 | 0.97623 | -0.45772 | 0.009981 | 0.0025015
134 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.009986 | -0.002502 | 0.0099878 | 0.0025029 | 1.8066e-06 | 9.0179e-07 | 0.015304 | 0.015304 | 0.015304 | 0.97092 | -0.56122 | 0.97112 | -0.55742 | 4.2044
1 | 0.0029542 | 0.00073967 | -0.002954 | -0.00073987 | 2.0877e-07 | -2.0229e-07 | 0.0045272 | 0.0045274 | 0.0045274 | 0.97092 | -0.56122 | 0.97085 | -0.5627 | 1.2438
2 | -0.0099878 | -0.0025029 | 0.010001 | 0.0025097 | 1.367e-05 | 6.8204e-06 | 0.015304 | 0.015303 | 0.015304 | 0.97112 | -0.55742 | 0.97257 | -0.52872 | 4.2044
3 | 0.002954 | 0.00073987 | -0.0029538 | -0.00074002 | 1.5811e-07 | -1.5315e-07 | 0.0045274 | 0.0045275 | 0.0045275 | 0.97085 | -0.5627 | 0.97079 | -0.56383 | 1.2438
4 | 0.0070874 | 0.0017761 | -0.0070871 | -0.001776 | 2.6478e-07 | 9.4945e-08 | 0.010844 | 0.010844 | 0.010844 | 0.97257 | -0.52872 | 0.97253 | -0.52951 | 2.979
5 | -0.017089 | -0.0042858 | 0.017094 | 0.004289 | 5.2834e-06 | 3.1255e-06 | 0.026147 | 0.026147 | 0.026147 | 0.97257 | -0.52872 | 0.9729 | -0.52224 | 7.1832
6 | 0.0029538 | 0.00074002 | -0.0029536 | -0.00074024 | 2.2354e-07 | -2.1646e-07 | 0.0045275 | 0.0045276 | 0.0045276 | 0.97079 | -0.56383 | 0.97071 | -0.56542 | 1.2438
7 | 0.02834 | 0.0071088 | -0.028332 | -0.0071035 | 8.6276e-06 | 5.3707e-06 | 0.043422 | 0.043422 | 0.043422 | 0.97123 | -0.55513 | 0.97091 | -0.56152 | 11.9292
8 | -0.02834 | -0.0071088 | 0.028354 | 0.0071172 | 1.3349e-05 | 8.3098e-06 | 0.043422 | 0.043422 | 0.043422 | 0.97123 | -0.55513 | 0.97173 | -0.54526 | 11.9292
9 | 0.021219 | 0.0053209 | -0.021213 | -0.0053174 | 5.6979e-06 | 3.469e-06 | 0.032521 | 0.032521 | 0.032521 | 0.97091 | -0.56152 | 0.97062 | -0.56716 | 8.9344
10 | -0.033316 | -0.0083608 | 0.033323 | 0.0083654 | 7.2815e-06 | 4.5677e-06 | 0.051021 | 0.051021 | 0.051021 | 0.97173 | -0.54526 | 0.97196 | -0.54068 | 14.0167
11 | 0.0070871 | 0.001776 | -0.0070865 | -0.0017758 | 5.7691e-07 | 2.0689e-07 | 0.010844 | 0.010844 | 0.010844 | 0.97253 | -0.52951 | 0.97244 | -0.53122 | 2.979
12 | -0.019579 | -0.0049117 | 0.019584 | 0.0049149 | 5.4219e-06 | 3.2698e-06 | 0.029947 | 0.029947 | 0.029947 | 0.9729 | -0.52224 | 0.97319 | -0.51643 | 8.2272
13 | 0.014094 | 0.0035331 | -0.014091 | -0.0035316 | 2.5006e-06 | 1.4239e-06 | 0.021607 | 0.021607 | 0.021607 | 0.97062 | -0.56716 | 0.97043 | -0.57088 | 5.9359
14 | -0.033323 | -0.0083654 | 0.033339 | 0.0083751 | 1.5607e-05 | 9.7899e-06 | 0.051021 | 0.051021 | 0.051021 | 0.97196 | -0.54068 | 0.97246 | -0.53086 | 14.0167
15 | 0.0046162 | 0.0011567 | -0.0046159 | -0.0011567 | 3.1551e-07 | -7.2568e-09 | 0.0070636 | 0.0070637 | 0.0070637 | 0.97244 | -0.53122 | 0.97237 | -0.53265 | 1.9406
16 | -0.02203 | -0.005528 | 0.02204 | 0.0055339 | 9.655e-06 | 5.8972e-06 | 0.033687 | 0.033687 | 0.033687 | 0.97319 | -0.51643 | 0.97366 | -0.50724 | 9.2546
17 | -0.0070595 | -0.0017693 | 0.0070601 | 0.0017695 | 6.2501e-07 | 2.2432e-07 | 0.010826 | 0.010826 | 0.010826 | 0.97034 | -0.57274 | 0.97043 | -0.57088 | 2.9741
18 | -0.0024382 | -0.00061106 | 0.0024382 | 0.00061092 | 7.9594e-08 | -1.3817e-07 | 0.0037312 | 0.0037312 | 0.0037312 | 0.97233 | -0.53334 | 0.97237 | -0.53265 | 1.0251
19 | -0.031984 | -0.0080269 | 0.031998 | 0.0080356 | 1.3891e-05 | 8.6938e-06 | 0.048678 | 0.048678 | 0.048678 | 0.97779 | -0.42704 | 0.97826 | -0.41793 | 13.373
20 | 0.024526 | 0.0061577 | -0.024514 | -0.0061501 | 1.2285e-05 | 7.5675e-06 | 0.037328 | 0.037328 | 0.037328 | 0.97779 | -0.42704 | 0.97726 | -0.43754 | 10.2549
21 | -0.034344 | -0.0086234 | 0.034365 | 0.0086369 | 2.1443e-05 | 1.346e-05 | 0.052245 | 0.052245 | 0.052245 | 0.97826 | -0.41793 | 0.97892 | -0.40485 | 14.3531
22 | 0.022399 | 0.0056204 | -0.022391 | -0.0056156 | 7.879e-06 | 4.8164e-06 | 0.034108 | 0.034108 | 0.034108 | 0.97726 | -0.43754 | 0.97688 | -0.44492 | 9.3705
23 | 0.0021145 | 0.00052974 | -0.0021145 | -0.00052993 | 7.3434e-08 | -1.8968e-07 | 0.0032196 | 0.0032197 | 0.0032197 | 0.97726 | -0.43754 | 0.97722 | -0.43827 | 0.88453
24 | -0.036104 | -0.0090728 | 0.036112 | 0.0090779 | 8.2405e-06 | 5.1822e-06 | 0.054889 | 0.054889 | 0.054889 | 0.97892 | -0.40485 | 0.97917 | -0.40007 | 15.0794
25 | 0.022391 | 0.0056156 | -0.022383 | -0.0056107 | 7.9642e-06 | 4.8686e-06 | 0.034108 | 0.034109 | 0.034109 | 0.97688 | -0.44492 | 0.9765 | -0.45239 | 9.3705
26 | -0.037838 | -0.0095104 | 0.03786 | 0.0095244 | 2.2257e-05 | 1.4019e-05 | 0.057511 | 0.057511 | 0.057511 | 0.97917 | -0.40007 | 0.9798 | -0.38776 | 15.7997
27 | 0.017895 | 0.0044858 | -0.017892 | -0.0044839 | 3.1352e-06 | 1.8659e-06 | 0.027269 | 0.027269 | 0.027269 | 0.9765 | -0.45239 | 0.97632 | -0.45606 | 7.4915
28 | -0.19228 | -0.048888 | 0.19248 | 0.049015 | 0.00019923 | 0.00012677 | 0.28922 | 0.28922 | 0.28922 | 0.99009 | -0.18841 | 0.99121 | -0.16693 | 26.4857
29 | 0.17713 | 0.04509 | -0.17702 | -0.045021 | 0.00010875 | 6.9126e-05 | 0.26646 | 0.26646 | 0.26646 | 0.99009 | -0.18841 | 0.98942 | -0.20115 | 24.4015
30 | 0.015143 | 0.0037979 | -0.015136 | -0.0037936 | 7.5025e-06 | 4.3052e-06 | 0.02276 | 0.02276 | 0.02276 | 0.99009 | -0.18841 | 0.98955 | -0.19881 | 6.2529
31 | -0.1992 | -0.0507 | 0.19936 | 0.050799 | 0.00015664 | 9.9708e-05 | 0.29932 | 0.29932 | 0.29932 | 0.99121 | -0.16693 | 0.99206 | -0.15063 | 27.41
32 | 0.17525 | 0.044575 | -0.17518 | -0.044531 | 6.8938e-05 | 4.3815e-05 | 0.26379 | 0.26379 | 0.26379 | 0.98942 | -0.20115 | 0.989 | -0.20932 | 24.1566
33 | 0.0081928 | 0.0020535 | -0.0081911 | -0.0020528 | 1.7016e-06 | 7.0505e-07 | 0.01232 | 0.01232 | 0.01232 | 0.98955 | -0.19881 | 0.98933 | -0.20317 | 3.3846
34 | 0.1148 | 0.029008 | -0.11459 | -0.028872 | 0.00021316 | 0.00013618 | 0.1738 | 0.1738 | 0.1738 | 0.98336 | -0.31836 | 0.98136 | -0.35717 | 47.7486
35 | -0.1148 | -0.029008 | 0.1149 | 0.029067 | 9.3309e-05 | 5.9613e-05 | 0.1738 | 0.1738 | 0.1738 | 0.98336 | -0.31836 | 0.98423 | -0.30142 | 47.7486
36 | 0.069732 | 0.017571 | -0.069639 | -0.017511 | 9.3186e-05 | 5.9359e-05 | 0.10577 | 0.10577 | 0.10577 | 0.98136 | -0.35717 | 0.97993 | -0.38515 | 29.0569
37 | 0.04135 | 0.010422 | -0.0413 | -0.01039 | 5.0205e-05 | 3.1702e-05 | 0.062719 | 0.062719 | 0.062719 | 0.98136 | -0.35717 | 0.98006 | -0.38258 | 17.2305
38 | 0.0035081 | 0.00087906 | -0.003508 | -0.00087917 | 1.8867e-07 | -1.039e-07 | 0.0053193 | 0.0053193 | 0.0053193 | 0.98136 | -0.35717 | 0.9813 | -0.3583 | 1.4614
39 | -0.16185 | -0.040907 | 0.16196 | 0.040974 | 0.00010519 | 6.7081e-05 | 0.24482 | 0.24482 | 0.24482 | 0.98423 | -0.30142 | 0.98493 | -0.28788 | 33.6293
40 | 0.04498 | 0.011344 | -0.044964 | -0.011333 | 1.6862e-05 | 1.0668e-05 | 0.068029 | 0.068029 | 0.068029 | 0.98423 | -0.30142 | 0.98383 | -0.30926 | 18.6894
41 | 0.054756 | 0.01378 | -0.054696 | -0.013742 | 6.0224e-05 | 3.8251e-05 | 0.083167 | 0.083168 | 0.083168 | 0.97993 | -0.38515 | 0.97875 | -0.40819 | 22.8482
42 | 0.014883 | 0.0037312 | -0.01488 | -0.0037295 | 3.0068e-06 | 1.7266e-06 | 0.0226 | 0.0226 | 0.0226 | 0.97993 | -0.38515 | 0.97971 | -0.38939 | 6.2087
43 | 0.039587 | 0.0099608 | -0.039577 | -0.0099547 | 9.793e-06 | 6.1765e-06 | 0.060118 | 0.060118 | 0.060118 | 0.98006 | -0.38258 | 0.9798 | -0.38776 | 16.516
44 | 0.0017314 | 0.00043392 | -0.0017314 | -0.00043393 | 2.3498e-09 | -9.9807e-09 | 0.0026254 | 0.0026254 | 0.0026254 | 0.9813 | -0.3583 | 0.9813 | -0.35833 | 0.72128
45 | 0.12762 | 0.032512 | -0.12755 | -0.032464 | 7.6069e-05 | 4.8052e-05 | 0.19231 | 0.19231 | 0.19231 | 0.98846 | -0.21952 | 0.98782 | -0.23188 | 17.6109
46 | -0.13041 | -0.03321 | 0.13041 | 0.033215 | 8.4851e-06 | 5.3628e-06 | 0.1965 | 0.1965 | 0.1965 | 0.98846 | -0.21952 | 0.98853 | -0.21817 | 17.9946
47 | 0.0027836 | 0.0006971 | -0.0027833 | -0.00069756 | 3.5282e-07 | -4.6091e-07 | 0.0041903 | 0.0041905 | 0.0041905 | 0.98846 | -0.21952 | 0.98832 | -0.22218 | 1.1512
48 | 0.010604 | 0.0026581 | -0.010603 | -0.0026579 | 2.3901e-07 | 1.2099e-07 | 0.015973 | 0.015973 | 0.015973 | 0.98782 | -0.23188 | 0.98779 | -0.23235 | 4.3883
49 | 0.11694 | 0.029806 | -0.11688 | -0.029766 | 6.4552e-05 | 4.0676e-05 | 0.17634 | 0.17634 | 0.17634 | 0.98782 | -0.23188 | 0.98722 | -0.24332 | 16.1481
50 | -0.13515 | -0.034402 | 0.1354 | 0.034559 | 0.0002475 | 0.00015656 | 0.20363 | 0.20363 | 0.20363 | 0.98853 | -0.21817 | 0.99051 | -0.18026 | 18.6476
51 | 0.0047377 | 0.0011872 | -0.0047372 | -0.0011872 | 5.2298e-07 | -1.6791e-08 | 0.0071315 | 0.0071316 | 0.0071316 | 0.98853 | -0.21817 | 0.98841 | -0.22049 | 1.9592
52 | 0.091257 | 0.023144 | -0.091174 | -0.023091 | 8.3005e-05 | 5.2539e-05 | 0.13841 | 0.13841 | 0.13841 | 0.98181 | -0.34793 | 0.98083 | -0.36687 | 19.0119
53 | 0.0046332 | 0.0011603 | -0.0046316 | -0.0011604 | 1.5475e-06 | -6.7633e-08 | 0.0070217 | 0.007022 | 0.007022 | 0.98181 | -0.34793 | 0.98145 | -0.35494 | 1.9291
54 | -0.09589 | -0.024304 | 0.095935 | 0.024332 | 4.476e-05 | 2.8004e-05 | 0.14543 | 0.14543 | 0.14543 | 0.98181 | -0.34793 | 0.98231 | -0.33822 | 13.3176
55 | 0.085306 | 0.02162 | -0.085104 | -0.021492 | 0.00020193 | 0.00012883 | 0.1295 | 0.1295 | 0.1295 | 0.98083 | -0.36687 | 0.9783 | -0.41626 | 35.578
56 | 0.0046316 | 0.0011604 | -0.0046306 | -0.0011604 | 1.0241e-06 | -4.4271e-08 | 0.007022 | 0.0070223 | 0.0070223 | 0.98145 | -0.35494 | 0.98121 | -0.35959 | 1.9292
57 | -0.098624 | -0.025006 | 0.098686 | 0.025045 | 6.1641e-05 | 3.8612e-05 | 0.1495 | 0.1495 | 0.1495 | 0.98231 | -0.33822 | 0.98298 | -0.32523 | 13.6906
58 | 0.0014516 | 0.00036366 | -0.0014515 | -0.00036379 | 2.0237e-08 | -1.2772e-07 | 0.0022012 | 0.0022013 | 0.0022013 | 0.98121 | -0.35959 | 0.9812 | -0.35988 | 0.60475
59 | 0.010603 | 0.0026579 | -0.010602 | -0.0026571 | 1.5618e-06 | 7.9064e-07 | 0.015973 | 0.015973 | 0.015973 | 0.98779 | -0.23235 | 0.98763 | -0.23544 | 4.3883
60 | 0.11608 | 0.029566 | -0.11605 | -0.029546 | 3.1322e-05 | 1.9733e-05 | 0.17514 | 0.17514 | 0.17514 | 0.98722 | -0.24332 | 0.98693 | -0.24892 | 16.0382
61 | 0.0044641 | 0.0011186 | -0.0044635 | -0.0011187 | 5.5069e-07 | -4.4214e-08 | 0.0068037 | 0.0068038 | 0.0068038 | 0.97632 | -0.45606 | 0.97619 | -0.45865 | 1.8692
62 | 0.0039606 | 0.00099227 | -0.0039601 | -0.00099242 | 5.3087e-07 | -1.5012e-07 | 0.0060236 | 0.0060238 | 0.0060238 | 0.97837 | -0.41588 | 0.97823 | -0.4187 | 1.6549
63 | -0.0039606 | -0.00099227 | 0.003961 | 0.00099214 | 4.2869e-07 | -1.2135e-07 | 0.0060236 | 0.0060234 | 0.0060236 | 0.97837 | -0.41588 | 0.97849 | -0.41361 | 1.6548
64 | 0.0025584 | 0.00064113 | -0.0025584 | -0.00064116 | 1.5781e-08 | -2.4784e-08 | 0.0038917 | 0.0038917 | 0.0038917 | 0.97823 | -0.4187 | 0.97822 | -0.41883 | 1.0691
65 | -0.020314 | -0.0050919 | 0.020321 | 0.0050958 | 6.3949e-06 | 3.8682e-06 | 0.030893 | 0.030893 | 0.030893 | 0.97849 | -0.41361 | 0.97882 | -0.40701 | 8.487
66 | 0.01085 | 0.0027205 | -0.010844 | -0.0027177 | 5.546e-06 | 2.8675e-06 | 0.0165 | 0.0165 | 0.0165 | 0.97849 | -0.41361 | 0.97794 | -0.42434 | 4.5331
67 | 0.0055034 | 0.0013792 | -0.005503 | -0.0013792 | 3.2876e-07 | 5.3198e-08 | 0.0083692 | 0.0083692 | 0.0083692 | 0.97849 | -0.41361 | 0.97842 | -0.41486 | 2.2992
68 | -0.0027417 | -0.00068713 | 0.0027417 | 0.00068706 | 4.777e-08 | -6.5616e-08 | 0.0041237 | 0.0041237 | 0.0041237 | 0.98931 | -0.20354 | 0.98933 | -0.20317 | 1.1329
69 | -0.20734 | -0.052801 | 0.20743 | 0.052855 | 8.5287e-05 | 5.4311e-05 | 0.31129 | 0.31129 | 0.31129 | 0.99206 | -0.15063 | 0.9925 | -0.1421 | 28.5067
70 | 0.0079845 | 0.0020013 | -0.0079831 | -0.0020008 | 1.4444e-06 | 5.7776e-07 | 0.011976 | 0.011976 | 0.011976 | 0.99206 | -0.15063 | 0.99186 | -0.15443 | 3.2902
71 | 0.1731 | 0.044011 | -0.17292 | -0.043898 | 0.00017784 | 0.00011301 | 0.26067 | 0.26067 | 0.26067 | 0.989 | -0.20932 | 0.98789 | -0.23067 | 23.8705
72 | -0.032201 | -0.0080779 | 0.032244 | 0.008105 | 4.3306e-05 | 2.7108e-05 | 0.048934 | 0.048934 | 0.048934 | 0.97924 | -0.3989 | 0.98067 | -0.37073 | 13.4434
73 | 0.032201 | 0.0080779 | -0.032188 | -0.0080702 | 1.2438e-05 | 7.7862e-06 | 0.048934 | 0.048934 | 0.048934 | 0.97924 | -0.3989 | 0.97882 | -0.40701 | 13.4435
74 | -0.032244 | -0.008105 | 0.032284 | 0.0081301 | 3.9963e-05 | 2.5014e-05 | 0.048934 | 0.048934 | 0.048934 | 0.98067 | -0.37073 | 0.982 | -0.34481 | 13.4434
75 | -0.035476 | -0.0089301 | 0.035486 | 0.0089361 | 9.6269e-06 | 6.0488e-06 | 0.053771 | 0.053771 | 0.053771 | 0.982 | -0.34481 | 0.98229 | -0.33913 | 14.7722
76 | 0.0031955 | 0.00080074 | -0.0031953 | -0.00080083 | 1.1489e-07 | -9.3014e-08 | 0.004833 | 0.0048331 | 0.0048331 | 0.98383 | -0.30926 | 0.98379 | -0.31001 | 1.3278
77 | 0.041768 | 0.010533 | -0.041735 | -0.010512 | 3.3067e-05 | 2.0882e-05 | 0.063196 | 0.063196 | 0.063196 | 0.98383 | -0.30926 | 0.98298 | -0.32581 | 17.3617
78 | 0.038607 | 0.0097277 | -0.038582 | -0.0097122 | 2.4582e-05 | 1.5489e-05 | 0.058461 | 0.058461 | 0.058461 | 0.98298 | -0.32581 | 0.98229 | -0.33913 | 16.0608
79 | 0.049327 | 0.012396 | -0.049308 | -0.012384 | 1.8948e-05 | 1.2014e-05 | 0.075005 | 0.075006 | 0.075006 | 0.97875 | -0.40819 | 0.97834 | -0.41624 | 20.6059
80 | 0.0098128 | 0.0024596 | -0.0098114 | -0.0024589 | 1.4462e-06 | 7.0698e-07 | 0.014904 | 0.014904 | 0.014904 | 0.97971 | -0.38939 | 0.97956 | -0.39248 | 4.0945
81 | -0.16406 | -0.0415 | 0.16422 | 0.041602 | 0.00016032 | 0.00010181 | 0.24799 | 0.24799 | 0.24799 | 0.98493 | -0.28788 | 0.98598 | -0.26753 | 22.7101
82 | -0.00247 | -0.00061903 | 0.0024701 | 0.00061883 | 1.1133e-07 | -2.0281e-07 | 0.0037224 | 0.0037223 | 0.0037224 | 0.98737 | -0.24063 | 0.98741 | -0.23969 | 1.0226
83 | -0.0064472 | -0.0016156 | 0.0064473 | 0.0016156 | 2.3268e-08 | 6.4837e-09 | 0.0097158 | 0.0097158 | 0.0097158 | 0.98741 | -0.23969 | 0.98742 | -0.23961 | 2.6692
84 | -0.14091 | -0.035939 | 0.14094 | 0.035961 | 3.594e-05 | 2.2754e-05 | 0.2119 | 0.2119 | 0.2119 | 0.99051 | -0.18026 | 0.99078 | -0.17498 | 19.4051
85 | 0.07827 | 0.019779 | -0.078186 | -0.019725 | 8.4341e-05 | 5.3779e-05 | 0.11911 | 0.11911 | 0.11911 | 0.9783 | -0.41626 | 0.97714 | -0.43876 | 32.7226
86 | -0.10024 | -0.025433 | 0.10029 | 0.02547 | 5.8209e-05 | 3.6485e-05 | 0.15185 | 0.15185 | 0.15185 | 0.98298 | -0.32523 | 0.9836 | -0.31316 | 13.9055
87 | 0.0083052 | 0.0020815 | -0.0083036 | -0.0020808 | 1.6481e-06 | 6.9569e-07 | 0.012513 | 0.012513 | 0.012513 | 0.98763 | -0.23544 | 0.98742 | -0.23961 | 3.4377
88 | 0.11529 | 0.029356 | -0.11522 | -0.029314 | 6.6893e-05 | 4.2134e-05 | 0.17399 | 0.17399 | 0.17399 | 0.98693 | -0.24892 | 0.9863 | -0.26096 | 15.9334
89 | 0.0014023 | 0.00035142 | -0.0014023 | -0.00035146 | 5.9531e-09 | -3.9988e-08 | 0.0021332 | 0.0021332 | 0.0021332 | 0.97822 | -0.41883 | 0.97822 | -0.41892 | 0.58603
90 | 0.0060804 | 0.0015239 | -0.0060802 | -0.0015238 | 2.3105e-07 | 5.7562e-08 | 0.0092519 | 0.0092519 | 0.0092519 | 0.97794 | -0.42434 | 0.9779 | -0.42514 | 2.5417
91 | 0.0047639 | 0.0011938 | -0.0047633 | -0.0011938 | 6.2164e-07 | 2.0563e-09 | 0.0072486 | 0.0072487 | 0.0072487 | 0.97794 | -0.42434 | 0.9778 | -0.42708 | 1.9914
92 | -0.063865 | -0.016051 | 0.063994 | 0.016133 | 0.00012835 | 8.1697e-05 | 0.09762 | 0.09762 | 0.09762 | 0.97366 | -0.50724 | 0.97579 | -0.46524 | 26.8187
93 | 0.041825 | 0.010518 | -0.041813 | -0.01051 | 1.2411e-05 | 7.8421e-06 | 0.063933 | 0.063933 | 0.063933 | 0.97366 | -0.50724 | 0.97334 | -0.51346 | 17.5641
94 | -0.07136 | -0.017979 | 0.07145 | 0.018037 | 9.0512e-05 | 5.7673e-05 | 0.10885 | 0.10885 | 0.10885 | 0.97579 | -0.46524 | 0.97714 | -0.43876 | 29.9046
95 | 0.0073661 | 0.0018462 | -0.0073654 | -0.0018459 | 7.4954e-07 | 2.8185e-07 | 0.011233 | 0.011233 | 0.011233 | 0.97579 | -0.46524 | 0.97568 | -0.46738 | 3.086
96 | 0.034331 | 0.0086347 | -0.034303 | -0.0086168 | 2.8515e-05 | 1.7907e-05 | 0.052496 | 0.052496 | 0.052496 | 0.97334 | -0.51346 | 0.97246 | -0.53086 | 14.422
97 | -0.14094 | -0.035961 | 0.1411 | 0.036064 | 0.00016135 | 0.00010215 | 0.2119 | 0.2119 | 0.2119 | 0.99078 | -0.17498 | 0.99202 | -0.15131 | 19.405
98 | -0.14428 | -0.036861 | 0.14435 | 0.036902 | 6.4238e-05 | 4.0688e-05 | 0.21667 | 0.21667 | 0.21667 | 0.99202 | -0.15131 | 0.9925 | -0.1421 | 19.8419
99 | 0.11266 | 0.028671 | -0.11257 | -0.028616 | 8.7041e-05 | 5.4786e-05 | 0.17012 | 0.17012 | 0.17012 | 0.9863 | -0.26096 | 0.98547 | -0.277 | 15.5788
100 | 0.10875 | 0.027658 | -0.10869 | -0.027623 | 5.6344e-05 | 3.5423e-05 | 0.16435 | 0.16435 | 0.16435 | 0.98547 | -0.277 | 0.98491 | -0.28776 | 15.0505
101 | 0.10562 | 0.026852 | -0.10555 | -0.026808 | 7.0174e-05 | 4.4072e-05 | 0.15971 | 0.15971 | 0.15971 | 0.98491 | -0.28776 | 0.9842 | -0.30156 | 14.6252
102 | 0.10329 | 0.026242 | -0.10323 | -0.026206 | 5.7637e-05 | 3.6168e-05 | 0.15629 | 0.15629 | 0.15629 | 0.9842 | -0.30156 | 0.9836 | -0.31316 | 14.3125
103 | -0.35177 | -0.089757 | 0.35223 | 0.090051 | 0.00046036 | 0.00029412 | 0.52797 | 0.52797 | 0.52797 | 0.9925 | -0.1421 | 0.99392 | -0.11505 | 48.3486
104 | 0.1707 | 0.043341 | -0.17063 | -0.043298 | 6.7312e-05 | 4.2767e-05 | 0.25732 | 0.25732 | 0.25732 | 0.98789 | -0.23067 | 0.98746 | -0.23887 | 23.5638
105 | -0.35933 | -0.091828 | 0.35936 | 0.091852 | 3.7922e-05 | 2.4229e-05 | 0.53858 | 0.53858 | 0.53858 | 0.99392 | -0.11505 | 0.99404 | -0.11287 | 49.3208
106 | -0.36161 | -0.092416 | 0.3623 | 0.092854 | 0.00068517 | 0.00043778 | 0.54195 | 0.54195 | 0.54195 | 0.99404 | -0.11287 | 0.99609 | -0.073773 | 49.6291
107 | -0.36445 | -0.093393 | 0.36464 | 0.093515 | 0.00019121 | 0.00012218 | 0.54517 | 0.54517 | 0.54517 | 0.99609 | -0.073773 | 0.99667 | -0.062955 | 49.9236
108 | -0.0047712 | -0.0011958 | 0.0047715 | 0.0011958 | 3.3922e-07 | 3.7002e-10 | 0.0072483 | 0.0072482 | 0.0072483 | 0.97948 | -0.39398 | 0.97956 | -0.39248 | 1.9913
109 | 0.049308 | 0.012384 | -0.049286 | -0.01237 | 2.274e-05 | 1.4419e-05 | 0.075006 | 0.075006 | 0.075006 | 0.97834 | -0.41624 | 0.97785 | -0.42591 | 20.6059
110 | 0.024799 | 0.0062247 | -0.024786 | -0.0062168 | 1.2753e-05 | 7.8624e-06 | 0.03774 | 0.03774 | 0.03774 | 0.97785 | -0.42591 | 0.9773 | -0.4367 | 10.3681
111 | 0.024487 | 0.0061454 | -0.024482 | -0.0061419 | 5.5244e-06 | 3.4026e-06 | 0.037266 | 0.037266 | 0.037266 | 0.97785 | -0.42591 | 0.97761 | -0.43064 | 10.2378
112 | 0.0020229 | 0.00050686 | -0.0020228 | -0.00050697 | 3.5379e-08 | -1.1342e-07 | 0.003013 | 0.0030131 | 0.0030131 | 0.99901 | -0.019009 | 0.99899 | -0.019377 | 0.82776
113 | -0.010718 | -0.0026861 | 0.010719 | 0.0026866 | 1.0721e-06 | 5.3926e-07 | 0.015964 | 0.015964 | 0.015964 | 0.99901 | -0.019009 | 0.99912 | -0.01691 | 4.3858
114 | -0.018293 | -0.0045849 | 0.018298 | 0.0045878 | 4.9286e-06 | 2.9223e-06 | 0.027245 | 0.027245 | 0.027245 | 0.99912 | -0.01691 | 0.99941 | -0.011256 | 7.4849
115 | -0.020303 | -0.0050902 | 0.020306 | 0.0050919 | 2.7317e-06 | 1.6438e-06 | 0.030229 | 0.030229 | 0.030229 | 0.99941 | -0.011256 | 0.99956 | -0.008433 | 8.3048
116 | -0.02242 | -0.0056217 | 0.022421 | 0.0056222 | 9.395e-07 | 5.718e-07 | 0.033376 | 0.033376 | 0.033376 | 0.99956 | -0.008433 | 0.99961 | -0.0075538 | 9.1693
117 | -0.026347 | -0.0066063 | 0.026356 | 0.0066122 | 9.4881e-06 | 5.8567e-06 | 0.039221 | 0.039221 | 0.039221 | 0.99961 | -0.0075538 | 1 | 0 | 10.7751
118 | -0.1661 | -0.042074 | 0.16617 | 0.042114 | 6.3445e-05 | 4.0296e-05 | 0.25084 | 0.25084 | 0.25084 | 0.98598 | -0.26753 | 0.98639 | -0.25958 | 22.9703
119 | 0.37971 | 0.097735 | -0.37943 | -0.097558 | 0.00027722 | 0.00017715 | 0.56593 | 0.56593 | 0.56593 | 1 | 0 | 0.9992 | -0.015022 | 51.8248
120 | 0.3744 | 0.096298 | -0.37436 | -0.096271 | 4.1589e-05 | 2.6575e-05 | 0.55844 | 0.55844 | 0.55844 | 0.9992 | -0.015022 | 0.99908 | -0.017308 | 51.139
121 | 0.37222 | 0.095734 | -0.3715 | -0.095275 | 0.0007174 | 0.00045841 | 0.55525 | 0.55525 | 0.55525 | 0.99908 | -0.017308 | 0.99698 | -0.057041 | 50.8467
122 | 0.36924 | 0.094709 | -0.36913 | -0.094641 | 0.00010587 | 6.7651e-05 | 0.55187 | 0.55187 | 0.55187 | 0.99698 | -0.057041 | 0.99667 | -0.062955 | 50.5376
123 | 0.16834 | 0.042722 | -0.16817 | -0.042616 | 0.00016753 | 0.00010642 | 0.25386 | 0.25386 | 0.25386 | 0.98746 | -0.23887 | 0.98639 | -0.25958 | 23.247
124 | 0.024482 | 0.0061419 | -0.024473 | -0.0061367 | 8.4399e-06 | 5.1984e-06 | 0.037266 | 0.037266 | 0.037266 | 0.97761 | -0.43064 | 0.97724 | -0.43788 | 10.2379
125 | 0.020449 | 0.0051282 | -0.020444 | -0.0051253 | 4.6947e-06 | 2.8429e-06 | 0.031138 | 0.031138 | 0.031138 | 0.97724 | -0.43788 | 0.977 | -0.44269 | 8.5545
126 | 0.020611 | 0.0051704 | -0.0206 | -0.0051641 | 1.0495e-05 | 6.361e-06 | 0.031383 | 0.031383 | 0.031383 | 0.9773 | -0.4367 | 0.97676 | -0.44739 | 8.6217
127 | 0.016404 | 0.0041127 | -0.016401 | -0.004111 | 2.8936e-06 | 1.6972e-06 | 0.024985 | 0.024985 | 0.024985 | 0.977 | -0.44269 | 0.97681 | -0.4464 | 6.8639
128 | 0.011814 | 0.0029613 | -0.011812 | -0.0029604 | 1.7338e-06 | 9.3096e-07 | 0.017997 | 0.017997 | 0.017997 | 0.97681 | -0.4464 | 0.97665 | -0.44948 | 4.9441
129 | 0.0073392 | 0.0018394 | -0.0073386 | -0.0018392 | 5.177e-07 | 1.9317e-07 | 0.011182 | 0.011182 | 0.011182 | 0.97665 | -0.44948 | 0.97658 | -0.45096 | 3.072
130 | 0.0043291 | 0.001085 | -0.0043291 | -0.001085 | 4.6871e-08 | -5.9433e-09 | 0.0065963 | 0.0065963 | 0.0065963 | 0.97658 | -0.45096 | 0.97657 | -0.45119 | 1.8122
131 | 0.0099859 | 0.0025039 | -0.0099848 | -0.0025033 | 1.1601e-06 | 5.7517e-07 | 0.015213 | 0.015213 | 0.015213 | 0.97676 | -0.44739 | 0.97663 | -0.44982 | 4.1795
132 | 0.0099848 | 0.0025033 | -0.009981 | -0.0025015 | 3.754e-06 | 1.8615e-06 | 0.015213 | 0.015213 | 0.015213 | 0.97663 | -0.44982 | 0.97623 | -0.45772 | 4.1795

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.40987 | 0.10489

## res_load
| p_mw | q_mvar
0 | 0.0070318 | 0.0017623
1 | 0.0071127 | 0.0017826
2 | 0.0049622 | 0.0012436
3 | 0.0024846 | 0.0006227
4 | 0.0029536 | 0.00074024
5 | 0.0071196 | 0.0017843
6 | 0.0024703 | 0.00061912
7 | 0.0024461 | 0.00061304
8 | 0.0070595 | 0.0017693
9 | 0.007031 | 0.0017621
10 | 0.0024382 | 0.00061106
11 | 0.0021777 | 0.00054578
12 | 0.0074581 | 0.0018692
13 | 0.0023456 | 0.00058785
14 | 0.0017392 | 0.00043589
15 | 0.0021145 | 0.00052993
16 | 0.0017254 | 0.00043242
17 | 0.0044884 | 0.0011249
18 | 0.0067234 | 0.001685
19 | 0.0017781 | 0.00044564
20 | 0.0069431 | 0.0017401
21 | 0.001976 | 0.00049522
22 | 0.0017128 | 0.00042928
23 | 0.0017766 | 0.00044525
24 | 0.0027833 | 0.00069756
25 | 0.0058681 | 0.0014707
26 | 0.0026895 | 0.00067405
27 | 0.003179 | 0.00079674
28 | 0.00079668 | 0.00019967
29 | 0.0017169 | 0.0004303
30 | 0.013428 | 0.0033653
31 | 0.0014016 | 0.00035128
32 | 0.0027417 | 0.00068713
33 | 0.0054494 | 0.0013657
34 | 0.0020769 | 0.00052051
35 | 0.011868 | 0.0029743
36 | 0.0031921 | 0.00080002
37 | 0.0031953 | 0.00080083
38 | 0.0031281 | 0.00078397
39 | 0.0053686 | 0.0013455
40 | 0.0050668 | 0.0012699
41 | 0.0020998 | 0.00052627
42 | 0.00247 | 0.00061903
43 | 0.0039772 | 0.00099677
44 | 0.0017314 | 0.00043393
45 | 0.0055063 | 0.00138
46 | 0.0047372 | 0.0011872
47 | 0.0068334 | 0.0017126
48 | 0.0015505 | 0.0003886
49 | 0.0014515 | 0.00036379
50 | 0.0022967 | 0.0005756
51 | 0.00075867 | 0.00019014
52 | 0.0018563 | 0.00046524
53 | 0.005503 | 0.0013792
54 | 0.0011561 | 0.00028974
55 | 0.0074814 | 0.001875
56 | 0.0067359 | 0.0016882
57 | 0.0073654 | 0.0018459
58 | 0.00096436 | 0.00024169
59 | 0.0031809 | 0.00079721
60 | 0.0025674 | 0.00064346
61 | 0.0038205 | 0.00095751
62 | 0.0030741 | 0.00077043
63 | 0.002259 | 0.00056615
64 | 0.0029378 | 0.00073628
65 | 0.0014023 | 0.00035146
66 | 0.0079831 | 0.0020008
67 | 0.0022233 | 0.0005572
68 | 0.0070917 | 0.0017774
69 | 0.002249 | 0.00056364
70 | 0.0060802 | 0.0015238
71 | 0.0047633 | 0.0011938
72 | 0.0021527 | 0.00053953
73 | 0.0044635 | 0.0011187
74 | 0.0030965 | 0.00077605
75 | 0.0047712 | 0.0011958
76 | 0.0050399 | 0.0012631
77 | 0.0086952 | 0.0021792
78 | 0.0020228 | 0.00050697
79 | 0.0075743 | 0.0018983
80 | 0.0020046 | 0.0005024
81 | 0.0021139 | 0.00052979
82 | 0.0039264 | 0.00098406
83 | 0.0018834 | 0.00047203
84 | 0.002153 | 0.00053959
85 | 0.0050292 | 0.0012604
86 | 0.0021434 | 0.00053719
87 | 0.0022613 | 0.00056673
88 | 0.0044914 | 0.0011257
89 | 0.0022961 | 0.00057547
90 | 0.0020027 | 0.00050193
91 | 0.0040242 | 0.0010086
92 | 0.0041753 | 0.0010464
93 | 0.0040404 | 0.0010126
94 | 0.0045873 | 0.0011497
95 | 0.0044729 | 0.001121
96 | 0.0030095 | 0.00075425
97 | 0.010614 | 0.0026601
98 | 0.0043291 | 0.001085
99 | 0.009981 | 0.0025015

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1