## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-127_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-127_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_261-127_0_4_node_6 | 0.4 | n |  | TRUE
3 | bus_LV_261-127_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-127_0_4_node_15 | 0.4 | n |  | TRUE
5 | bus_LV_261-127_0_4_node_17 | 0.4 | n |  | TRUE
6 | bus_LV_261-127_0_4_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_261-127_0_4_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_261-127_0_4_node_13 | 0.4 | n |  | TRUE
9 | bus_LV_261-127_0_4_node_18 | 0.4 | n |  | TRUE
10 | bus_LV_261-127_0_4_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_261-127_0_4_node_22 | 0.4 | n |  | TRUE
12 | bus_LV_261-127_0_4_node_19 | 0.4 | n |  | TRUE
13 | bus_LV_261-127_0_4_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_261-127_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_261-127_0_4_node_28 | 0.4 | n |  | TRUE
16 | bus_LV_261-127_0_4_node_21 | 0.4 | n |  | TRUE
17 | bus_LV_261-127_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_261-127_0_4_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_261-127_0_4_node_25 | 0.4 | n |  | TRUE
20 | bus_LV_261-127_0_4_node_27 | 0.4 | n |  | TRUE
21 | bus_LV_261-127_0_4_node_30 | 0.4 | n |  | TRUE
22 | bus_LV_261-127_0_4_node_24 | 0.4 | n |  | TRUE
23 | bus_LV_261-127_0_4_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_261-127_0_4_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_261-127_0_4_node_26 | 0.4 | n |  | TRUE
26 | bus_LV_261-127_0_4_node_29 | 0.4 | n |  | TRUE
27 | bus_MV_535_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-127_0_4_load_0 | 0 | 0.087501 | 0.02193 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-127_0_4_load_17 | 5 | 0.015086 | 0.003781 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-127_0_4_load_18 | 9 | 0.025922 | 0.0064967 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-127_0_4_load_22 | 11 | 0.055999 | 0.014035 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-127_0_4_load_19 | 12 | 0.03014 | 0.0075537 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-127_0_4_load_28 | 15 | 0.028784 | 0.0072139 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-127_0_4_load_21 | 16 | 0.021091 | 0.0052859 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-127_0_4_load_25 | 19 | 0.014187 | 0.0035555 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-127_0_4_load_27 | 20 | 0.028784 | 0.0072141 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-127_0_4_load_30 | 21 | 0.040782 | 0.010221 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-127_0_4_load_24 | 22 | 0.02357 | 0.0059071 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-127_0_4_load_20 | 23 | 0.046584 | 0.011675 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-127_0_4_load_23 | 24 | 0.031673 | 0.007938 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-127_0_4_load_26 | 25 | 0.010156 | 0.0025454 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-127_0_4_load_29 | 26 | 0.055436 | 0.013894 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-127_0_4_line_0 |  | 0 | 1 | 0.017946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-127_0_4_line_1 |  | 1 | 2 | 0.043542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-127_0_4_line_2 |  | 2 | 12 | 0.0063675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-127_0_4_line_3 |  | 2 | 10 | 0.023318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_261-127_0_4_line_4 |  | 3 | 4 | 0.001697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-127_0_4_line_5 |  | 3 | 5 | 0.0091145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-127_0_4_line_6 |  | 4 | 22 | 0.024391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-127_0_4_line_7 |  | 5 | 9 | 0.013909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-127_0_4_line_8 |  | 6 | 7 | 0.0093978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-127_0_4_line_9 |  | 6 | 8 | 0.003366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-127_0_4_line_10 |  | 6 | 9 | 0.015012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-127_0_4_line_11 |  | 7 | 16 | 0.003287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-127_0_4_line_12 |  | 8 | 20 | 0.0085784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_261-127_0_4_line_13 |  | 8 | 13 | 0.0091164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_261-127_0_4_line_14 |  | 10 | 11 | 0.016699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_261-127_0_4_line_15 |  | 11 | 14 | 0.0094666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_261-127_0_4_line_16 |  | 12 | 23 | 0.025956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-127_0_4_line_17 |  | 13 | 14 | 0.013283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_261-127_0_4_line_18 |  | 13 | 15 | 0.00759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_261-127_0_4_line_19 |  | 17 | 18 | 0.012239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-127_0_4_line_20 |  | 17 | 19 | 0.017641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-127_0_4_line_21 |  | 18 | 21 | 0.014451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-127_0_4_line_22 |  | 19 | 25 | 0.02103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-127_0_4_line_23 |  | 20 | 25 | 0.012265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-127_0_4_line_24 |  | 21 | 26 | 0.020567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-127_0_4_line_25 |  | 22 | 24 | 0.014605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-127_0_4_trafo_28 | 0.63 MVA 20/0.4 kV | 27 | 15 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2682227.0003 | 1247815.2613 | 2682212.1958 | 1247825.4043
1 | 2682227.0003 | 1247815.2613 | 2682244.3144 | 1247831.9582 | 2682253.3477 | 1247836.8648 | 2682260.9571 | 1247842.052
2 | 2682260.9571 | 1247842.052 | 2682255.7218 | 1247845.6763
3 | 2682260.9571 | 1247842.052 | 2682253.3477 | 1247836.8648 | 2682258.1798 | 1247833.1847 | 2682260.3137 | 1247835.0824 | 2682264.2651 | 1247831.7347
4 | 2682314.9397 | 1247896.3521 | 2682313.8016 | 1247895.0909
5 | 2682313.8016 | 1247895.0909 | 2682311.9048 | 1247892.9852 | 2682307.4807 | 1247888.5275
6 | 2682314.9397 | 1247896.3521 | 2682312.4036 | 1247897.8624 | 2682291.4351 | 1247902.3308
7 | 2682307.4807 | 1247888.5275 | 2682297.6829 | 1247878.6556
8 | 2682287.1079 | 1247868.0005 | 2682290.3476 | 1247864.7764 | 2682293.7636 | 1247861.3658
9 | 2682284.7317 | 1247865.6102 | 2682287.1079 | 1247868.0005
10 | 2682287.1079 | 1247868.0005 | 2682297.6829 | 1247878.6556
11 | 2682293.7636 | 1247861.3658 | 2682296.0928 | 1247863.685
12 | 2682284.7317 | 1247865.6102 | 2682278.9503 | 1247871.9478
13 | 2682278.3109 | 1247859.1386 | 2682281.5734 | 1247862.4307 | 2682284.7317 | 1247865.6102
14 | 2682264.2651 | 1247831.7347 | 2682276.1643 | 1247843.4508
15 | 2682282.8849 | 1247850.1177 | 2682280.8514 | 1247848.0657 | 2682276.1643 | 1247843.4508
16 | 2682234.3804 | 1247860.4508 | 2682255.7218 | 1247845.6763
17 | 2682278.3109 | 1247859.1386 | 2682275.7262 | 1247856.5342 | 2682279.2214 | 1247853.4026 | 2682282.8849 | 1247850.1177
18 | 2682278.3109 | 1247859.1386 | 2682273.0834 | 1247864.6414
19 | 2682233.0307 | 1247907.5684 | 2682238.6205 | 1247908.6133 | 2682245.0616 | 1247909.8146
20 | 2682245.0616 | 1247909.8146 | 2682245.2706 | 1247908.9058 | 2682245.8771 | 1247908.2025 | 2682256.5118 | 1247896.5448
21 | 2682233.0307 | 1247907.5684 | 2682242.8324 | 1247896.9498
22 | 2682256.5118 | 1247896.5448 | 2682270.6846 | 1247881.0086
23 | 2682270.6846 | 1247881.0086 | 2682278.9503 | 1247871.9478
24 | 2682256.7827 | 1247881.8366 | 2682242.8324 | 1247896.9498
25 | 2682277.1509 | 1247905.3747 | 2682291.4351 | 1247902.3308

## bus_geodata
| x | y | coords
0 | 2682212.1958 | 1247825.4043
1 | 2682227.0003 | 1247815.2613
2 | 2682260.9571 | 1247842.052
3 | 2682313.8016 | 1247895.0909
4 | 2682314.9397 | 1247896.3521
5 | 2682307.4807 | 1247888.5275
6 | 2682287.1079 | 1247868.0005
7 | 2682293.7636 | 1247861.3658
8 | 2682284.7317 | 1247865.6102
9 | 2682297.6829 | 1247878.6556
10 | 2682264.2651 | 1247831.7347
11 | 2682276.1643 | 1247843.4508
12 | 2682255.7218 | 1247845.6763
13 | 2682278.3109 | 1247859.1386
14 | 2682282.8849 | 1247850.1177
15 | 2682273.0834 | 1247864.6414
16 | 2682296.0928 | 1247863.685
17 | 2682245.0616 | 1247909.8146
18 | 2682233.0307 | 1247907.5684
19 | 2682256.5118 | 1247896.5448
20 | 2682278.9503 | 1247871.9478
21 | 2682242.8324 | 1247896.9498
22 | 2682291.4351 | 1247902.3308
23 | 2682234.3804 | 1247860.4508
24 | 2682277.1509 | 1247905.3747
25 | 2682270.6846 | 1247881.0086
26 | 2682256.7827 | 1247881.8366
27 | 2682278.3109 | 1247859.1386

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99071 | -0.17869 | 0.087501 | 0.02193
1 | 0.99215 | -0.15085 | 0 | 0
2 | 0.99564 | -0.083622 | 0 | 0
3 | 0.99502 | -0.095663 | 0 | 0
4 | 0.99493 | -0.097314 | 0 | 0
5 | 0.99548 | -0.086803 | 0.015086 | 0.003781
6 | 0.99769 | -0.044279 | 0 | 0
7 | 0.99751 | -0.04775 | 0 | 0
8 | 0.99805 | -0.037365 | 0 | 0
9 | 0.99637 | -0.069614 | 0.025922 | 0.0064967
10 | 0.99739 | -0.050015 | 0 | 0
11 | 0.99801 | -0.03801 | 0.055999 | 0.014035
12 | 0.99519 | -0.092215 | 0.03014 | 0.0075537
13 | 0.99916 | -0.016117 | 0 | 0
14 | 0.99849 | -0.028894 | 0 | 0
15 | 1 | 0 | -0.49145 | -0.12387
16 | 0.99744 | -0.048964 | 0.021091 | 0.0052859
17 | 0.99242 | -0.14538 | 0 | 0
18 | 0.99134 | -0.16624 | 0 | 0
19 | 0.99398 | -0.11539 | 0.014187 | 0.0035555
20 | 0.99746 | -0.04858 | 0.028784 | 0.0072141
21 | 0.99007 | -0.19094 | 0.040782 | 0.010221
22 | 0.9937 | -0.12107 | 0.02357 | 0.0059071
23 | 0.99409 | -0.11352 | 0.046584 | 0.011675
24 | 0.99328 | -0.12924 | 0.031673 | 0.007938
25 | 0.99611 | -0.074519 | 0.010156 | 0.0025454
26 | 0.98902 | -0.21123 | 0.055436 | 0.013894
27 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.087501 | -0.02193 | 0.087617 | 0.022004 | 0.00011624 | 7.4159e-05 | 0.13142 | 0.13142 | 0.13142 | 0.99071 | -0.17869 | 0.99215 | -0.15085 | 36.1053
1 | -0.087617 | -0.022004 | 0.087899 | 0.022184 | 0.00028203 | 0.00017993 | 0.13142 | 0.13142 | 0.13142 | 0.99215 | -0.15085 | 0.99564 | -0.083622 | 36.1053
2 | 0.076802 | 0.019279 | -0.076771 | -0.019259 | 3.1466e-05 | 2.0055e-05 | 0.11479 | 0.11479 | 0.11479 | 0.99564 | -0.083622 | 0.99519 | -0.092215 | 31.5368
3 | -0.1647 | -0.041463 | 0.16497 | 0.041632 | 0.00026505 | 0.00016902 | 0.24622 | 0.24622 | 0.24622 | 0.99564 | -0.083622 | 0.99739 | -0.050015 | 33.821
4 | 0.055322 | 0.013895 | -0.055318 | -0.013893 | 4.3569e-06 | 2.7664e-06 | 0.082743 | 0.082743 | 0.082743 | 0.99502 | -0.095663 | 0.99493 | -0.097314 | 22.7316
5 | -0.055322 | -0.013895 | 0.055345 | 0.01391 | 2.34e-05 | 1.4858e-05 | 0.082743 | 0.082743 | 0.082743 | 0.99502 | -0.095663 | 0.99548 | -0.086803 | 22.7315
6 | 0.055318 | 0.013893 | -0.055255 | -0.013853 | 6.2622e-05 | 3.9761e-05 | 0.082743 | 0.082743 | 0.082743 | 0.99493 | -0.097314 | 0.9937 | -0.12107 | 22.7316
7 | -0.070432 | -0.017691 | 0.070489 | 0.017728 | 5.7826e-05 | 3.6827e-05 | 0.10529 | 0.10529 | 0.10529 | 0.99548 | -0.086803 | 0.99637 | -0.069614 | 28.9268
8 | 0.021096 | 0.0052888 | -0.021092 | -0.0052867 | 3.489e-06 | 2.1102e-06 | 0.031464 | 0.031464 | 0.031464 | 0.99769 | -0.044279 | 0.99751 | -0.04775 | 8.6441
9 | -0.11762 | -0.029588 | 0.11766 | 0.029613 | 3.8865e-05 | 2.4829e-05 | 0.17547 | 0.17547 | 0.17547 | 0.99769 | -0.044279 | 0.99805 | -0.037365 | 48.2063
10 | 0.096528 | 0.024299 | -0.096412 | -0.024225 | 0.00011674 | 7.4521e-05 | 0.14401 | 0.14401 | 0.14401 | 0.99769 | -0.044279 | 0.99637 | -0.069614 | 39.5623
11 | 0.021092 | 0.0052867 | -0.021091 | -0.0052859 | 1.2203e-06 | 7.3808e-07 | 0.031464 | 0.031464 | 0.031464 | 0.99751 | -0.04775 | 0.99744 | -0.048964 | 8.6441
12 | 0.1502 | 0.037972 | -0.15011 | -0.037921 | 8.074e-05 | 5.1449e-05 | 0.22405 | 0.22405 | 0.22405 | 0.99805 | -0.037365 | 0.99746 | -0.04858 | 30.7757
13 | -0.26786 | -0.067585 | 0.26813 | 0.067759 | 0.00027283 | 0.00017438 | 0.39952 | 0.39952 | 0.39952 | 0.99805 | -0.037365 | 0.99916 | -0.016117 | 54.8789
14 | -0.16497 | -0.041632 | 0.16506 | 0.041691 | 9.4907e-05 | 5.9868e-05 | 0.24622 | 0.24622 | 0.24622 | 0.99739 | -0.050015 | 0.99801 | -0.03801 | 16.9105
15 | -0.22106 | -0.055726 | 0.22116 | 0.055787 | 9.6478e-05 | 6.1251e-05 | 0.32971 | 0.32971 | 0.32971 | 0.99801 | -0.03801 | 0.99849 | -0.028894 | 22.6449
16 | 0.046631 | 0.011705 | -0.046584 | -0.011675 | 4.7327e-05 | 2.9952e-05 | 0.069729 | 0.069729 | 0.069729 | 0.99519 | -0.092215 | 0.99409 | -0.11352 | 19.1564
17 | 0.22129 | 0.055873 | -0.22116 | -0.055787 | 0.00013537 | 8.5942e-05 | 0.32971 | 0.32971 | 0.32971 | 0.99916 | -0.016117 | 0.99849 | -0.028894 | 22.6449
18 | -0.48942 | -0.12363 | 0.4898 | 0.12387 | 0.00037839 | 0.00024177 | 0.72923 | 0.72923 | 0.72923 | 0.99916 | -0.016117 | 1 | 0 | 50.0843
19 | 0.096481 | 0.024282 | -0.096385 | -0.024221 | 9.6093e-05 | 6.1342e-05 | 0.1447 | 0.1447 | 0.1447 | 0.99242 | -0.14538 | 0.99134 | -0.16624 | 39.7521
20 | -0.096481 | -0.024282 | 0.09662 | 0.024371 | 0.00013851 | 8.8417e-05 | 0.1447 | 0.1447 | 0.1447 | 0.99242 | -0.14538 | 0.99398 | -0.11539 | 39.752
21 | 0.096385 | 0.024221 | -0.096271 | -0.024149 | 0.00011346 | 7.2429e-05 | 0.1447 | 0.1447 | 0.1447 | 0.99134 | -0.16624 | 0.99007 | -0.19094 | 39.7521
22 | -0.11081 | -0.027926 | 0.11102 | 0.028065 | 0.00021714 | 0.0001387 | 0.16594 | 0.16593 | 0.16594 | 0.99398 | -0.11539 | 0.99611 | -0.074519 | 45.5865
23 | 0.12133 | 0.030707 | -0.12118 | -0.03061 | 0.00015085 | 9.6386e-05 | 0.18111 | 0.18111 | 0.18111 | 0.99746 | -0.04858 | 0.99611 | -0.074519 | 49.7546
24 | 0.055489 | 0.013928 | -0.055436 | -0.013894 | 5.3653e-05 | 3.4073e-05 | 0.083405 | 0.083405 | 0.083405 | 0.99007 | -0.19094 | 0.98902 | -0.21123 | 22.9134
25 | 0.031685 | 0.0079457 | -0.031673 | -0.007938 | 1.233e-05 | 7.7024e-06 | 0.047449 | 0.047449 | 0.047449 | 0.9937 | -0.12107 | 0.99328 | -0.12924 | 13.0353

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.52024 | 0.13109

## res_load
| p_mw | q_mvar
0 | 0.087501 | 0.02193
1 | 0.015086 | 0.003781
2 | 0.025922 | 0.0064967
3 | 0.055999 | 0.014035
4 | 0.03014 | 0.0075537
5 | 0.028784 | 0.0072139
6 | 0.021091 | 0.0052859
7 | 0.014187 | 0.0035555
8 | 0.028784 | 0.0072141
9 | 0.040782 | 0.010221
10 | 0.02357 | 0.0059071
11 | 0.046584 | 0.011675
12 | 0.031673 | 0.007938
13 | 0.010156 | 0.0025454
14 | 0.055436 | 0.013894

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1