## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-133_0_10_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-133_0_10_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-133_0_10_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_261-133_0_10_node_29 | 0.4 | n |  | TRUE
4 | bus_LV_261-133_0_10_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-133_0_10_node_44 | 0.4 | n |  | TRUE
6 | bus_LV_261-133_0_10_node_15 | 0.4 | n |  | TRUE
7 | bus_LV_261-133_0_10_node_14 | 0.4 | n |  | TRUE
8 | bus_LV_261-133_0_10_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_261-133_0_10_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_261-133_0_10_node_39 | 0.4 | n |  | TRUE
11 | bus_LV_261-133_0_10_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_261-133_0_10_node_30 | 0.4 | n |  | TRUE
13 | bus_LV_261-133_0_10_node_23 | 0.4 | n |  | TRUE
14 | bus_LV_261-133_0_10_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_261-133_0_10_node_28 | 0.4 | n |  | TRUE
16 | bus_LV_261-133_0_10_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_261-133_0_10_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_261-133_0_10_node_36 | 0.4 | n |  | TRUE
19 | bus_LV_261-133_0_10_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_261-133_0_10_node_43 | 0.4 | n |  | TRUE
21 | bus_LV_261-133_0_10_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_261-133_0_10_node_24 | 0.4 | n |  | TRUE
23 | bus_LV_261-133_0_10_node_32 | 0.4 | n |  | TRUE
24 | bus_LV_261-133_0_10_node_42 | 0.4 | n |  | TRUE
25 | bus_LV_261-133_0_10_node_31 | 0.4 | n |  | TRUE
26 | bus_LV_261-133_0_10_node_45 | 0.4 | n |  | TRUE
27 | bus_LV_261-133_0_10_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_261-133_0_10_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_261-133_0_10_node_35 | 0.4 | n |  | TRUE
30 | bus_LV_261-133_0_10_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_261-133_0_10_node_41 | 0.4 | n |  | TRUE
32 | bus_LV_261-133_0_10_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_261-133_0_10_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_261-133_0_10_node_34 | 0.4 | n |  | TRUE
35 | bus_LV_261-133_0_10_node_38 | 0.4 | n |  | TRUE
36 | bus_LV_261-133_0_10_node_40 | 0.4 | n |  | TRUE
37 | bus_LV_261-133_0_10_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_261-133_0_10_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_261-133_0_10_node_33 | 0.4 | n |  | TRUE
40 | bus_LV_261-133_0_10_node_26 | 0.4 | n |  | TRUE
41 | bus_MV_526_0_node_97 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-133_0_10_load_0 | 0 | 0.081443 | 0.020411 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-133_0_10_load_29 | 3 | 0.060336 | 0.015122 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-133_0_10_load_44 | 5 | 0.087204 | 0.021855 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-133_0_10_load_39 | 10 | 0.0072971 | 0.0018288 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-133_0_10_load_30 | 12 | 0.0073969 | 0.0018538 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-133_0_10_load_28 | 15 | 0.032757 | 0.0082098 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-133_0_10_load_36 | 18 | 0.006554 | 0.0016426 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-133_0_10_load_43 | 20 | 0.027727 | 0.0069491 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-133_0_10_load_24 | 22 | 0.014985 | 0.0037555 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-133_0_10_load_32 | 23 | 0.0064865 | 0.0016257 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-133_0_10_load_42 | 24 | 0.098872 | 0.02478 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-133_0_10_load_31 | 25 | 0.010825 | 0.0027129 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-133_0_10_load_45 | 26 | 0.043649 | 0.01094 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-133_0_10_load_35 | 29 | 0.0078013 | 0.0019552 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-133_0_10_load_41 | 31 | 0.014687 | 0.0036809 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-133_0_10_load_34 | 34 | 0.0078459 | 0.0019664 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-133_0_10_load_38 | 35 | 0.010675 | 0.0026755 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-133_0_10_load_40 | 36 | 0.0074841 | 0.0018757 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-133_0_10_load_27 | 37 | 0.032773 | 0.0082137 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-133_0_10_load_25 | 38 | 0.0088021 | 0.002206 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-133_0_10_load_33 | 39 | 0.0089422 | 0.0022411 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-133_0_10_load_26 | 40 | 0.0090284 | 0.0022627 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-133_0_10_line_0 |  | 0 | 1 | 0.015148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-133_0_10_line_1 |  | 1 | 2 | 0.04608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-133_0_10_line_2 |  | 2 | 3 | 0.01279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-133_0_10_line_3 |  | 3 | 11 | 0.012537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_261-133_0_10_line_4 |  | 4 | 5 | 0.011191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-133_0_10_line_5 |  | 4 | 6 | 0.017758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
6 | LV_261-133_0_10_line_6 |  | 4 | 7 | 0.080694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_261-133_0_10_line_7 |  | 6 | 26 | 0.010666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-133_0_10_line_8 |  | 6 | 21 | 0.10101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
9 | LV_261-133_0_10_line_9 |  | 7 | 25 | 0.10033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_261-133_0_10_line_10 |  | 8 | 9 | 0.16659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-133_0_10_line_11 |  | 8 | 10 | 0.050491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-133_0_10_line_12 |  | 9 | 23 | 0.089435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-133_0_10_line_13 |  | 10 | 36 | 0.02893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-133_0_10_line_14 |  | 11 | 12 | 0.021783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-133_0_10_line_15 |  | 11 | 13 | 0.017336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
16 | LV_261-133_0_10_line_16 |  | 12 | 36 | 0.028772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-133_0_10_line_17 |  | 13 | 35 | 0.053311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-133_0_10_line_18 |  | 13 | 14 | 0.021327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
19 | LV_261-133_0_10_line_19 |  | 14 | 15 | 0.009299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
20 | LV_261-133_0_10_line_20 |  | 15 | 37 | 0.013824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
21 | LV_261-133_0_10_line_21 |  | 16 | 17 | 0.015212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-133_0_10_line_22 |  | 16 | 18 | 0.011654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-133_0_10_line_23 |  | 17 | 22 | 0.0046872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
24 | LV_261-133_0_10_line_24 |  | 17 | 19 | 0.10253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
25 | LV_261-133_0_10_line_25 |  | 19 | 20 | 0.019993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-133_0_10_line_26 |  | 19 | 21 | 0.12072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
27 | LV_261-133_0_10_line_27 |  | 21 | 24 | 0.041329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-133_0_10_line_28 |  | 22 | 38 | 0.02529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_261-133_0_10_line_29 |  | 25 | 28 | 0.020099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-133_0_10_line_30 |  | 27 | 28 | 0.034331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-133_0_10_line_31 |  | 27 | 29 | 0.040368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-133_0_10_line_32 |  | 28 | 30 | 0.009314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-133_0_10_line_33 |  | 29 | 32 | 0.024645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-133_0_10_line_34 |  | 30 | 31 | 0.010855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-133_0_10_line_35 |  | 32 | 33 | 0.018881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-133_0_10_line_36 |  | 33 | 34 | 0.039613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-133_0_10_line_37 |  | 34 | 39 | 0.02019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-133_0_10_line_38 |  | 37 | 40 | 0.020856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
39 | LV_261-133_0_10_line_39 |  | 38 | 40 | 0.013732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-133_0_10_trafo_8 | 0.63 MVA 20/0.4 kV | 41 | 14 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2681909.1289 | 1249699.9622 | 2681923.5246 | 1249695.247
1 | 2681873.3101 | 1249680.731 | 2681875.6523 | 1249682.8093 | 2681886.8232 | 1249694.5723 | 2681892.1499 | 1249697.6037 | 2681897.8371 | 1249704.0425 | 2681909.1289 | 1249699.9622
2 | 2681873.3101 | 1249680.731 | 2681867.7467 | 1249683.3561 | 2681863.0991 | 1249688.0957
3 | 2681854.3212 | 1249697.0475 | 2681863.0991 | 1249688.0957
4 | 2681910.3416 | 1249599.1489 | 2681899.8951 | 1249603.2409
5 | 2681904.4926 | 1249591.2956 | 2681907.2901 | 1249595.9377 | 2681908.9161 | 1249595.204 | 2681914.4778 | 1249598.1719 | 2681910.3416 | 1249599.1489
6 | 2681910.3416 | 1249599.1489 | 2681914.4778 | 1249598.1719 | 2681917.2947 | 1249606.328 | 2681919.3021 | 1249613.5055 | 2681924.8166 | 1249614.9717 | 2681929.5212 | 1249616.5712 | 2681939.7398 | 1249611.4864 | 2681944.2408 | 1249609.247 | 2681950.042 | 1249606.3584 | 2681955.2502 | 1249603.7618 | 2681948.8143 | 1249595.2221 | 2681943.1257 | 1249586.6927
7 | 2681894.7588 | 1249595.7199 | 2681904.4926 | 1249591.2956
8 | 2681821.4642 | 1249596.7531 | 2681841.6765 | 1249590.8277 | 2681894.3594 | 1249571.6299 | 2681902.8703 | 1249585.202 | 2681901.3483 | 1249586.0594 | 2681904.4926 | 1249591.2956
9 | 2681943.1257 | 1249586.6927 | 2681932.0398 | 1249569.8604 | 2681893.7276 | 1249509.731 | 2681888.8487 | 1249502.3155
10 | 2681763.2489 | 1249789.7815 | 2681768.3581 | 1249801.4495 | 2681786.8724 | 1249845.1706 | 2681790.6043 | 1249854.3288 | 2681795.3451 | 1249852.2038 | 2681798.5033 | 1249853.6929 | 2681799.6893 | 1249854.1985 | 2681815.2669 | 1249850.8443 | 2681828.7878 | 1249847.1616 | 2681830.5176 | 1249852.0224 | 2681869.587 | 1249837.0285 | 2681878.5791 | 1249833.7947
11 | 2681763.2489 | 1249789.7815 | 2681798.6254 | 1249753.7559
12 | 2681878.5791 | 1249833.7947 | 2681870.8147 | 1249826.8713 | 2681857.1963 | 1249787.8766 | 2681856.7836 | 1249783.3231 | 2681858.1007 | 1249779.2605 | 2681860.5124 | 1249775.213 | 2681875.9792 | 1249760.2266 | 2681878.2192 | 1249758.8358
13 | 2681798.6254 | 1249753.7559 | 2681818.8952 | 1249733.1141
14 | 2681854.3212 | 1249697.0475 | 2681852.0927 | 1249699.3073 | 2681839.0542 | 1249712.5851
15 | 2681842.0008 | 1249687.5926 | 2681843.3789 | 1249686.2218 | 2681849.2635 | 1249692.0406 | 2681854.3212 | 1249697.0475
16 | 2681818.8952 | 1249733.1141 | 2681839.0542 | 1249712.5851
17 | 2681842.0008 | 1249687.5926 | 2681805.0599 | 1249726.03
18 | 2681833.7705 | 1249667.92 | 2681836.4797 | 1249674.5846 | 2681839.2253 | 1249681.3497 | 2681842.0008 | 1249687.5926
19 | 2681833.7705 | 1249667.92 | 2681825.1743 | 1249671.4664
20 | 2681812.3948 | 1249676.7386 | 2681825.1743 | 1249671.4664
21 | 2681752.7786 | 1249701.5274 | 2681755.2486 | 1249707.477 | 2681758.6177 | 1249715.5739
22 | 2681758.6177 | 1249715.5739 | 2681750.8165 | 1249718.9577 | 2681747.9077 | 1249720.1674
23 | 2681752.7786 | 1249701.5274 | 2681757.0865 | 1249699.6801
24 | 2681752.7786 | 1249701.5274 | 2681732.0578 | 1249710.415 | 2681720.1919 | 1249683.8762 | 2681765.9476 | 1249661.5462
25 | 2681765.9476 | 1249661.5462 | 2681783.9565 | 1249652.7548
26 | 2681765.9476 | 1249661.5462 | 2681750.3732 | 1249617.5767 | 2681821.4642 | 1249596.7531
27 | 2681821.4642 | 1249596.7531 | 2681815.0901 | 1249625.2751 | 2681804.2255 | 1249630.6736
28 | 2681757.0865 | 1249699.6801 | 2681764.7113 | 1249696.4105 | 2681780.4207 | 1249689.9295
29 | 2681878.8405 | 1249484.9071 | 2681885.0822 | 1249496.5908 | 2681888.8487 | 1249502.3155
30 | 2681850.8539 | 1249504.7909 | 2681857.7781 | 1249499.8717 | 2681863.6805 | 1249495.6723 | 2681868.4846 | 1249492.2695 | 2681878.8405 | 1249484.9071
31 | 2681850.8539 | 1249504.7909 | 2681842.8457 | 1249499.6321 | 2681831.0356 | 1249496.9337 | 2681824.0495 | 1249493.2123 | 2681814.7474 | 1249487.7021
32 | 2681878.8405 | 1249484.9071 | 2681881.8017 | 1249476.0748
33 | 2681807.3102 | 1249471.2651 | 2681801.8687 | 1249476.5384 | 2681809.0238 | 1249483.331 | 2681814.7474 | 1249487.7021
34 | 2681881.8017 | 1249476.0748 | 2681892.2716 | 1249474.6739 | 2681892.5463 | 1249474.5749
35 | 2681791.4228 | 1249470.1895 | 2681795.1152 | 1249468.5504 | 2681799.767 | 1249465.7792 | 2681805.3249 | 1249469.0361 | 2681807.3102 | 1249471.2651
36 | 2681791.4228 | 1249470.1895 | 2681779.2154 | 1249475.4806 | 2681754.1828 | 1249483.5723
37 | 2681734.9716 | 1249489.7824 | 2681754.1828 | 1249483.5723
38 | 2681812.3948 | 1249676.7386 | 2681793.1148 | 1249684.6926
39 | 2681780.4207 | 1249689.9295 | 2681793.1148 | 1249684.6926

## bus_geodata
| x | y | coords
0 | 2681923.5246 | 1249695.247
1 | 2681909.1289 | 1249699.9622
2 | 2681873.3101 | 1249680.731
3 | 2681863.0991 | 1249688.0957
4 | 2681910.3416 | 1249599.1489
5 | 2681899.8951 | 1249603.2409
6 | 2681904.4926 | 1249591.2956
7 | 2681943.1257 | 1249586.6927
8 | 2681763.2489 | 1249789.7815
9 | 2681878.5791 | 1249833.7947
10 | 2681798.6254 | 1249753.7559
11 | 2681854.3212 | 1249697.0475
12 | 2681839.0542 | 1249712.5851
13 | 2681842.0008 | 1249687.5926
14 | 2681833.7705 | 1249667.92
15 | 2681825.1743 | 1249671.4664
16 | 2681758.6177 | 1249715.5739
17 | 2681752.7786 | 1249701.5274
18 | 2681747.9077 | 1249720.1674
19 | 2681765.9476 | 1249661.5462
20 | 2681783.9565 | 1249652.7548
21 | 2681821.4642 | 1249596.7531
22 | 2681757.0865 | 1249699.6801
23 | 2681878.2192 | 1249758.8358
24 | 2681804.2255 | 1249630.6736
25 | 2681888.8487 | 1249502.3155
26 | 2681894.7588 | 1249595.7199
27 | 2681850.8539 | 1249504.7909
28 | 2681878.8405 | 1249484.9071
29 | 2681814.7474 | 1249487.7021
30 | 2681881.8017 | 1249476.0748
31 | 2681892.5463 | 1249474.5749
32 | 2681807.3102 | 1249471.2651
33 | 2681791.4228 | 1249470.1895
34 | 2681754.1828 | 1249483.5723
35 | 2681805.0599 | 1249726.03
36 | 2681818.8952 | 1249733.1141
37 | 2681812.3948 | 1249676.7386
38 | 2681780.4207 | 1249689.9295
39 | 2681734.9716 | 1249489.7824
40 | 2681793.1148 | 1249684.6926
41 | 2681836.4797 | 1249674.5846

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99244 | -0.14543 | 0.081443 | 0.020411
1 | 0.99357 | -0.12362 | 0 | 0
2 | 0.997 | -0.057588 | 0 | 0
3 | 0.99795 | -0.03934 | 0.060336 | 0.015122
4 | 0.97832 | -0.41621 | 0 | 0
5 | 0.97741 | -0.43399 | 0.087204 | 0.021855
6 | 0.97877 | -0.40733 | 0 | 0
7 | 0.97643 | -0.4531 | 0 | 0
8 | 0.99697 | -0.058176 | 0 | 0
9 | 0.99599 | -0.07716 | 0 | 0
10 | 0.99727 | -0.052426 | 0.0072971 | 0.0018288
11 | 0.99876 | -0.023798 | 0 | 0
12 | 0.99819 | -0.034719 | 0.0073969 | 0.0018538
13 | 0.9993 | -0.013476 | 0 | 0
14 | 1 | 0 | -0.60258 | -0.15343
15 | 0.99929 | -0.013382 | 0.032757 | 0.0082098
16 | 0.99421 | -0.10961 | 0 | 0
17 | 0.9943 | -0.10785 | 0 | 0
18 | 0.99414 | -0.11095 | 0.006554 | 0.0016426
19 | 0.98845 | -0.21972 | 0 | 0
20 | 0.98794 | -0.22961 | 0.027727 | 0.0069491
21 | 0.98217 | -0.34104 | 0 | 0
22 | 0.99457 | -0.10266 | 0.014985 | 0.0037555
23 | 0.99546 | -0.087361 | 0.0064865 | 0.0016257
24 | 0.97838 | -0.41516 | 0.098872 | 0.02478
25 | 0.97409 | -0.49917 | 0.010825 | 0.0027129
26 | 0.97834 | -0.4158 | 0.043649 | 0.01094
27 | 0.97256 | -0.52923 | 0 | 0
28 | 0.97335 | -0.51368 | 0 | 0
29 | 0.97164 | -0.54754 | 0.0078013 | 0.0019552
30 | 0.97323 | -0.5162 | 0 | 0
31 | 0.97308 | -0.51913 | 0.014687 | 0.0036809
32 | 0.97125 | -0.55518 | 0 | 0
33 | 0.97095 | -0.56104 | 0 | 0
34 | 0.97033 | -0.57334 | 0.0078459 | 0.0019664
35 | 0.99878 | -0.023416 | 0.010675 | 0.0026755
36 | 0.99763 | -0.045435 | 0.0074841 | 0.0018757
37 | 0.99832 | -0.031728 | 0.032773 | 0.0082137
38 | 0.99612 | -0.073366 | 0.0088021 | 0.002206
39 | 0.97016 | -0.57668 | 0.0089422 | 0.0022411
40 | 0.99698 | -0.057075 | 0.0090284 | 0.0022627
41 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.081443 | -0.020411 | 0.081527 | 0.020465 | 8.4704e-05 | 5.4015e-05 | 0.12211 | 0.12211 | 0.12211 | 0.99244 | -0.14543 | 0.99357 | -0.12362 | 33.547
1 | -0.081527 | -0.020465 | 0.081785 | 0.02063 | 0.00025766 | 0.0001643 | 0.12211 | 0.12211 | 0.12211 | 0.99357 | -0.12362 | 0.997 | -0.057588 | 33.547
2 | -0.081785 | -0.02063 | 0.081856 | 0.020675 | 7.1516e-05 | 4.5603e-05 | 0.12211 | 0.12211 | 0.12211 | 0.997 | -0.057588 | 0.99795 | -0.03934 | 33.5469
3 | -0.14219 | -0.035797 | 0.1423 | 0.035864 | 0.00010573 | 6.7338e-05 | 0.21208 | 0.21208 | 0.21208 | 0.99795 | -0.03934 | 0.99876 | -0.023798 | 29.1314
4 | 0.087278 | 0.021903 | -0.087204 | -0.021855 | 7.3966e-05 | 4.7198e-05 | 0.13276 | 0.13276 | 0.13276 | 0.97832 | -0.41621 | 0.97741 | -0.43399 | 36.4724
5 | -0.13767 | -0.034639 | 0.13773 | 0.034675 | 5.8424e-05 | 3.6276e-05 | 0.20945 | 0.20945 | 0.20945 | 0.97832 | -0.41621 | 0.97877 | -0.40733 | 11.508
6 | 0.050394 | 0.012737 | -0.050305 | -0.012682 | 8.8978e-05 | 5.4924e-05 | 0.076687 | 0.076687 | 0.076687 | 0.97832 | -0.41621 | 0.97643 | -0.4531 | 10.534
7 | 0.043667 | 0.010951 | -0.043649 | -0.01094 | 1.7629e-05 | 1.1148e-05 | 0.066388 | 0.066388 | 0.066388 | 0.97877 | -0.40733 | 0.97834 | -0.4158 | 18.2386
8 | -0.1814 | -0.045626 | 0.18197 | 0.045989 | 0.00057639 | 0.00036252 | 0.27583 | 0.27583 | 0.27583 | 0.97877 | -0.40733 | 0.98217 | -0.34104 | 15.1557
9 | 0.050305 | 0.012682 | -0.050194 | -0.012613 | 0.00011063 | 6.8301e-05 | 0.076687 | 0.076688 | 0.076688 | 0.97643 | -0.4531 | 0.97409 | -0.49917 | 10.5341
10 | 0.0064955 | 0.0016281 | -0.0064896 | -0.0016265 | 5.8723e-06 | 1.588e-06 | 0.0096949 | 0.0096956 | 0.0096956 | 0.99697 | -0.058176 | 0.99599 | -0.07716 | 2.6636
11 | -0.0064955 | -0.0016281 | 0.0064973 | 0.0016286 | 1.7796e-06 | 4.8033e-07 | 0.0096949 | 0.0096946 | 0.0096949 | 0.99697 | -0.058176 | 0.99727 | -0.052426 | 2.6634
12 | 0.0064896 | 0.0016265 | -0.0064865 | -0.0016257 | 3.1529e-06 | 8.5453e-07 | 0.0096956 | 0.009696 | 0.009696 | 0.99599 | -0.07716 | 0.99546 | -0.087361 | 2.6637
13 | -0.013794 | -0.0034574 | 0.013799 | 0.00346 | 4.596e-06 | 2.5638e-06 | 0.020583 | 0.020582 | 0.020583 | 0.99727 | -0.052426 | 0.99763 | -0.045435 | 5.6546
14 | 0.028706 | 0.0072054 | -0.028691 | -0.0071961 | 1.4944e-05 | 9.2792e-06 | 0.042772 | 0.042772 | 0.042772 | 0.99876 | -0.023798 | 0.99819 | -0.034719 | 11.7505
15 | -0.171 | -0.04307 | 0.17109 | 0.043123 | 8.4447e-05 | 5.2911e-05 | 0.25485 | 0.25485 | 0.25485 | 0.99876 | -0.023798 | 0.9993 | -0.013476 | 14.0026
16 | 0.021294 | 0.0053423 | -0.021283 | -0.0053357 | 1.0873e-05 | 6.583e-06 | 0.031745 | 0.031745 | 0.031745 | 0.99819 | -0.034719 | 0.99763 | -0.045435 | 8.7213
17 | 0.010681 | 0.0026781 | -0.010675 | -0.0026755 | 5.057e-06 | 2.5384e-06 | 0.015904 | 0.015905 | 0.015905 | 0.9993 | -0.013476 | 0.99878 | -0.023416 | 4.3694
18 | -0.18177 | -0.045801 | 0.18189 | 0.045874 | 0.00011726 | 7.3647e-05 | 0.27075 | 0.27075 | 0.27075 | 0.9993 | -0.013476 | 1 | 0 | 14.8765
19 | 0.41904 | 0.10755 | -0.41877 | -0.10738 | 0.00027194 | 0.00017343 | 0.62444 | 0.62444 | 0.62444 | 1 | 0 | 0.99929 | -0.013382 | 34.3098
20 | 0.38601 | 0.099167 | -0.38567 | -0.098948 | 0.00034359 | 0.00021899 | 0.57566 | 0.57566 | 0.57566 | 0.99929 | -0.013382 | 0.99832 | -0.031728 | 31.6297
21 | -0.0065544 | -0.0016427 | 0.0065549 | 0.0016429 | 5.4895e-07 | 1.5405e-07 | 0.0098098 | 0.0098098 | 0.0098098 | 0.99421 | -0.10961 | 0.9943 | -0.10785 | 2.695
22 | 0.0065544 | 0.0016427 | -0.006554 | -0.0016426 | 4.2056e-07 | 1.1804e-07 | 0.0098098 | 0.0098099 | 0.0098099 | 0.99421 | -0.10961 | 0.99414 | -0.11095 | 2.695
23 | -0.31882 | -0.081708 | 0.3189 | 0.081759 | 8.0245e-05 | 5.1053e-05 | 0.47777 | 0.47777 | 0.47777 | 0.9943 | -0.10785 | 0.99457 | -0.10266 | 26.2512
24 | 0.31226 | 0.080065 | -0.31058 | -0.078994 | 0.001684 | 0.0010711 | 0.46796 | 0.46796 | 0.46796 | 0.9943 | -0.10785 | 0.98845 | -0.21972 | 25.7124
25 | 0.02774 | 0.0069572 | -0.027727 | -0.0069491 | 1.3076e-05 | 8.1126e-06 | 0.041762 | 0.041763 | 0.041763 | 0.98845 | -0.21972 | 0.98794 | -0.22961 | 11.4732
26 | 0.28284 | 0.072037 | -0.2812 | -0.070992 | 0.0016447 | 0.0010449 | 0.4262 | 0.42621 | 0.42621 | 0.98845 | -0.21972 | 0.98217 | -0.34104 | 23.4179
27 | 0.099223 | 0.025003 | -0.098872 | -0.02478 | 0.00035045 | 0.00022377 | 0.15037 | 0.15037 | 0.15037 | 0.98217 | -0.34104 | 0.97838 | -0.41516 | 41.3115
28 | -0.33388 | -0.085515 | 0.33436 | 0.085817 | 0.00047455 | 0.00030207 | 0.50019 | 0.50019 | 0.50019 | 0.99457 | -0.10266 | 0.99612 | -0.073366 | 27.483
29 | 0.039369 | 0.0099004 | -0.039342 | -0.0098832 | 2.7272e-05 | 1.7204e-05 | 0.060153 | 0.060153 | 0.060153 | 0.97409 | -0.49917 | 0.97335 | -0.51368 | 16.5254
30 | -0.024633 | -0.0061888 | 0.024651 | 0.0062001 | 1.8292e-05 | 1.128e-05 | 0.037694 | 0.037694 | 0.037694 | 0.97256 | -0.52923 | 0.97335 | -0.51368 | 10.3554
31 | 0.024633 | 0.0061888 | -0.024611 | -0.0061755 | 2.1508e-05 | 1.3265e-05 | 0.037694 | 0.037694 | 0.037694 | 0.97256 | -0.52923 | 0.97164 | -0.54754 | 10.3555
32 | 0.014691 | 0.0036831 | -0.014689 | -0.0036821 | 1.7618e-06 | 1.0118e-06 | 0.022459 | 0.022459 | 0.022459 | 0.97335 | -0.51368 | 0.97323 | -0.5162 | 6.1701
33 | 0.01681 | 0.0042203 | -0.016804 | -0.0042167 | 6.1264e-06 | 3.6158e-06 | 0.025747 | 0.025747 | 0.025747 | 0.97164 | -0.54754 | 0.97125 | -0.55518 | 7.0733
34 | 0.014689 | 0.0036821 | -0.014687 | -0.0036809 | 2.0533e-06 | 1.1792e-06 | 0.022459 | 0.022459 | 0.022459 | 0.97323 | -0.5162 | 0.97308 | -0.51913 | 6.1701
35 | 0.016804 | 0.0042167 | -0.016799 | -0.004214 | 4.6937e-06 | 2.7703e-06 | 0.025747 | 0.025747 | 0.025747 | 0.97125 | -0.55518 | 0.97095 | -0.56104 | 7.0733
36 | 0.016799 | 0.004214 | -0.016789 | -0.0042082 | 9.8473e-06 | 5.8126e-06 | 0.025747 | 0.025747 | 0.025747 | 0.97095 | -0.56104 | 0.97033 | -0.57334 | 7.0734
37 | 0.0089436 | 0.0022418 | -0.0089422 | -0.0022411 | 1.4242e-06 | 6.6215e-07 | 0.013715 | 0.013715 | 0.013715 | 0.97033 | -0.57334 | 0.97016 | -0.57668 | 3.768
38 | 0.3529 | 0.090735 | -0.35246 | -0.090458 | 0.00043412 | 0.00027648 | 0.52681 | 0.52681 | 0.52681 | 0.99832 | -0.031728 | 0.99698 | -0.057075 | 28.9458
39 | -0.34316 | -0.088023 | 0.34343 | 0.088196 | 0.00027139 | 0.0001728 | 0.51334 | 0.51334 | 0.51334 | 0.99612 | -0.073366 | 0.99698 | -0.057075 | 28.2054

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.60258 | 0.15343

## res_load
| p_mw | q_mvar
0 | 0.081443 | 0.020411
1 | 0.060336 | 0.015122
2 | 0.087204 | 0.021855
3 | 0.0072971 | 0.0018288
4 | 0.0073969 | 0.0018538
5 | 0.032757 | 0.0082098
6 | 0.006554 | 0.0016426
7 | 0.027727 | 0.0069491
8 | 0.014985 | 0.0037555
9 | 0.0064865 | 0.0016257
10 | 0.098872 | 0.02478
11 | 0.010825 | 0.0027129
12 | 0.043649 | 0.01094
13 | 0.0078013 | 0.0019552
14 | 0.014687 | 0.0036809
15 | 0.0078459 | 0.0019664
16 | 0.010675 | 0.0026755
17 | 0.0074841 | 0.0018757
18 | 0.032773 | 0.0082137
19 | 0.0088021 | 0.002206
20 | 0.0089422 | 0.0022411
21 | 0.0090284 | 0.0022627

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1