## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-14_1_2_node_7 | 0.4 | n |  | TRUE
1 | bus_LV_261-14_1_2_node_13 | 0.4 | n |  | TRUE
2 | bus_LV_261-14_1_2_node_65 | 0.4 | n |  | TRUE
3 | bus_LV_261-14_1_2_node_8 | 0.4 | n |  | TRUE
4 | bus_LV_261-14_1_2_node_11 | 0.4 | n |  | TRUE
5 | bus_LV_261-14_1_2_node_20 | 0.4 | n |  | TRUE
6 | bus_LV_261-14_1_2_node_40 | 0.4 | n |  | TRUE
7 | bus_LV_261-14_1_2_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_261-14_1_2_node_68 | 0.4 | n |  | TRUE
9 | bus_LV_261-14_1_2_node_67 | 0.4 | n |  | TRUE
10 | bus_LV_261-14_1_2_node_70 | 0.4 | n |  | TRUE
11 | bus_LV_261-14_1_2_node_120 | 0.4 | n |  | TRUE
12 | bus_LV_261-14_1_2_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_261-14_1_2_node_35 | 0.4 | n |  | TRUE
14 | bus_LV_261-14_1_2_node_88 | 0.4 | n |  | TRUE
15 | bus_LV_261-14_1_2_node_87 | 0.4 | n |  | TRUE
16 | bus_LV_261-14_1_2_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_261-14_1_2_node_34 | 0.4 | n |  | TRUE
18 | bus_LV_261-14_1_2_node_48 | 0.4 | n |  | TRUE
19 | bus_LV_261-14_1_2_node_33 | 0.4 | n |  | TRUE
20 | bus_LV_261-14_1_2_node_28 | 0.4 | n |  | TRUE
21 | bus_LV_261-14_1_2_node_41 | 0.4 | n |  | TRUE
22 | bus_LV_261-14_1_2_node_61 | 0.4 | n |  | TRUE
23 | bus_LV_261-14_1_2_node_29 | 0.4 | n |  | TRUE
24 | bus_LV_261-14_1_2_node_89 | 0.4 | n |  | TRUE
25 | bus_LV_261-14_1_2_node_84 | 0.4 | n |  | TRUE
26 | bus_LV_261-14_1_2_node_30 | 0.4 | n |  | TRUE
27 | bus_LV_261-14_1_2_node_49 | 0.4 | n |  | TRUE
28 | bus_LV_261-14_1_2_node_59 | 0.4 | n |  | TRUE
29 | bus_LV_261-14_1_2_node_66 | 0.4 | n |  | TRUE
30 | bus_LV_261-14_1_2_node_64 | 0.4 | n |  | TRUE
31 | bus_LV_261-14_1_2_node_118 | 0.4 | n |  | TRUE
32 | bus_LV_261-14_1_2_node_85 | 0.4 | n |  | TRUE
33 | bus_LV_261-14_1_2_node_60 | 0.4 | n |  | TRUE
34 | bus_LV_261-14_1_2_node_62 | 0.4 | n |  | TRUE
35 | bus_LV_261-14_1_2_node_69 | 0.4 | n |  | TRUE
36 | bus_LV_261-14_1_2_node_71 | 0.4 | n |  | TRUE
37 | bus_LV_261-14_1_2_node_73 | 0.4 | n |  | TRUE
38 | bus_LV_261-14_1_2_node_72 | 0.4 | n |  | TRUE
39 | bus_LV_261-14_1_2_node_74 | 0.4 | n |  | TRUE
40 | bus_LV_261-14_1_2_node_75 | 0.4 | n |  | TRUE
41 | bus_LV_261-14_1_2_node_76 | 0.4 | n |  | TRUE
42 | bus_LV_261-14_1_2_node_78 | 0.4 | n |  | TRUE
43 | bus_LV_261-14_1_2_node_79 | 0.4 | n |  | TRUE
44 | bus_LV_261-14_1_2_node_80 | 0.4 | n |  | TRUE
45 | bus_LV_261-14_1_2_node_81 | 0.4 | n |  | TRUE
46 | bus_LV_261-14_1_2_node_86 | 0.4 | n |  | TRUE
47 | bus_LV_261-14_1_2_node_82 | 0.4 | n |  | TRUE
48 | bus_LV_261-14_1_2_node_83 | 0.4 | n |  | TRUE
49 | bus_MV_542_0_node_106 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-14_1_2_load_65 | 2 | 0.0084986 | 0.0021299 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-14_1_2_load_40 | 6 | 0.03402 | 0.0085262 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-14_1_2_load_68 | 8 | 0.015701 | 0.0039351 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-14_1_2_load_67 | 9 | 0.0067266 | 0.0016858 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-14_1_2_load_120 | 11 | 0.0089178 | 0.002235 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-14_1_2_load_88 | 14 | 0.0055828 | 0.0013992 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-14_1_2_load_87 | 15 | 0.0087368 | 0.0021896 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-14_1_2_load_48 | 18 | 0.0095036 | 0.0023818 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-14_1_2_load_61 | 22 | 0.0054359 | 0.0013624 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-14_1_2_load_89 | 24 | 0.011903 | 0.0029832 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-14_1_2_load_84 | 25 | 0.0047834 | 0.0011988 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-14_1_2_load_49 | 27 | 0.0068924 | 0.0017274 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-14_1_2_load_59 | 28 | 0.0050417 | 0.0012636 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-14_1_2_load_66 | 29 | 0.0035028 | 0.00087788 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-14_1_2_load_64 | 30 | 0.007937 | 0.0019892 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-14_1_2_load_118 | 31 | 0.018825 | 0.004718 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-14_1_2_load_85 | 32 | 0.0056408 | 0.0014137 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-14_1_2_load_62 | 34 | 0.0058322 | 0.0014617 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-14_1_2_load_69 | 35 | 0.0084622 | 0.0021208 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-14_1_2_load_71 | 36 | 0.0061997 | 0.0015538 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-14_1_2_load_73 | 37 | 0.0095376 | 0.0023903 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-14_1_2_load_72 | 38 | 0.014171 | 0.0035517 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-14_1_2_load_75 | 40 | 0.0060591 | 0.0015185 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-14_1_2_load_76 | 41 | 0.0084161 | 0.0021093 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-14_1_2_load_78 | 42 | 0.0065589 | 0.0016438 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-14_1_2_load_79 | 43 | 0.0064513 | 0.0016168 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-14_1_2_load_80 | 44 | 0.0065869 | 0.0016508 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-14_1_2_load_86 | 46 | 0.0088087 | 0.0022077 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-14_1_2_load_82 | 47 | 0.0048623 | 0.0012186 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-14_1_2_load_83 | 48 | 0.0073131 | 0.0018328 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 24 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-14_1_2_line_0 |  | 0 | 1 | 0.011532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-14_1_2_line_1 |  | 0 | 2 | 0.031707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-14_1_2_line_2 |  | 1 | 15 | 0.029643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-14_1_2_line_3 |  | 2 | 30 | 0.01597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-14_1_2_line_4 |  | 3 | 4 | 0.070727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_261-14_1_2_line_5 |  | 3 | 5 | 0.14956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_261-14_1_2_line_6 |  | 3 | 6 | 0.037499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-14_1_2_line_7 |  | 4 | 10 | 0.016901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-14_1_2_line_8 |  | 4 | 11 | 0.019696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-14_1_2_line_9 |  | 5 | 19 | 0.045972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_261-14_1_2_line_10 |  | 7 | 8 | 0.033062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-14_1_2_line_11 |  | 7 | 9 | 0.013247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-14_1_2_line_12 |  | 8 | 31 | 0.026888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-14_1_2_line_13 |  | 10 | 36 | 0.013051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-14_1_2_line_14 |  | 10 | 35 | 0.0022269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-14_1_2_line_15 |  | 11 | 41 | 0.016217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-14_1_2_line_16 |  | 12 | 13 | 0.018231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_261-14_1_2_line_17 |  | 12 | 14 | 0.011831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_261-14_1_2_line_18 |  | 13 | 31 | 0.017059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-14_1_2_line_19 |  | 13 | 16 | 0.017416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_261-14_1_2_line_20 |  | 14 | 21 | 0.014093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_261-14_1_2_line_21 |  | 15 | 46 | 0.019965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-14_1_2_line_22 |  | 16 | 17 | 0.036746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-14_1_2_line_23 |  | 16 | 18 | 0.016578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_261-14_1_2_line_24 |  | 17 | 29 | 0.049226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-14_1_2_line_25 |  | 17 | 30 | 0.014308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-14_1_2_line_26 |  | 18 | 26 | 0.0016598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_261-14_1_2_line_27 |  | 19 | 28 | 0.041411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_261-14_1_2_line_28 |  | 20 | 21 | 0.002792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_261-14_1_2_line_29 |  | 20 | 22 | 0.020144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_261-14_1_2_line_30 |  | 22 | 33 | 0.0053558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_261-14_1_2_line_31 |  | 23 | 24 | 0.011131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
32 | LV_261-14_1_2_line_32 |  | 23 | 25 | 0.0018711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_261-14_1_2_line_33 |  | 25 | 47 | 0.015322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_261-14_1_2_line_34 |  | 26 | 27 | 0.0085293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_261-14_1_2_line_35 |  | 27 | 32 | 0.019042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_261-14_1_2_line_36 |  | 28 | 33 | 0.011096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_261-14_1_2_line_37 |  | 32 | 48 | 0.0092615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_261-14_1_2_line_38 |  | 33 | 34 | 0.012049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-14_1_2_line_39 |  | 36 | 37 | 0.017701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-14_1_2_line_40 |  | 38 | 39 | 0.014103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-14_1_2_line_41 |  | 39 | 40 | 0.0041962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-14_1_2_line_42 |  | 39 | 41 | 0.019324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-14_1_2_line_43 |  | 42 | 43 | 0.019923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-14_1_2_line_44 |  | 43 | 44 | 0.019836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-14_1_2_line_45 |  | 44 | 45 | 0.036239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-14_1_2_line_46 |  | 45 | 46 | 0.028442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-14_1_2_line_47 |  | 47 | 48 | 0.0033383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-14_1_2_trafo_89 | 0.63 MVA 20/0.4 kV | 49 | 24 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2683265.5427 | 1250003.8283 | 2683268.6668 | 1250002.8715 | 2683271.4955 | 1250001.9883 | 2683276.5611 | 1250000.425
1 | 2683265.5427 | 1250003.8283 | 2683260.1634 | 1249983.66 | 2683257.132 | 1249973.259
2 | 2683276.5611 | 1250000.425 | 2683274.4583 | 1249993.179 | 2683268.7789 | 1249974.4853 | 2683268.0337 | 1249972.0359
3 | 2683252.6636 | 1249957.9273 | 2683257.132 | 1249973.259
4 | 2683323.9343 | 1249909.5342 | 2683334.079 | 1249933.906 | 2683342.4276 | 1249954.4498 | 2683363.0265 | 1249946.3
5 | 2683253.9272 | 1249806.3406 | 2683266.6196 | 1249803.1276 | 2683270.889 | 1249801.8199 | 2683273.1598 | 1249810.5472 | 2683275.6487 | 1249818.2657 | 2683277.8569 | 1249825.0017 | 2683282.6086 | 1249821.6104 | 2683287.8319 | 1249835.6942 | 2683292.9814 | 1249848.5761 | 2683296.2524 | 1249847.3879 | 2683297.6565 | 1249846.8739 | 2683305.4096 | 1249865.7524 | 2683311.9714 | 1249882.3681 | 2683313.8934 | 1249884.7524 | 2683318.7253 | 1249896.5958 | 2683323.9343 | 1249909.5342
6 | 2683323.9343 | 1249909.5342 | 2683358.7364 | 1249895.5703
7 | 2683369.5115 | 1249961.9139 | 2683363.0265 | 1249946.3
8 | 2683356.1588 | 1249927.8342 | 2683363.0265 | 1249946.3
9 | 2683253.9272 | 1249806.3406 | 2683251.276 | 1249806.9483 | 2683245.3903 | 1249807.2214 | 2683223.9347 | 1249804.8517 | 2683208.0287 | 1249805.1731
10 | 2683178.3734 | 1249969.479 | 2683190.4317 | 1249954.9374 | 2683199.3399 | 1249943.9157
11 | 2683178.3734 | 1249969.479 | 2683188.5917 | 1249977.9086
12 | 2683199.3399 | 1249943.9157 | 2683216.2415 | 1249923.0042
13 | 2683369.5115 | 1249961.9139 | 2683381.5002 | 1249956.7561
14 | 2683369.5115 | 1249961.9139 | 2683370.3386 | 1249963.9816
15 | 2683356.1588 | 1249927.8342 | 2683359.6082 | 1249926.3038 | 2683370.246 | 1249925.8197 | 2683371.9563 | 1249925.2768
16 | 2683219.4119 | 1249896.2228 | 2683218.3343 | 1249899.8326 | 2683223.8373 | 1249905.8365 | 2683227.8764 | 1249910.6968
17 | 2683219.4119 | 1249896.2228 | 2683216.3609 | 1249891.9657 | 2683212.4723 | 1249886.6408
18 | 2683227.8764 | 1249910.6968 | 2683224.889 | 1249912.6674 | 2683221.3826 | 1249916.6434 | 2683216.2415 | 1249923.0042
19 | 2683227.8764 | 1249910.6968 | 2683230.3122 | 1249910.9089 | 2683233.6801 | 1249911.957 | 2683236.4795 | 1249914.2313 | 2683237.6598 | 1249915.6712 | 2683240.57 | 1249914.3667 | 2683243.1153 | 1249913.2349
20 | 2683204.3886 | 1249875.1073 | 2683206.0564 | 1249877.855 | 2683212.4723 | 1249886.6408
21 | 2683262.2227 | 1249952.9354 | 2683262.8466 | 1249954.9875 | 2683268.0337 | 1249972.0359
22 | 2683243.1153 | 1249913.2349 | 2683240.57 | 1249914.3667 | 2683237.6598 | 1249915.6712 | 2683241.5647 | 1249922.5645 | 2683245.3793 | 1249931.0466 | 2683248.6602 | 1249944.1913
23 | 2683243.1153 | 1249913.2349 | 2683259.0345 | 1249908.607
24 | 2683248.6602 | 1249944.1913 | 2683227.7964 | 1249949.7136 | 2683227.3586 | 1249960.4487 | 2683216.7991 | 1249973.6436
25 | 2683248.6602 | 1249944.1913 | 2683252.6636 | 1249957.9273
26 | 2683260.6283 | 1249908.1437 | 2683259.0345 | 1249908.607
27 | 2683208.0287 | 1249805.1731 | 2683210.9561 | 1249819.3025 | 2683214.73 | 1249833.377 | 2683219.9259 | 1249844.6466
28 | 2683204.3886 | 1249875.1073 | 2683206.4239 | 1249873.19
29 | 2683206.4239 | 1249873.19 | 2683208.7466 | 1249870.7097 | 2683220.4423 | 1249858.7254
30 | 2683224.183 | 1249854.8924 | 2683220.4423 | 1249858.7254
31 | 2683287.4833 | 1249900.2262 | 2683291.6874 | 1249910.5373
32 | 2683287.4833 | 1249900.2262 | 2683286.7769 | 1249898.4936
33 | 2683280.9923 | 1249884.3055 | 2683286.7769 | 1249898.4936
34 | 2683260.6283 | 1249908.1437 | 2683261.5651 | 1249905.9552 | 2683259.4339 | 1249900.1877
35 | 2683259.4339 | 1249900.1877 | 2683259.4339 | 1249900.1877 | 2683271.8065 | 1249885.7124
36 | 2683224.183 | 1249854.8924 | 2683222.555 | 1249850.9221 | 2683220.4526 | 1249845.7888 | 2683219.9259 | 1249844.6466
37 | 2683279.732 | 1249881.2143 | 2683276.0454 | 1249882.43 | 2683272.3001 | 1249885.135 | 2683271.8065 | 1249885.7124
38 | 2683224.183 | 1249854.8924 | 2683228.8793 | 1249851.6782 | 2683232.5584 | 1249846.4926
39 | 2683397.7603 | 1249949.7606 | 2683381.5002 | 1249956.7561
40 | 2683390.3747 | 1249919.4314 | 2683396.3841 | 1249932.1897
41 | 2683390.3747 | 1249919.4314 | 2683392.3597 | 1249915.7343
42 | 2683390.3747 | 1249919.4314 | 2683371.9563 | 1249925.2768
43 | 2683318.6804 | 1249976.244 | 2683311.1514 | 1249958.3909 | 2683310.9388 | 1249957.8866
44 | 2683303.234 | 1249939.6085 | 2683310.9388 | 1249957.8866
45 | 2683275.6428 | 1249937.3875 | 2683298.7082 | 1249928.8718 | 2683303.234 | 1249939.6085
46 | 2683275.6428 | 1249937.3875 | 2683259.0001 | 1249942.3351 | 2683262.2227 | 1249952.9354
47 | 2683280.9923 | 1249884.3055 | 2683279.732 | 1249881.2143 | 2683279.732 | 1249881.2143

## bus_geodata
| x | y | coords
0 | 2683265.5427 | 1250003.8283
1 | 2683276.5611 | 1250000.425
2 | 2683257.132 | 1249973.259
3 | 2683323.9343 | 1249909.5342
4 | 2683363.0265 | 1249946.3
5 | 2683253.9272 | 1249806.3406
6 | 2683358.7364 | 1249895.5703
7 | 2683178.3734 | 1249969.479
8 | 2683199.3399 | 1249943.9157
9 | 2683188.5917 | 1249977.9086
10 | 2683369.5115 | 1249961.9139
11 | 2683356.1588 | 1249927.8342
12 | 2683219.4119 | 1249896.2228
13 | 2683227.8764 | 1249910.6968
14 | 2683212.4723 | 1249886.6408
15 | 2683268.0337 | 1249972.0359
16 | 2683243.1153 | 1249913.2349
17 | 2683248.6602 | 1249944.1913
18 | 2683259.0345 | 1249908.607
19 | 2683208.0287 | 1249805.1731
20 | 2683206.4239 | 1249873.19
21 | 2683204.3886 | 1249875.1073
22 | 2683220.4423 | 1249858.7254
23 | 2683287.4833 | 1249900.2262
24 | 2683291.6874 | 1249910.5373
25 | 2683286.7769 | 1249898.4936
26 | 2683260.6283 | 1249908.1437
27 | 2683259.4339 | 1249900.1877
28 | 2683219.9259 | 1249844.6466
29 | 2683216.7991 | 1249973.6436
30 | 2683252.6636 | 1249957.9273
31 | 2683216.2415 | 1249923.0042
32 | 2683271.8065 | 1249885.7124
33 | 2683224.183 | 1249854.8924
34 | 2683232.5584 | 1249846.4926
35 | 2683370.3386 | 1249963.9816
36 | 2683381.5002 | 1249956.7561
37 | 2683397.7603 | 1249949.7606
38 | 2683396.3841 | 1249932.1897
39 | 2683390.3747 | 1249919.4314
40 | 2683392.3597 | 1249915.7343
41 | 2683371.9563 | 1249925.2768
42 | 2683318.6804 | 1249976.244
43 | 2683310.9388 | 1249957.8866
44 | 2683303.234 | 1249939.6085
45 | 2683275.6428 | 1249937.3875
46 | 2683262.2227 | 1249952.9354
47 | 2683280.9923 | 1249884.3055
48 | 2683279.732 | 1249881.2143
49 | 2683287.4833 | 1249900.2262

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98613 | -0.26534 | 0 | 0
1 | 0.98573 | -0.27302 | 0 | 0
2 | 0.98721 | -0.24425 | 0.0084986 | 0.0021299
3 | 0.97427 | -0.49489 | 0 | 0
4 | 0.97224 | -0.53508 | 0 | 0
5 | 0.98096 | -0.36425 | 0 | 0
6 | 0.97309 | -0.51834 | 0.03402 | 0.0085262
7 | 0.98784 | -0.2321 | 0 | 0
8 | 0.98804 | -0.22813 | 0.015701 | 0.0039351
9 | 0.98775 | -0.23369 | 0.0067266 | 0.0016858
10 | 0.97185 | -0.54263 | 0 | 0
11 | 0.97154 | -0.54874 | 0.0089178 | 0.002235
12 | 0.98824 | -0.22395 | 0 | 0
13 | 0.98924 | -0.20482 | 0 | 0
14 | 0.98759 | -0.23639 | 0.0055828 | 0.0013992
15 | 0.98472 | -0.29279 | 0.0087368 | 0.0021896
16 | 0.99052 | -0.1802 | 0 | 0
17 | 0.98859 | -0.21754 | 0 | 0
18 | 0.99218 | -0.14844 | 0.0095036 | 0.0023818
19 | 0.98302 | -0.32444 | 0 | 0
20 | 0.98671 | -0.25332 | 0 | 0
21 | 0.98685 | -0.25052 | 0 | 0
22 | 0.98566 | -0.27356 | 0.0054359 | 0.0013624
23 | 0.99869 | -0.024774 | 0 | 0
24 | 1 | 0 | -0.2609 | -0.066608
25 | 0.99847 | -0.028945 | 0.0047834 | 0.0011988
26 | 0.99236 | -0.14513 | 0 | 0
27 | 0.99325 | -0.12812 | 0.0068924 | 0.0017274
28 | 0.98487 | -0.28873 | 0.0050417 | 0.0012636
29 | 0.98843 | -0.22062 | 0.0035028 | 0.00087788
30 | 0.98789 | -0.23122 | 0.007937 | 0.0019892
31 | 0.98859 | -0.21737 | 0.018825 | 0.004718
32 | 0.99529 | -0.089094 | 0.0056408 | 0.0014137
33 | 0.98539 | -0.27868 | 0 | 0
34 | 0.98533 | -0.27994 | 0.0058322 | 0.0014617
35 | 0.97184 | -0.54298 | 0.0084622 | 0.0021208
36 | 0.97166 | -0.54642 | 0.0061997 | 0.0015538
37 | 0.9715 | -0.54954 | 0.0095376 | 0.0023903
38 | 0.97056 | -0.56824 | 0.014171 | 0.0035517
39 | 0.97075 | -0.56455 | 0 | 0
40 | 0.97072 | -0.56502 | 0.0060591 | 0.0015185
41 | 0.97111 | -0.55732 | 0.0084161 | 0.0021093
42 | 0.98267 | -0.33284 | 0.0065589 | 0.0016438
43 | 0.98279 | -0.33049 | 0.0064513 | 0.0016168
44 | 0.98303 | -0.32583 | 0.0065869 | 0.0016508
45 | 0.98368 | -0.31303 | 0 | 0
46 | 0.9842 | -0.30299 | 0.0088087 | 0.0022077
47 | 0.99669 | -0.062525 | 0.0048623 | 0.0012186
48 | 0.99631 | -0.069714 | 0.0073131 | 0.0018328
49 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.03723 | 0.0093628 | -0.037217 | -0.0093542 | 1.3654e-05 | 8.5914e-06 | 0.05619 | 0.05619 | 0.05619 | 0.98613 | -0.26534 | 0.98573 | -0.27302 | 15.4368
1 | -0.03723 | -0.0093628 | 0.037268 | 0.0093864 | 3.7541e-05 | 2.3621e-05 | 0.05619 | 0.05619 | 0.05619 | 0.98613 | -0.26534 | 0.98721 | -0.24425 | 15.4367
2 | 0.037217 | 0.0093542 | -0.037181 | -0.0093321 | 3.5096e-05 | 2.2084e-05 | 0.05619 | 0.05619 | 0.05619 | 0.98573 | -0.27302 | 0.98472 | -0.29279 | 15.4368
3 | -0.045766 | -0.011516 | 0.045795 | 0.011534 | 2.8511e-05 | 1.8043e-05 | 0.068999 | 0.068999 | 0.068999 | 0.98721 | -0.24425 | 0.98789 | -0.23122 | 18.9559
4 | 0.061942 | 0.01559 | -0.061823 | -0.015516 | 0.00011875 | 7.424e-05 | 0.094628 | 0.094628 | 0.094628 | 0.97427 | -0.49489 | 0.97224 | -0.53508 | 12.9984
5 | -0.095999 | -0.02414 | 0.096602 | 0.024522 | 0.00060306 | 0.00038221 | 0.14665 | 0.14665 | 0.14665 | 0.97427 | -0.49489 | 0.98096 | -0.36425 | 20.1442
6 | 0.034058 | 0.0085501 | -0.03402 | -0.0085262 | 3.8056e-05 | 2.389e-05 | 0.052022 | 0.052022 | 0.052022 | 0.97427 | -0.49489 | 0.97309 | -0.51834 | 14.2918
7 | 0.024213 | 0.0060727 | -0.024204 | -0.0060674 | 8.7044e-06 | 5.3613e-06 | 0.037059 | 0.037059 | 0.037059 | 0.97224 | -0.53508 | 0.97185 | -0.54263 | 10.1811
8 | 0.03761 | 0.0094429 | -0.037586 | -0.0094275 | 2.4479e-05 | 1.5422e-05 | 0.057569 | 0.057569 | 0.057569 | 0.97224 | -0.53508 | 0.97154 | -0.54874 | 15.8157
9 | -0.096602 | -0.024522 | 0.096788 | 0.02464 | 0.00018537 | 0.00011748 | 0.14665 | 0.14665 | 0.14665 | 0.98096 | -0.36425 | 0.98302 | -0.32444 | 20.144
10 | -0.0067271 | -0.001686 | 0.0067284 | 0.0016864 | 1.2731e-06 | 3.9143e-07 | 0.010133 | 0.010133 | 0.010133 | 0.98784 | -0.2321 | 0.98804 | -0.22813 | 2.7839
11 | 0.0067271 | 0.001686 | -0.0067266 | -0.0016858 | 5.1008e-07 | 1.5688e-07 | 0.010133 | 0.010133 | 0.010133 | 0.98784 | -0.2321 | 0.98775 | -0.23369 | 2.7839
12 | -0.02243 | -0.0056215 | 0.022441 | 0.0056285 | 1.1505e-05 | 7.0189e-06 | 0.03378 | 0.03378 | 0.03378 | 0.98804 | -0.22813 | 0.98859 | -0.21737 | 9.2802
13 | 0.015742 | 0.0039465 | -0.015739 | -0.0039448 | 2.8432e-06 | 1.658e-06 | 0.024102 | 0.024103 | 0.024103 | 0.97185 | -0.54263 | 0.97166 | -0.54642 | 6.6216
14 | 0.0084624 | 0.0021209 | -0.0084622 | -0.0021208 | 1.402e-07 | 6.2131e-08 | 0.012957 | 0.012957 | 0.012957 | 0.97185 | -0.54263 | 0.97184 | -0.54298 | 3.5596
15 | 0.028668 | 0.0071925 | -0.028656 | -0.0071852 | 1.1726e-05 | 7.3037e-06 | 0.043911 | 0.043911 | 0.043911 | 0.97154 | -0.54874 | 0.97111 | -0.55732 | 12.0634
16 | -0.1192 | -0.030456 | 0.11931 | 0.030526 | 0.00011037 | 7.0171e-05 | 0.17969 | 0.17969 | 0.17969 | 0.98824 | -0.22395 | 0.98924 | -0.20482 | 24.6826
17 | 0.1192 | 0.030456 | -0.11913 | -0.03041 | 7.1626e-05 | 4.5538e-05 | 0.17969 | 0.17969 | 0.17969 | 0.98824 | -0.22395 | 0.98759 | -0.23639 | 24.6826
18 | 0.041291 | 0.010362 | -0.041266 | -0.010347 | 2.4681e-05 | 1.5577e-05 | 0.062115 | 0.062115 | 0.062115 | 0.98924 | -0.20482 | 0.98859 | -0.21737 | 17.0645
19 | -0.1606 | -0.040888 | 0.16079 | 0.04101 | 0.00019093 | 0.00012175 | 0.2418 | 0.2418 | 0.2418 | 0.98924 | -0.20482 | 0.99052 | -0.1802 | 33.2148
20 | 0.11354 | 0.029011 | -0.11347 | -0.028962 | 7.7521e-05 | 4.9253e-05 | 0.17128 | 0.17128 | 0.17128 | 0.98759 | -0.23639 | 0.98685 | -0.25052 | 23.5272
21 | 0.028445 | 0.0071424 | -0.028431 | -0.0071338 | 1.3835e-05 | 8.6007e-06 | 0.042988 | 0.042988 | 0.042988 | 0.98472 | -0.29279 | 0.9842 | -0.30299 | 11.8098
22 | 0.057373 | 0.014489 | -0.05727 | -0.014423 | 0.00010245 | 6.5098e-05 | 0.086227 | 0.086227 | 0.086227 | 0.99052 | -0.1802 | 0.98859 | -0.21754 | 23.6888
23 | -0.21816 | -0.055498 | 0.2185 | 0.055712 | 0.00033448 | 0.00021364 | 0.32803 | 0.32803 | 0.32803 | 0.99052 | -0.1802 | 0.99218 | -0.14844 | 45.0591
24 | 0.0035033 | 0.00087757 | -0.0035028 | -0.00087788 | 5.1328e-07 | -3.0257e-07 | 0.0052729 | 0.0052732 | 0.0052732 | 0.98859 | -0.21754 | 0.98843 | -0.22062 | 1.4487
25 | 0.053767 | 0.013546 | -0.053732 | -0.013524 | 3.5162e-05 | 2.2321e-05 | 0.080954 | 0.080954 | 0.080954 | 0.98859 | -0.21754 | 0.98789 | -0.23122 | 22.2402
26 | -0.228 | -0.058094 | 0.22804 | 0.058117 | 3.646e-05 | 2.3292e-05 | 0.34228 | 0.34228 | 0.34228 | 0.99218 | -0.14844 | 0.99236 | -0.14513 | 47.0169
27 | -0.096788 | -0.02464 | 0.096955 | 0.024745 | 0.00016698 | 0.00010582 | 0.14665 | 0.14665 | 0.14665 | 0.98302 | -0.32444 | 0.98487 | -0.28873 | 20.1439
28 | -0.11345 | -0.028952 | 0.11347 | 0.028962 | 1.5358e-05 | 9.7575e-06 | 0.17128 | 0.17128 | 0.17128 | 0.98671 | -0.25332 | 0.98685 | -0.25052 | 23.5272
29 | 0.11345 | 0.028952 | -0.11334 | -0.028882 | 0.0001108 | 7.0398e-05 | 0.17128 | 0.17128 | 0.17128 | 0.98671 | -0.25332 | 0.98566 | -0.27356 | 23.5273
30 | 0.10791 | 0.027519 | -0.10788 | -0.027502 | 2.6705e-05 | 1.6954e-05 | 0.16307 | 0.16307 | 0.16307 | 0.98566 | -0.27356 | 0.98539 | -0.27868 | 22.4
31 | -0.25894 | -0.066409 | 0.25925 | 0.066608 | 0.00031153 | 0.00019909 | 0.38635 | 0.38635 | 0.38635 | 0.99869 | -0.024774 | 1 | 0 | 53.0702
32 | 0.25894 | 0.066409 | -0.25889 | -0.066376 | 5.2366e-05 | 3.3465e-05 | 0.38635 | 0.38635 | 0.38635 | 0.99869 | -0.024774 | 0.99847 | -0.028945 | 53.0702
33 | 0.2541 | 0.065177 | -0.25369 | -0.064913 | 0.00041315 | 0.00026401 | 0.37922 | 0.37922 | 0.37922 | 0.99847 | -0.028945 | 0.99669 | -0.062525 | 52.0911
34 | -0.22804 | -0.058117 | 0.22823 | 0.058237 | 0.00018736 | 0.00011969 | 0.34228 | 0.34228 | 0.34228 | 0.99236 | -0.14513 | 0.99325 | -0.12812 | 47.0169
35 | -0.23512 | -0.059964 | 0.23556 | 0.060248 | 0.00044393 | 0.00028362 | 0.35261 | 0.35261 | 0.35261 | 0.99325 | -0.12812 | 0.99529 | -0.089094 | 48.4353
36 | -0.102 | -0.026009 | 0.10205 | 0.02604 | 4.9511e-05 | 3.1405e-05 | 0.15426 | 0.15426 | 0.15426 | 0.98487 | -0.28873 | 0.98539 | -0.27868 | 21.1902
37 | -0.2412 | -0.061661 | 0.24143 | 0.061806 | 0.00022636 | 0.00014463 | 0.36104 | 0.36104 | 0.36104 | 0.99529 | -0.089094 | 0.99631 | -0.069714 | 49.5937
38 | 0.0058325 | 0.0014617 | -0.0058322 | -0.0014617 | 3.5051e-07 | 7.0845e-08 | 0.0088075 | 0.0088076 | 0.0088076 | 0.98539 | -0.27868 | 0.98533 | -0.27994 | 2.4197
39 | 0.009539 | 0.002391 | -0.0095376 | -0.0023903 | 1.4165e-06 | 6.8738e-07 | 0.014608 | 0.014608 | 0.014608 | 0.97166 | -0.54642 | 0.9715 | -0.54954 | 4.0133
40 | -0.014171 | -0.0035517 | 0.014174 | 0.0035531 | 2.4965e-06 | 1.4235e-06 | 0.021727 | 0.021727 | 0.021727 | 0.97056 | -0.56824 | 0.97075 | -0.56455 | 5.969
41 | 0.0060592 | 0.0015186 | -0.0060591 | -0.0015185 | 1.3575e-07 | 3.5001e-08 | 0.0092879 | 0.0092879 | 0.0092879 | 0.97075 | -0.56455 | 0.97072 | -0.56502 | 2.5516
42 | -0.020233 | -0.0050717 | 0.02024 | 0.0050759 | 6.9705e-06 | 4.2221e-06 | 0.031015 | 0.031015 | 0.031015 | 0.97075 | -0.56455 | 0.97111 | -0.55732 | 8.5206
43 | -0.0065589 | -0.0016438 | 0.0065597 | 0.001644 | 7.3697e-07 | 2.1923e-07 | 0.0099319 | 0.0099318 | 0.0099319 | 0.98267 | -0.33284 | 0.98279 | -0.33049 | 2.7285
44 | -0.013011 | -0.0032609 | 0.013014 | 0.0032625 | 2.8866e-06 | 1.596e-06 | 0.0197 | 0.019699 | 0.0197 | 0.98279 | -0.33049 | 0.98303 | -0.32583 | 5.412
45 | -0.019601 | -0.0049133 | 0.019613 | 0.0049205 | 1.1963e-05 | 7.1966e-06 | 0.02967 | 0.02967 | 0.02967 | 0.98303 | -0.32583 | 0.98368 | -0.31303 | 8.1511
46 | -0.019613 | -0.0049205 | 0.019622 | 0.0049262 | 9.3891e-06 | 5.6478e-06 | 0.02967 | 0.02967 | 0.02967 | 0.98368 | -0.31303 | 0.9842 | -0.30299 | 8.1511
47 | 0.24883 | 0.063694 | -0.24874 | -0.063639 | 8.6603e-05 | 5.5339e-05 | 0.37196 | 0.37196 | 0.37196 | 0.99669 | -0.062525 | 0.99631 | -0.069714 | 51.0939

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.27281 | 0.069592

## res_load
| p_mw | q_mvar
0 | 0.0084986 | 0.0021299
1 | 0.03402 | 0.0085262
2 | 0.015701 | 0.0039351
3 | 0.0067266 | 0.0016858
4 | 0.0089178 | 0.002235
5 | 0.0055828 | 0.0013992
6 | 0.0087368 | 0.0021896
7 | 0.0095036 | 0.0023818
8 | 0.0054359 | 0.0013624
9 | 0.011903 | 0.0029832
10 | 0.0047834 | 0.0011988
11 | 0.0068924 | 0.0017274
12 | 0.0050417 | 0.0012636
13 | 0.0035028 | 0.00087788
14 | 0.007937 | 0.0019892
15 | 0.018825 | 0.004718
16 | 0.0056408 | 0.0014137
17 | 0.0058322 | 0.0014617
18 | 0.0084622 | 0.0021208
19 | 0.0061997 | 0.0015538
20 | 0.0095376 | 0.0023903
21 | 0.014171 | 0.0035517
22 | 0.0060591 | 0.0015185
23 | 0.0084161 | 0.0021093
24 | 0.0065589 | 0.0016438
25 | 0.0064513 | 0.0016168
26 | 0.0065869 | 0.0016508
27 | 0.0088087 | 0.0022077
28 | 0.0048623 | 0.0012186
29 | 0.0073131 | 0.0018328

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1