## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-162_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-162_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-162_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-162_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-162_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_261-162_0_3_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_261-162_0_3_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_261-162_0_3_node_69 | 0.4 | n |  | TRUE
8 | bus_LV_261-162_0_3_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_261-162_0_3_node_22 | 0.4 | n |  | TRUE
10 | bus_LV_261-162_0_3_node_76 | 0.4 | n |  | TRUE
11 | bus_LV_261-162_0_3_node_73 | 0.4 | n |  | TRUE
12 | bus_LV_261-162_0_3_node_13 | 0.4 | n |  | TRUE
13 | bus_LV_261-162_0_3_node_50 | 0.4 | n |  | TRUE
14 | bus_LV_261-162_0_3_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_261-162_0_3_node_32 | 0.4 | n |  | TRUE
16 | bus_LV_261-162_0_3_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_261-162_0_3_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_261-162_0_3_node_75 | 0.4 | n |  | TRUE
19 | bus_LV_261-162_0_3_node_74 | 0.4 | n |  | TRUE
20 | bus_LV_261-162_0_3_node_88 | 0.4 | n |  | TRUE
21 | bus_LV_261-162_0_3_node_38 | 0.4 | n |  | TRUE
22 | bus_LV_261-162_0_3_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_261-162_0_3_node_80 | 0.4 | n |  | TRUE
24 | bus_LV_261-162_0_3_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_261-162_0_3_node_79 | 0.4 | n |  | TRUE
26 | bus_LV_261-162_0_3_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_261-162_0_3_node_84 | 0.4 | n |  | TRUE
28 | bus_LV_261-162_0_3_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_261-162_0_3_node_83 | 0.4 | n |  | TRUE
30 | bus_LV_261-162_0_3_node_82 | 0.4 | n |  | TRUE
31 | bus_LV_261-162_0_3_node_72 | 0.4 | n |  | TRUE
32 | bus_LV_261-162_0_3_node_68 | 0.4 | n |  | TRUE
33 | bus_LV_261-162_0_3_node_53 | 0.4 | n |  | TRUE
34 | bus_LV_261-162_0_3_node_52 | 0.4 | n |  | TRUE
35 | bus_LV_261-162_0_3_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_261-162_0_3_node_33 | 0.4 | n |  | TRUE
37 | bus_LV_261-162_0_3_node_28 | 0.4 | n |  | TRUE
38 | bus_LV_261-162_0_3_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_261-162_0_3_node_81 | 0.4 | n |  | TRUE
40 | bus_LV_261-162_0_3_node_36 | 0.4 | n |  | TRUE
41 | bus_LV_261-162_0_3_node_49 | 0.4 | n |  | TRUE
42 | bus_LV_261-162_0_3_node_47 | 0.4 | n |  | TRUE
43 | bus_LV_261-162_0_3_node_78 | 0.4 | n |  | TRUE
44 | bus_LV_261-162_0_3_node_77 | 0.4 | n |  | TRUE
45 | bus_LV_261-162_0_3_node_86 | 0.4 | n |  | TRUE
46 | bus_LV_261-162_0_3_node_85 | 0.4 | n |  | TRUE
47 | bus_LV_261-162_0_3_node_55 | 0.4 | n |  | TRUE
48 | bus_LV_261-162_0_3_node_60 | 0.4 | n |  | TRUE
49 | bus_LV_261-162_0_3_node_54 | 0.4 | n |  | TRUE
50 | bus_LV_261-162_0_3_node_61 | 0.4 | n |  | TRUE
51 | bus_LV_261-162_0_3_node_87 | 0.4 | n |  | TRUE
52 | bus_LV_261-162_0_3_node_58 | 0.4 | n |  | TRUE
53 | bus_LV_261-162_0_3_node_66 | 0.4 | n |  | TRUE
54 | bus_LV_261-162_0_3_node_67 | 0.4 | n |  | TRUE
55 | bus_LV_261-162_0_3_node_29 | 0.4 | n |  | TRUE
56 | bus_LV_261-162_0_3_node_31 | 0.4 | n |  | TRUE
57 | bus_LV_261-162_0_3_node_41 | 0.4 | n |  | TRUE
58 | bus_LV_261-162_0_3_node_40 | 0.4 | n |  | TRUE
59 | bus_LV_261-162_0_3_node_51 | 0.4 | n |  | TRUE
60 | bus_LV_261-162_0_3_node_34 | 0.4 | n |  | TRUE
61 | bus_LV_261-162_0_3_node_35 | 0.4 | n |  | TRUE
62 | bus_LV_261-162_0_3_node_44 | 0.4 | n |  | TRUE
63 | bus_LV_261-162_0_3_node_37 | 0.4 | n |  | TRUE
64 | bus_LV_261-162_0_3_node_39 | 0.4 | n |  | TRUE
65 | bus_LV_261-162_0_3_node_42 | 0.4 | n |  | TRUE
66 | bus_LV_261-162_0_3_node_45 | 0.4 | n |  | TRUE
67 | bus_LV_261-162_0_3_node_43 | 0.4 | n |  | TRUE
68 | bus_LV_261-162_0_3_node_46 | 0.4 | n |  | TRUE
69 | bus_LV_261-162_0_3_node_48 | 0.4 | n |  | TRUE
70 | bus_LV_261-162_0_3_node_70 | 0.4 | n |  | TRUE
71 | bus_LV_261-162_0_3_node_56 | 0.4 | n |  | TRUE
72 | bus_LV_261-162_0_3_node_57 | 0.4 | n |  | TRUE
73 | bus_LV_261-162_0_3_node_59 | 0.4 | n |  | TRUE
74 | bus_LV_261-162_0_3_node_62 | 0.4 | n |  | TRUE
75 | bus_LV_261-162_0_3_node_63 | 0.4 | n |  | TRUE
76 | bus_LV_261-162_0_3_node_71 | 0.4 | n |  | TRUE
77 | bus_LV_261-162_0_3_node_65 | 0.4 | n |  | TRUE
78 | bus_LV_261-162_0_3_node_64 | 0.4 | n |  | TRUE
79 | bus_MV_518_0_node_31 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-162_0_3_load_0 | 0 | 0.010277 | 0.0025757 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-162_0_3_load_5 | 4 | 0.0066338 | 0.0016626 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-162_0_3_load_69 | 7 | 0.007131 | 0.0017872 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-162_0_3_load_76 | 10 | 0.0093535 | 0.0023442 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-162_0_3_load_73 | 11 | 0.0065737 | 0.0016475 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-162_0_3_load_50 | 13 | 0.0019245 | 0.00048231 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-162_0_3_load_32 | 15 | 0.0043548 | 0.0010914 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-162_0_3_load_74 | 19 | 0.0072455 | 0.0018159 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-162_0_3_load_88 | 20 | 0.0077912 | 0.0019527 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-162_0_3_load_38 | 21 | 0.0049598 | 0.001243 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-162_0_3_load_80 | 23 | 0.0072055 | 0.0018059 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-162_0_3_load_79 | 25 | 0.007175 | 0.0017982 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-162_0_3_load_84 | 27 | 0.0093219 | 0.0023363 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-162_0_3_load_83 | 29 | 0.012135 | 0.0030414 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-162_0_3_load_82 | 30 | 0.011958 | 0.002997 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-162_0_3_load_72 | 31 | 0.0074109 | 0.0018573 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-162_0_3_load_68 | 32 | 0.0054035 | 0.0013542 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-162_0_3_load_53 | 33 | 0.0046726 | 0.0011711 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-162_0_3_load_52 | 34 | 0.0050683 | 0.0012702 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-162_0_3_load_30 | 35 | 0.0018633 | 0.00046698 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-162_0_3_load_33 | 36 | 0.0030571 | 0.00076618 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-162_0_3_load_28 | 37 | 0.003045 | 0.00076314 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-162_0_3_load_27 | 38 | 0.0018724 | 0.00046927 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-162_0_3_load_81 | 39 | 0.012406 | 0.0031092 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-162_0_3_load_36 | 40 | 0.0040442 | 0.0010136 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-162_0_3_load_49 | 41 | 0.0082383 | 0.0020647 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-162_0_3_load_47 | 42 | 0.0094091 | 0.0023581 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-162_0_3_load_78 | 43 | 0.0071914 | 0.0018023 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-162_0_3_load_86 | 45 | 0.012114 | 0.0030361 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-162_0_3_load_85 | 46 | 0.009024 | 0.0022616 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-162_0_3_load_55 | 47 | 0.002945 | 0.00073808 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-162_0_3_load_87 | 51 | 0.0032146 | 0.00080565 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-162_0_3_load_66 | 53 | 0.0017661 | 0.00044263 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-162_0_3_load_67 | 54 | 0.0008088 | 0.00020271 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-162_0_3_load_40 | 58 | 0.0085073 | 0.0021321 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-162_0_3_load_51 | 59 | 0.0027762 | 0.00069578 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-162_0_3_load_34 | 60 | 0.0075408 | 0.0018899 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-162_0_3_load_35 | 61 | 0.01064 | 0.0026667 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-162_0_3_load_44 | 62 | 0.0025736 | 0.00064501 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-162_0_3_load_37 | 63 | 0.0034374 | 0.00086149 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-162_0_3_load_39 | 64 | 0.0033637 | 0.00084303 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-162_0_3_load_45 | 66 | 0.0021106 | 0.00052896 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-162_0_3_load_43 | 67 | 0.0068615 | 0.0017196 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-162_0_3_load_48 | 69 | 0.006251 | 0.0015667 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-162_0_3_load_70 | 70 | 0.00069974 | 0.00017537 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-162_0_3_load_56 | 71 | 0.007744 | 0.0019408 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-162_0_3_load_57 | 72 | 0.0017517 | 0.00043901 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-162_0_3_load_59 | 73 | 0.0087227 | 0.0021861 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-162_0_3_load_62 | 74 | 0.0007513 | 0.00018829 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-162_0_3_load_71 | 76 | 0.0015246 | 0.00038209 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-162_0_3_load_65 | 77 | 0.00055543 | 0.0001392 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-162_0_3_load_64 | 78 | 0.0017633 | 0.00044191 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 37 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-162_0_3_line_0 |  | 0 | 1 | 0.027661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-162_0_3_line_1 |  | 0 | 2 | 0.017879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-162_0_3_line_2 |  | 1 | 3 | 0.037681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-162_0_3_line_3 |  | 2 | 4 | 0.018797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-162_0_3_line_4 |  | 2 | 5 | 0.024199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-162_0_3_line_5 |  | 3 | 6 | 0.039203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_261-162_0_3_line_6 |  | 3 | 7 | 0.033729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-162_0_3_line_7 |  | 4 | 8 | 0.0053189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-162_0_3_line_8 |  | 5 | 9 | 0.00531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-162_0_3_line_9 |  | 5 | 10 | 0.016273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-162_0_3_line_10 |  | 6 | 12 | 0.009396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-162_0_3_line_11 |  | 6 | 13 | 0.030456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_261-162_0_3_line_12 |  | 7 | 32 | 0.024343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-162_0_3_line_13 |  | 8 | 11 | 0.016993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-162_0_3_line_14 |  | 9 | 31 | 0.014796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-162_0_3_line_15 |  | 10 | 26 | 0.016155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-162_0_3_line_16 |  | 11 | 19 | 0.023877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-162_0_3_line_17 |  | 12 | 20 | 0.026187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-162_0_3_line_18 |  | 13 | 35 | 0.026275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_261-162_0_3_line_19 |  | 14 | 15 | 0.0088301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-162_0_3_line_20 |  | 14 | 16 | 0.031983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-162_0_3_line_21 |  | 15 | 36 | 0.028173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-162_0_3_line_22 |  | 16 | 21 | 0.037838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-162_0_3_line_23 |  | 17 | 18 | 0.004536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-162_0_3_line_24 |  | 17 | 19 | 0.019946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-162_0_3_line_25 |  | 18 | 39 | 0.017917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-162_0_3_line_26 |  | 20 | 33 | 0.013237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-162_0_3_line_27 |  | 21 | 40 | 0.01621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-162_0_3_line_28 |  | 22 | 23 | 0.013359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-162_0_3_line_29 |  | 22 | 24 | 0.047293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-162_0_3_line_30 |  | 22 | 25 | 0.0088828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-162_0_3_line_31 |  | 24 | 26 | 0.03528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-162_0_3_line_32 |  | 24 | 27 | 0.018305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-162_0_3_line_33 |  | 25 | 43 | 0.022193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-162_0_3_line_34 |  | 27 | 46 | 0.028478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-162_0_3_line_35 |  | 28 | 29 | 0.0062162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-162_0_3_line_36 |  | 28 | 30 | 0.022215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-162_0_3_line_37 |  | 30 | 39 | 0.028716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-162_0_3_line_38 |  | 33 | 34 | 0.016441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-162_0_3_line_39 |  | 34 | 59 | 0.015321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-162_0_3_line_40 |  | 35 | 55 | 0.012554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_261-162_0_3_line_41 |  | 36 | 60 | 0.031954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-162_0_3_line_42 |  | 37 | 38 | 0.0047046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_261-162_0_3_line_43 |  | 38 | 55 | 0.0082981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_261-162_0_3_line_44 |  | 40 | 63 | 0.0099696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-162_0_3_line_45 |  | 41 | 42 | 0.018031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-162_0_3_line_46 |  | 42 | 68 | 0.017674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-162_0_3_line_47 |  | 44 | 45 | 0.01521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-162_0_3_line_48 |  | 44 | 46 | 0.013366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-162_0_3_line_49 |  | 47 | 48 | 0.011291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-162_0_3_line_50 |  | 47 | 49 | 0.015172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-162_0_3_line_51 |  | 48 | 70 | 0.1261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-162_0_3_line_52 |  | 48 | 52 | 0.017167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-162_0_3_line_53 |  | 49 | 62 | 0.0057472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-162_0_3_line_54 |  | 49 | 61 | 0.022543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-162_0_3_line_55 |  | 50 | 51 | 0.0054875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-162_0_3_line_56 |  | 50 | 52 | 0.009146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-162_0_3_line_57 |  | 52 | 71 | 0.0029015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-162_0_3_line_58 |  | 53 | 54 | 0.034568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-162_0_3_line_59 |  | 54 | 75 | 0.021219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-162_0_3_line_60 |  | 55 | 56 | 0.033037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-162_0_3_line_61 |  | 56 | 57 | 0.010116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-162_0_3_line_62 |  | 57 | 58 | 0.027723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-162_0_3_line_63 |  | 58 | 65 | 0.015967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-162_0_3_line_64 |  | 60 | 61 | 0.022231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-162_0_3_line_65 |  | 62 | 65 | 0.016326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-162_0_3_line_66 |  | 63 | 64 | 0.0018111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-162_0_3_line_67 |  | 65 | 66 | 0.021631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-162_0_3_line_68 |  | 66 | 69 | 0.025792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-162_0_3_line_69 |  | 67 | 68 | 0.014573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-162_0_3_line_70 |  | 68 | 69 | 0.026403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-162_0_3_line_71 |  | 70 | 76 | 7.2865e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-162_0_3_line_72 |  | 71 | 72 | 0.024729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-162_0_3_line_73 |  | 72 | 73 | 0.0068611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-162_0_3_line_74 |  | 73 | 74 | 0.019071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-162_0_3_line_75 |  | 74 | 75 | 0.023876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-162_0_3_line_76 |  | 75 | 77 | 0.0079156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-162_0_3_line_77 |  | 77 | 78 | 0.026154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-162_0_3_trafo_28 | 0.63 MVA 20/0.4 kV | 79 | 37 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2678440.7987 | 1251911.3828 | 2678413.3303 | 1251908.1284
1 | 2678395.5758 | 1251906.0249 | 2678413.3303 | 1251908.1284
2 | 2678409.4832 | 1251932.4728 | 2678440.7987 | 1251911.3828
3 | 2678395.5758 | 1251906.0249 | 2678376.9087 | 1251903.8191
4 | 2678398.9423 | 1251882.0629 | 2678397.5677 | 1251891.8185 | 2678395.5758 | 1251906.0249
5 | 2678379.5358 | 1251943.1735 | 2678383.4629 | 1251934.4412 | 2678388.4843 | 1251933.14 | 2678394.315 | 1251933.4173 | 2678401.541 | 1251938.3276 | 2678409.4832 | 1251932.4728
6 | 2678409.4832 | 1251932.4728 | 2678439.6839 | 1251947.4923
7 | 2678371.6266 | 1251903.1949 | 2678376.9087 | 1251903.8191
8 | 2678398.9423 | 1251882.0629 | 2678404.2412 | 1251882.6
9 | 2678398.9423 | 1251882.0629 | 2678382.7531 | 1251880.409
10 | 2678386.8695 | 1251949.0748 | 2678379.5358 | 1251943.1735
11 | 2678379.5358 | 1251943.1735 | 2678374.3832 | 1251949.8325 | 2678367.514 | 1251952.7438 | 2678353.3272 | 1251956.09
12 | 2678461.5061 | 1251946.1773 | 2678457.1679 | 1251947.4038 | 2678448.9917 | 1251952.1213 | 2678439.6839 | 1251947.4923
13 | 2678371.6266 | 1251903.1949 | 2678354.7522 | 1251901.1946
14 | 2678404.2412 | 1251882.6 | 2678418.9602 | 1251884.1034
15 | 2678366.6815 | 1251878.7671 | 2678382.7531 | 1251880.409
16 | 2678354.7522 | 1251901.1946 | 2678331.0412 | 1251898.3838
17 | 2678386.8695 | 1251949.0748 | 2678382.432 | 1251953.5973 | 2678381.4429 | 1251960.467 | 2678381.0969 | 1251965.5106 | 2678380.9395 | 1251973.3642
18 | 2678353.3272 | 1251956.09 | 2678333.678 | 1251960.7246 | 2678327.7543 | 1251961.2022 | 2678327.6125 | 1251961.1805
19 | 2678272.2838 | 1251930.58 | 2678268.6209 | 1251938.6146
20 | 2678272.2838 | 1251930.58 | 2678280.0252 | 1251903.3622 | 2678276.4119 | 1251902.6362
21 | 2678256.9342 | 1251964.2498 | 2678268.6209 | 1251938.6146
22 | 2678276.4119 | 1251902.6362 | 2678244.9778 | 1251923.6985
23 | 2678311.7312 | 1251891.5279 | 2678311.2338 | 1251896.0358
24 | 2678311.2338 | 1251896.0358 | 2678331.0412 | 1251898.3838
25 | 2678311.7312 | 1251891.5279 | 2678293.9082 | 1251889.6921
26 | 2678380.6744 | 1251986.5984 | 2678380.9395 | 1251973.3642
27 | 2678233.4369 | 1251935.0381 | 2678234.8696 | 1251934.033 | 2678244.8243 | 1251923.8013 | 2678244.9778 | 1251923.6985
28 | 2678352.518 | 1251844.8326 | 2678339.2352 | 1251843.4094
29 | 2678352.518 | 1251844.8326 | 2678352.2032 | 1251846.9522 | 2678358.7152 | 1251847.6499 | 2678369.5348 | 1251849.094 | 2678368.7993 | 1251860.1814 | 2678363.666 | 1251859.6687 | 2678362.1276 | 1251870.9789
30 | 2678352.518 | 1251844.8326 | 2678361.3529 | 1251845.7543
31 | 2678362.1276 | 1251870.9789 | 2678363.666 | 1251859.6687 | 2678368.7993 | 1251860.1814 | 2678367.3213 | 1251872.6266 | 2678366.6815 | 1251878.7671
32 | 2678362.1276 | 1251870.9789 | 2678343.9323 | 1251868.982
33 | 2678383.4263 | 1251848.0572 | 2678361.3529 | 1251845.7543
34 | 2678343.9323 | 1251868.982 | 2678315.6239 | 1251865.8752
35 | 2678243.2457 | 1251884.4737 | 2678237.0645 | 1251883.8142
36 | 2678243.2457 | 1251884.4737 | 2678265.3435 | 1251886.7498
37 | 2678293.9082 | 1251889.6921 | 2678265.3435 | 1251886.7498
38 | 2678380.6744 | 1251986.5984 | 2678371.4217 | 1251986.5426 | 2678364.2332 | 1251986.5329
39 | 2678348.912 | 1251986.5123 | 2678364.2332 | 1251986.5329
40 | 2678315.7426 | 1251957.4629 | 2678322.0974 | 1251960.3379 | 2678327.6125 | 1251961.1805
41 | 2678256.9342 | 1251964.2498 | 2678255.7817 | 1251966.7777 | 2678246.6333 | 1251979.9666 | 2678240.9822 | 1251991.8119
42 | 2678308.608 | 1251953.2254 | 2678304.563 | 1251950.8229
43 | 2678315.7426 | 1251957.4629 | 2678308.608 | 1251953.2254
44 | 2678233.4369 | 1251935.0381 | 2678225.2753 | 1251940.7635
45 | 2678346.1213 | 1252028.7751 | 2678328.0901 | 1252028.6982
46 | 2678310.4164 | 1252028.6228 | 2678328.0901 | 1252028.6982
47 | 2678302.338 | 1251864.4171 | 2678287.2192 | 1251862.7549
48 | 2678302.338 | 1251864.4171 | 2678315.6239 | 1251865.8752
49 | 2678234.0224 | 1252048.4395 | 2678227.0891 | 1252057.3657
50 | 2678234.0224 | 1252048.4395 | 2678242.117 | 1252038.4501 | 2678243.1484 | 1252036.3622
51 | 2678227.0891 | 1252057.3657 | 2678207.8273 | 1252040.8326 | 2678200.0759 | 1252035.6932 | 2678195.2041 | 1252034.2501 | 2678188.7418 | 1252033.7978 | 2678137.8386 | 1252040.8539 | 2678109.6202 | 1252044.608
52 | 2678216.562 | 1252070.9479 | 2678227.0891 | 1252057.3657
53 | 2678243.1484 | 1252036.3622 | 2678247.5191 | 1252032.6303
54 | 2678243.1484 | 1252036.3622 | 2678242.6738 | 1252024.8697 | 2678240.6431 | 1252014.0176
55 | 2678223.6479 | 1252076.7568 | 2678228.9362 | 1252078.2218
56 | 2678216.562 | 1252070.9479 | 2678223.6479 | 1252076.7568
57 | 2678216.562 | 1252070.9479 | 2678214.3575 | 1252072.8344
58 | 2678123.6129 | 1252161.5859 | 2678131.6578 | 1252148.3517 | 2678141.5677 | 1252132.0465
59 | 2678152.5884 | 1252113.9134 | 2678141.5677 | 1252132.0465
60 | 2678300.3018 | 1251986.4469 | 2678306.4096 | 1251978.3216 | 2678310.8597 | 1251969.9854 | 2678315.7426 | 1251957.4629
61 | 2678300.3018 | 1251986.4469 | 2678292.9861 | 1251993.4554
62 | 2678292.9861 | 1251993.4554 | 2678272.0139 | 1252011.5863
63 | 2678259.9349 | 1252022.0289 | 2678272.0139 | 1252011.5863
64 | 2678240.6431 | 1252014.0176 | 2678240.4461 | 1252012.9648 | 2678240.9822 | 1251991.8119 | 2678240.9822 | 1251991.8119
65 | 2678259.9349 | 1252022.0289 | 2678247.5191 | 1252032.6303
66 | 2678223.7927 | 1251941.8036 | 2678225.2753 | 1251940.7635
67 | 2678259.9349 | 1252022.0289 | 2678274.4462 | 1252038.0703
68 | 2678274.4462 | 1252038.0703 | 2678278.2494 | 1252042.2746 | 2678298.3673 | 1252042.6934
69 | 2678310.4164 | 1252028.6228 | 2678310.2427 | 1252014.0512
70 | 2678310.4164 | 1252028.6228 | 2678310.4459 | 1252042.9449 | 2678298.3673 | 1252042.6934
71 | 2678109.5479 | 1252044.6176 | 2678109.6202 | 1252044.608
72 | 2678214.3575 | 1252072.8344 | 2678202.3708 | 1252083.0918 | 2678195.1381 | 1252088.3676
73 | 2678189.3837 | 1252092.0923 | 2678193.0429 | 1252089.896 | 2678195.1381 | 1252088.3676
74 | 2678189.3837 | 1252092.0923 | 2678184.7048 | 1252094.9008 | 2678172.5546 | 1252101.0429
75 | 2678152.5884 | 1252113.9134 | 2678162.2826 | 1252106.2356 | 2678172.5546 | 1252101.0429
76 | 2678152.5884 | 1252113.9134 | 2678145.9799 | 1252112.5363 | 2678144.8201 | 1252112.426
77 | 2678118.8473 | 1252113.5171 | 2678134.5825 | 1252111.4519 | 2678144.8201 | 1252112.426

## bus_geodata
| x | y | coords
0 | 2678413.3303 | 1251908.1284
1 | 2678440.7987 | 1251911.3828
2 | 2678395.5758 | 1251906.0249
3 | 2678409.4832 | 1251932.4728
4 | 2678376.9087 | 1251903.8191
5 | 2678398.9423 | 1251882.0629
6 | 2678379.5358 | 1251943.1735
7 | 2678439.6839 | 1251947.4923
8 | 2678371.6266 | 1251903.1949
9 | 2678404.2412 | 1251882.6
10 | 2678382.7531 | 1251880.409
11 | 2678354.7522 | 1251901.1946
12 | 2678386.8695 | 1251949.0748
13 | 2678353.3272 | 1251956.09
14 | 2678272.2838 | 1251930.58
15 | 2678268.6209 | 1251938.6146
16 | 2678276.4119 | 1251902.6362
17 | 2678311.2338 | 1251896.0358
18 | 2678311.7312 | 1251891.5279
19 | 2678331.0412 | 1251898.3838
20 | 2678380.9395 | 1251973.3642
21 | 2678244.9778 | 1251923.6985
22 | 2678352.518 | 1251844.8326
23 | 2678339.2352 | 1251843.4094
24 | 2678362.1276 | 1251870.9789
25 | 2678361.3529 | 1251845.7543
26 | 2678366.6815 | 1251878.7671
27 | 2678343.9323 | 1251868.982
28 | 2678243.2457 | 1251884.4737
29 | 2678237.0645 | 1251883.8142
30 | 2678265.3435 | 1251886.7498
31 | 2678418.9602 | 1251884.1034
32 | 2678461.5061 | 1251946.1773
33 | 2678380.6744 | 1251986.5984
34 | 2678364.2332 | 1251986.5329
35 | 2678327.6125 | 1251961.1805
36 | 2678256.9342 | 1251964.2498
37 | 2678304.563 | 1251950.8229
38 | 2678308.608 | 1251953.2254
39 | 2678293.9082 | 1251889.6921
40 | 2678233.4369 | 1251935.0381
41 | 2678346.1213 | 1252028.7751
42 | 2678328.0901 | 1252028.6982
43 | 2678383.4263 | 1251848.0572
44 | 2678302.338 | 1251864.4171
45 | 2678287.2192 | 1251862.7549
46 | 2678315.6239 | 1251865.8752
47 | 2678234.0224 | 1252048.4395
48 | 2678227.0891 | 1252057.3657
49 | 2678243.1484 | 1252036.3622
50 | 2678223.6479 | 1252076.7568
51 | 2678228.9362 | 1252078.2218
52 | 2678216.562 | 1252070.9479
53 | 2678123.6129 | 1252161.5859
54 | 2678141.5677 | 1252132.0465
55 | 2678315.7426 | 1251957.4629
56 | 2678300.3018 | 1251986.4469
57 | 2678292.9861 | 1251993.4554
58 | 2678272.0139 | 1252011.5863
59 | 2678348.912 | 1251986.5123
60 | 2678240.9822 | 1251991.8119
61 | 2678240.6431 | 1252014.0176
62 | 2678247.5191 | 1252032.6303
63 | 2678225.2753 | 1251940.7635
64 | 2678223.7927 | 1251941.8036
65 | 2678259.9349 | 1252022.0289
66 | 2678274.4462 | 1252038.0703
67 | 2678310.2427 | 1252014.0512
68 | 2678310.4164 | 1252028.6228
69 | 2678298.3673 | 1252042.6934
70 | 2678109.6202 | 1252044.608
71 | 2678214.3575 | 1252072.8344
72 | 2678195.1381 | 1252088.3676
73 | 2678189.3837 | 1252092.0923
74 | 2678172.5546 | 1252101.0429
75 | 2678152.5884 | 1252113.9134
76 | 2678109.5479 | 1252044.6176
77 | 2678144.8201 | 1252112.426
78 | 2678118.8473 | 1252113.5171
79 | 2678315.7426 | 1251957.4629

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98425 | -0.30097 | 0.010277 | 0.0025757
1 | 0.98774 | -0.23351 | 0 | 0
2 | 0.98216 | -0.34151 | 0 | 0
3 | 0.9925 | -0.14237 | 0 | 0
4 | 0.98117 | -0.36087 | 0.0066338 | 0.0016626
5 | 0.98062 | -0.37164 | 0 | 0
6 | 0.9952 | -0.090975 | 0 | 0
7 | 0.99211 | -0.14985 | 0.007131 | 0.0017872
8 | 0.98092 | -0.36572 | 0 | 0
9 | 0.98058 | -0.37235 | 0 | 0
10 | 0.97969 | -0.38977 | 0.0093535 | 0.0023442
11 | 0.98013 | -0.38122 | 0.0065737 | 0.0016475
12 | 0.99502 | -0.094335 | 0 | 0
13 | 0.99678 | -0.060849 | 0.0019245 | 0.00048231
14 | 0.98522 | -0.28438 | 0 | 0
15 | 0.98534 | -0.28188 | 0.0043548 | 0.0010914
16 | 0.98475 | -0.29347 | 0 | 0
17 | 0.97848 | -0.41344 | 0 | 0
18 | 0.97833 | -0.41645 | 0 | 0
19 | 0.97916 | -0.40019 | 0.0072455 | 0.0018159
20 | 0.99454 | -0.1037 | 0.0077912 | 0.0019527
21 | 0.9842 | -0.30422 | 0.0049598 | 0.001243
22 | 0.97626 | -0.45714 | 0 | 0
23 | 0.97617 | -0.4589 | 0.0072055 | 0.0018059
24 | 0.9772 | -0.4385 | 0 | 0
25 | 0.97614 | -0.45947 | 0.007175 | 0.0017982
26 | 0.97891 | -0.40505 | 0 | 0
27 | 0.97669 | -0.44868 | 0.0093219 | 0.0023363
28 | 0.97683 | -0.44592 | 0 | 0
29 | 0.97676 | -0.4473 | 0.012135 | 0.0030414
30 | 0.97708 | -0.44099 | 0.011958 | 0.002997
31 | 0.98048 | -0.37434 | 0.0074109 | 0.0018573
32 | 0.99199 | -0.15218 | 0.0054035 | 0.0013542
33 | 0.99439 | -0.10662 | 0.0046726 | 0.0011711
34 | 0.99427 | -0.1089 | 0.0050683 | 0.0012702
35 | 0.99817 | -0.034641 | 0.0018633 | 0.00046698
36 | 0.98587 | -0.27168 | 0.0030571 | 0.00076618
37 | 1 | 0 | -0.2982 | -0.07602
38 | 0.99958 | -0.0079897 | 0.0018724 | 0.00046927
39 | 0.97772 | -0.42837 | 0.012406 | 0.0031092
40 | 0.98404 | -0.30739 | 0.0040442 | 0.0010136
41 | 0.98717 | -0.24634 | 0.0082383 | 0.0020647
42 | 0.98731 | -0.24368 | 0.0094091 | 0.0023581
43 | 0.97599 | -0.46239 | 0.0071914 | 0.0018023
44 | 0.97598 | -0.46265 | 0 | 0
45 | 0.9758 | -0.46602 | 0.012114 | 0.0030361
46 | 0.97613 | -0.45968 | 0.009024 | 0.0022616
47 | 0.98759 | -0.23821 | 0.002945 | 0.00073808
48 | 0.98728 | -0.24413 | 0 | 0
49 | 0.98804 | -0.22947 | 0 | 0
50 | 0.98683 | -0.25297 | 0 | 0
51 | 0.98681 | -0.25329 | 0.0032146 | 0.00080565
52 | 0.98686 | -0.25244 | 0 | 0
53 | 0.98602 | -0.26869 | 0.0017661 | 0.00044263
54 | 0.98608 | -0.2676 | 0.0008088 | 0.00020271
55 | 0.99884 | -0.022008 | 0 | 0
56 | 0.99526 | -0.090138 | 0 | 0
57 | 0.99417 | -0.1111 | 0 | 0
58 | 0.99117 | -0.16877 | 0.0085073 | 0.0021321
59 | 0.99423 | -0.10965 | 0.0027762 | 0.00069578
60 | 0.98655 | -0.25839 | 0.0075408 | 0.0018899
61 | 0.98718 | -0.24615 | 0.01064 | 0.0026667
62 | 0.98843 | -0.22191 | 0.0025736 | 0.00064501
63 | 0.98397 | -0.30861 | 0.0034374 | 0.00086149
64 | 0.98397 | -0.30872 | 0.0033637 | 0.00084303
65 | 0.98957 | -0.19973 | 0 | 0
66 | 0.98892 | -0.2124 | 0.0021106 | 0.00052896
67 | 0.9875 | -0.23989 | 0.0068615 | 0.0017196
68 | 0.9876 | -0.23811 | 0 | 0
69 | 0.98819 | -0.22655 | 0.006251 | 0.0015667
70 | 0.98703 | -0.24915 | 0.00069974 | 0.00017537
71 | 0.98679 | -0.25368 | 0.007744 | 0.0019408
72 | 0.98643 | -0.26082 | 0.0017517 | 0.00043901
73 | 0.98634 | -0.26259 | 0.0087227 | 0.0021861
74 | 0.98624 | -0.26452 | 0.0007513 | 0.00018829
75 | 0.98613 | -0.26662 | 0 | 0
76 | 0.98703 | -0.24915 | 0.0015246 | 0.00038209
77 | 0.98611 | -0.26694 | 0.00055543 | 0.0001392
78 | 0.98607 | -0.26777 | 0.0017633 | 0.00044191
79 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.13681 | -0.034586 | 0.13725 | 0.03487 | 0.00044419 | 0.00028393 | 0.20694 | 0.20694 | 0.20694 | 0.98425 | -0.30097 | 0.98774 | -0.23351 | 56.8507
1 | 0.12653 | 0.03201 | -0.12628 | -0.031853 | 0.00024561 | 0.00015696 | 0.1914 | 0.1914 | 0.1914 | 0.98425 | -0.30097 | 0.98216 | -0.34151 | 52.5823
2 | -0.13725 | -0.03487 | 0.13786 | 0.035256 | 0.0006051 | 0.00038678 | 0.20694 | 0.20694 | 0.20694 | 0.98774 | -0.23351 | 0.9925 | -0.14237 | 56.8507
3 | 0.057161 | 0.014405 | -0.057108 | -0.014372 | 5.29e-05 | 3.3618e-05 | 0.08663 | 0.08663 | 0.08663 | 0.98216 | -0.34151 | 0.98117 | -0.36087 | 23.7995
4 | 0.069124 | 0.017448 | -0.069024 | -0.017384 | 9.9609e-05 | 6.3444e-05 | 0.10477 | 0.10477 | 0.10477 | 0.98216 | -0.34151 | 0.98062 | -0.37164 | 28.7829
5 | -0.1504 | -0.0384 | 0.15077 | 0.038639 | 0.00037456 | 0.0002387 | 0.22574 | 0.22574 | 0.22574 | 0.9925 | -0.14237 | 0.9952 | -0.090975 | 31.0078
6 | 0.01254 | 0.0031439 | -0.012535 | -0.0031415 | 4.4708e-06 | 2.4256e-06 | 0.018801 | 0.018801 | 0.018801 | 0.9925 | -0.14237 | 0.99211 | -0.14985 | 5.1651
7 | 0.050475 | 0.012709 | -0.050463 | -0.012702 | 1.1694e-05 | 7.417e-06 | 0.076569 | 0.07657 | 0.07657 | 0.98117 | -0.36087 | 0.98092 | -0.36572 | 21.0356
8 | 0.0074119 | 0.0018577 | -0.0074116 | -0.0018576 | 2.5188e-07 | 9.4219e-08 | 0.011247 | 0.011247 | 0.011247 | 0.98062 | -0.37164 | 0.98058 | -0.37235 | 3.0898
9 | 0.061612 | 0.015527 | -0.061559 | -0.015493 | 5.3376e-05 | 3.3955e-05 | 0.093523 | 0.093523 | 0.093523 | 0.98062 | -0.37164 | 0.97969 | -0.38977 | 25.693
10 | 0.020323 | 0.0050983 | -0.02032 | -0.0050963 | 3.2539e-06 | 1.9605e-06 | 0.030389 | 0.030389 | 0.030389 | 0.9952 | -0.090975 | 0.99502 | -0.094335 | 8.3487
11 | -0.17109 | -0.043737 | 0.17134 | 0.043896 | 0.00024974 | 0.00015865 | 0.25613 | 0.25612 | 0.25613 | 0.9952 | -0.090975 | 0.99678 | -0.060849 | 23.4547
12 | 0.0054041 | 0.0013543 | -0.0054035 | -0.0013542 | 5.9972e-07 | 6.9517e-08 | 0.0081053 | 0.0081054 | 0.0081054 | 0.99211 | -0.14985 | 0.99199 | -0.15218 | 2.2268
13 | 0.050463 | 0.012702 | -0.050426 | -0.012678 | 3.736e-05 | 2.3696e-05 | 0.07657 | 0.07657 | 0.07657 | 0.98092 | -0.36572 | 0.98013 | -0.38122 | 21.0356
14 | 0.0074116 | 0.0018576 | -0.0074109 | -0.0018573 | 7.0184e-07 | 2.6256e-07 | 0.011247 | 0.011247 | 0.011247 | 0.98058 | -0.37235 | 0.98048 | -0.37434 | 3.0899
15 | 0.052205 | 0.013149 | -0.052167 | -0.013124 | 3.8112e-05 | 2.4189e-05 | 0.079316 | 0.079316 | 0.079316 | 0.97969 | -0.38977 | 0.97891 | -0.40505 | 21.7901
16 | 0.043852 | 0.01103 | -0.043812 | -0.011005 | 3.9703e-05 | 2.5109e-05 | 0.06659 | 0.06659 | 0.06659 | 0.98013 | -0.38122 | 0.97916 | -0.40019 | 18.2939
17 | 0.02032 | 0.0050963 | -0.020311 | -0.0050909 | 9.0689e-06 | 5.4641e-06 | 0.030389 | 0.030389 | 0.030389 | 0.99502 | -0.094335 | 0.99454 | -0.1037 | 8.3487
18 | -0.17327 | -0.044378 | 0.17349 | 0.044518 | 0.00022031 | 0.00013997 | 0.259 | 0.259 | 0.259 | 0.99678 | -0.060849 | 0.99817 | -0.034641 | 23.7177
19 | -0.015822 | -0.0039708 | 0.015824 | 0.0039719 | 1.8913e-06 | 1.0979e-06 | 0.023899 | 0.023899 | 0.023899 | 0.98522 | -0.28438 | 0.98534 | -0.28188 | 6.5656
20 | 0.015822 | 0.0039708 | -0.015815 | -0.0039668 | 6.8502e-06 | 3.977e-06 | 0.023899 | 0.023899 | 0.023899 | 0.98522 | -0.28438 | 0.98475 | -0.29347 | 6.5656
21 | -0.020179 | -0.0050633 | 0.020189 | 0.0050692 | 9.8121e-06 | 5.9207e-06 | 0.030475 | 0.030475 | 0.030475 | 0.98534 | -0.28188 | 0.98587 | -0.27168 | 8.3723
22 | 0.015815 | 0.0039668 | -0.015807 | -0.0039621 | 8.1044e-06 | 4.7057e-06 | 0.023899 | 0.023899 | 0.023899 | 0.98475 | -0.29347 | 0.9842 | -0.30422 | 6.5657
23 | 0.036544 | 0.0091749 | -0.036538 | -0.0091716 | 5.2544e-06 | 3.3058e-06 | 0.055579 | 0.055579 | 0.055579 | 0.97848 | -0.41344 | 0.97833 | -0.41645 | 15.2689
24 | -0.036544 | -0.0091749 | 0.036567 | 0.0091894 | 2.3105e-05 | 1.4537e-05 | 0.055579 | 0.055579 | 0.055579 | 0.97848 | -0.41344 | 0.97916 | -0.40019 | 15.2689
25 | 0.036538 | 0.0091716 | -0.036517 | -0.0091585 | 2.0755e-05 | 1.3058e-05 | 0.055579 | 0.055579 | 0.055579 | 0.97833 | -0.41645 | 0.97772 | -0.42837 | 15.2689
26 | 0.01252 | 0.0031382 | -0.012518 | -0.0031373 | 1.7418e-06 | 9.4299e-07 | 0.018732 | 0.018732 | 0.018732 | 0.99454 | -0.1037 | 0.99439 | -0.10662 | 5.1462
27 | 0.010847 | 0.0027191 | -0.010846 | -0.0027182 | 1.635e-06 | 8.4046e-07 | 0.0164 | 0.0164 | 0.0164 | 0.9842 | -0.30422 | 0.98404 | -0.30739 | 4.5056
28 | 0.0072061 | 0.0018061 | -0.0072055 | -0.0018059 | 6.0435e-07 | 2.1977e-07 | 0.010984 | 0.010984 | 0.010984 | 0.97626 | -0.45714 | 0.97617 | -0.4589 | 3.0175
29 | -0.021575 | -0.0054079 | 0.021594 | 0.0054196 | 1.9179e-05 | 1.1683e-05 | 0.032885 | 0.032885 | 0.032885 | 0.97626 | -0.45714 | 0.9772 | -0.4385 | 9.0344
30 | 0.014369 | 0.0036018 | -0.014367 | -0.0036009 | 1.5978e-06 | 9.1157e-07 | 0.021902 | 0.021902 | 0.021902 | 0.97626 | -0.45714 | 0.97614 | -0.45947 | 6.0169
31 | -0.052084 | -0.013072 | 0.052167 | 0.013124 | 8.323e-05 | 5.2824e-05 | 0.079316 | 0.079316 | 0.079316 | 0.9772 | -0.4385 | 0.97891 | -0.40505 | 21.7902
32 | 0.03049 | 0.007652 | -0.030475 | -0.0076428 | 1.4798e-05 | 9.2417e-06 | 0.046431 | 0.046431 | 0.046431 | 0.9772 | -0.4385 | 0.97669 | -0.44868 | 12.7559
33 | 0.0071924 | 0.0018027 | -0.0071914 | -0.0018023 | 1.0005e-06 | 3.6291e-07 | 0.010964 | 0.010964 | 0.010964 | 0.97614 | -0.45947 | 0.97599 | -0.46239 | 3.0121
34 | 0.021153 | 0.0053065 | -0.021142 | -0.0052997 | 1.1093e-05 | 6.7433e-06 | 0.032229 | 0.032229 | 0.032229 | 0.97669 | -0.44868 | 0.97613 | -0.45968 | 8.8542
35 | 0.012136 | 0.0030418 | -0.012135 | -0.0030414 | 7.9671e-07 | 4.3208e-07 | 0.018487 | 0.018487 | 0.018487 | 0.97683 | -0.44592 | 0.97676 | -0.4473 | 5.0789
36 | -0.012136 | -0.0030418 | 0.012139 | 0.0030434 | 2.8472e-06 | 1.544e-06 | 0.018487 | 0.018487 | 0.018487 | 0.97683 | -0.44592 | 0.97708 | -0.44099 | 5.0789
37 | -0.024097 | -0.0060404 | 0.024112 | 0.0060493 | 1.4503e-05 | 8.9219e-06 | 0.036699 | 0.036698 | 0.036699 | 0.97708 | -0.44099 | 0.97772 | -0.42837 | 10.082
38 | 0.0078454 | 0.0019662 | -0.0078446 | -0.0019659 | 8.4978e-07 | 3.306e-07 | 0.01174 | 0.01174 | 0.01174 | 0.99439 | -0.10662 | 0.99427 | -0.1089 | 3.2253
39 | 0.0027763 | 0.00069564 | -0.0027762 | -0.00069578 | 9.9187e-08 | -1.3522e-07 | 0.0041549 | 0.004155 | 0.004155 | 0.99427 | -0.1089 | 0.99423 | -0.10965 | 1.1415
40 | -0.17535 | -0.044985 | 0.17546 | 0.045054 | 0.00010753 | 6.8329e-05 | 0.26177 | 0.26177 | 0.26177 | 0.99817 | -0.034641 | 0.99884 | -0.022008 | 23.972
41 | -0.023246 | -0.0058354 | 0.023261 | 0.0058444 | 1.4754e-05 | 9.0346e-06 | 0.035089 | 0.035089 | 0.035089 | 0.98587 | -0.27168 | 0.98655 | -0.25839 | 9.6399
42 | 0.29655 | 0.07602 | -0.29643 | -0.075947 | 0.00011482 | 7.3301e-05 | 0.44187 | 0.44187 | 0.44187 | 1 | 0 | 0.99958 | -0.0079897 | 40.4641
43 | 0.29456 | 0.075477 | -0.29436 | -0.07535 | 0.00019998 | 0.00012766 | 0.43908 | 0.43908 | 0.43908 | 0.99958 | -0.0079897 | 0.99884 | -0.022008 | 40.2089
44 | 0.0068015 | 0.0017046 | -0.0068011 | -0.0017045 | 3.9547e-07 | 1.2646e-07 | 0.010285 | 0.010285 | 0.010285 | 0.98404 | -0.30739 | 0.98397 | -0.30861 | 2.8256
45 | -0.0082383 | -0.0020647 | 0.0082394 | 0.0020652 | 1.0427e-06 | 4.3678e-07 | 0.012418 | 0.012418 | 0.012418 | 0.98717 | -0.24634 | 0.98731 | -0.24368 | 3.4116
46 | -0.017648 | -0.0044233 | 0.017653 | 0.0044261 | 4.689e-06 | 2.7749e-06 | 0.026599 | 0.026599 | 0.026599 | 0.98731 | -0.24368 | 0.9876 | -0.23811 | 7.3074
47 | 0.012116 | 0.0030372 | -0.012114 | -0.0030361 | 1.9464e-06 | 1.0557e-06 | 0.018473 | 0.018473 | 0.018473 | 0.97598 | -0.46265 | 0.9758 | -0.46602 | 5.075
48 | -0.012116 | -0.0030372 | 0.012118 | 0.0030381 | 1.7104e-06 | 9.2761e-07 | 0.018473 | 0.018473 | 0.018473 | 0.97598 | -0.46265 | 0.97613 | -0.45968 | 5.075
49 | 0.029331 | 0.0073581 | -0.029323 | -0.007353 | 8.2706e-06 | 5.1488e-06 | 0.044196 | 0.044196 | 0.044196 | 0.98759 | -0.23821 | 0.98728 | -0.24413 | 12.1419
50 | -0.032276 | -0.0080962 | 0.03229 | 0.0081046 | 1.3457e-05 | 8.4182e-06 | 0.048634 | 0.048634 | 0.048634 | 0.98759 | -0.23821 | 0.98804 | -0.22947 | 13.3609
51 | 0.0022248 | 0.00055619 | -0.0022243 | -0.00055747 | 5.3165e-07 | -1.2719e-06 | 0.0033528 | 0.0033533 | 0.0033533 | 0.98728 | -0.24413 | 0.98703 | -0.24915 | 0.92124
52 | 0.027098 | 0.0067968 | -0.027087 | -0.0067901 | 1.0739e-05 | 6.6537e-06 | 0.040844 | 0.040844 | 0.040844 | 0.98728 | -0.24413 | 0.98686 | -0.25244 | 11.2208
53 | -0.073782 | -0.018538 | 0.073809 | 0.018555 | 2.6619e-05 | 1.6962e-05 | 0.11113 | 0.11113 | 0.11113 | 0.98804 | -0.22947 | 0.98843 | -0.22191 | 30.5316
54 | 0.041493 | 0.010433 | -0.04146 | -0.010412 | 3.3023e-05 | 2.0846e-05 | 0.062501 | 0.062502 | 0.062502 | 0.98804 | -0.22947 | 0.98718 | -0.24615 | 17.1707
55 | 0.0032146 | 0.00080562 | -0.0032146 | -0.00080565 | 4.8351e-08 | -3.9163e-08 | 0.0048473 | 0.0048473 | 0.0048473 | 0.98683 | -0.25297 | 0.98681 | -0.25329 | 1.3317
56 | -0.0032146 | -0.00080562 | 0.0032147 | 0.00080555 | 8.0585e-08 | -6.5278e-08 | 0.0048473 | 0.0048472 | 0.0048473 | 0.98683 | -0.25297 | 0.98686 | -0.25244 | 1.3317
57 | 0.023873 | 0.0059846 | -0.023871 | -0.0059837 | 1.4099e-06 | 8.6524e-07 | 0.035997 | 0.035997 | 0.035997 | 0.98686 | -0.25244 | 0.98679 | -0.25368 | 9.8892
58 | -0.0017661 | -0.00044263 | 0.0017662 | 0.00044225 | 9.2078e-08 | -3.8201e-07 | 0.0026653 | 0.0026651 | 0.0026653 | 0.98602 | -0.26869 | 0.98608 | -0.2676 | 0.73221
59 | -0.002575 | -0.00064495 | 0.0025751 | 0.00064476 | 1.2014e-07 | -1.9382e-07 | 0.0038856 | 0.0038855 | 0.0038856 | 0.98608 | -0.2676 | 0.98613 | -0.26662 | 1.0675
60 | 0.1189 | 0.030296 | -0.11851 | -0.030047 | 0.00038948 | 0.00024883 | 0.17731 | 0.17731 | 0.17731 | 0.99884 | -0.022008 | 0.99526 | -0.090138 | 48.7107
61 | 0.11851 | 0.030047 | -0.11839 | -0.029971 | 0.00011926 | 7.6194e-05 | 0.17731 | 0.17731 | 0.17731 | 0.99526 | -0.090138 | 0.99417 | -0.1111 | 48.7107
62 | 0.11839 | 0.029971 | -0.11806 | -0.029762 | 0.00032683 | 0.00020881 | 0.17731 | 0.17731 | 0.17731 | 0.99417 | -0.1111 | 0.99117 | -0.16877 | 48.7107
63 | 0.10956 | 0.02763 | -0.10939 | -0.027527 | 0.0001621 | 0.00010354 | 0.16454 | 0.16454 | 0.16454 | 0.99117 | -0.16877 | 0.98957 | -0.19973 | 45.202
64 | -0.030801 | -0.0077343 | 0.030819 | 0.0077456 | 1.7997e-05 | 1.1234e-05 | 0.046463 | 0.046463 | 0.046463 | 0.98655 | -0.25839 | 0.98718 | -0.24615 | 12.7645
65 | -0.076383 | -0.0192 | 0.076464 | 0.019251 | 8.0981e-05 | 5.1618e-05 | 0.11501 | 0.11501 | 0.11501 | 0.98843 | -0.22191 | 0.98957 | -0.19973 | 31.596
66 | 0.0033637 | 0.00084302 | -0.0033637 | -0.00084303 | 1.7574e-08 | -1.1758e-08 | 0.0050868 | 0.0050868 | 0.0050868 | 0.98397 | -0.30861 | 0.98397 | -0.30872 | 1.3975
67 | 0.032931 | 0.0082752 | -0.032911 | -0.0082628 | 1.9897e-05 | 1.2456e-05 | 0.049526 | 0.049526 | 0.049526 | 0.98957 | -0.19973 | 0.98892 | -0.2124 | 13.6061
68 | 0.0308 | 0.0077338 | -0.03078 | -0.0077209 | 2.0779e-05 | 1.2968e-05 | 0.04635 | 0.04635 | 0.04635 | 0.98892 | -0.2124 | 0.98819 | -0.22655 | 12.7336
69 | -0.0068615 | -0.0017196 | 0.0068621 | 0.0017198 | 5.8417e-07 | 1.8742e-07 | 0.010339 | 0.010339 | 0.010339 | 0.9875 | -0.23989 | 0.9876 | -0.23811 | 2.8404
70 | -0.024515 | -0.0061459 | 0.024529 | 0.0061542 | 1.3509e-05 | 8.3078e-06 | 0.036938 | 0.036938 | 0.036938 | 0.9876 | -0.23811 | 0.98819 | -0.22655 | 10.1477
71 | 0.0015246 | 0.00038209 | -0.0015246 | -0.00038209 | 1.4388e-10 | -8.4033e-10 | 0.0022984 | 0.0022984 | 0.0022984 | 0.98703 | -0.24915 | 0.98703 | -0.24915 | 0.63143
72 | 0.016127 | 0.0040429 | -0.016122 | -0.0040397 | 5.4845e-06 | 3.1943e-06 | 0.024319 | 0.024319 | 0.024319 | 0.98679 | -0.25368 | 0.98643 | -0.26082 | 6.6811
73 | 0.01437 | 0.0036007 | -0.014369 | -0.0036 | 1.209e-06 | 6.8618e-07 | 0.021677 | 0.021677 | 0.021677 | 0.98643 | -0.26082 | 0.98634 | -0.26259 | 5.9552
74 | 0.0056462 | 0.0014139 | -0.0056457 | -0.0014138 | 5.1887e-07 | 8.8687e-08 | 0.0085176 | 0.0085177 | 0.0085177 | 0.98634 | -0.26259 | 0.98624 | -0.26452 | 2.34
75 | 0.0048944 | 0.0012255 | -0.0048939 | -0.0012255 | 4.8821e-07 | 7.8111e-09 | 0.0073842 | 0.0073843 | 0.0073843 | 0.98624 | -0.26452 | 0.98613 | -0.26662 | 2.0286
76 | 0.0023188 | 0.00058075 | -0.0023187 | -0.00058083 | 3.6337e-08 | -7.7728e-08 | 0.0034988 | 0.0034988 | 0.0034988 | 0.98613 | -0.26662 | 0.98611 | -0.26694 | 0.96121
77 | 0.0017633 | 0.00044162 | -0.0017633 | -0.00044191 | 6.9435e-08 | -2.892e-07 | 0.0026607 | 0.0026608 | 0.0026608 | 0.98611 | -0.26694 | 0.98607 | -0.26777 | 0.73099

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.30124 | 0.076783

## res_load
| p_mw | q_mvar
0 | 0.010277 | 0.0025757
1 | 0.0066338 | 0.0016626
2 | 0.007131 | 0.0017872
3 | 0.0093535 | 0.0023442
4 | 0.0065737 | 0.0016475
5 | 0.0019245 | 0.00048231
6 | 0.0043548 | 0.0010914
7 | 0.0072455 | 0.0018159
8 | 0.0077912 | 0.0019527
9 | 0.0049598 | 0.001243
10 | 0.0072055 | 0.0018059
11 | 0.007175 | 0.0017982
12 | 0.0093219 | 0.0023363
13 | 0.012135 | 0.0030414
14 | 0.011958 | 0.002997
15 | 0.0074109 | 0.0018573
16 | 0.0054035 | 0.0013542
17 | 0.0046726 | 0.0011711
18 | 0.0050683 | 0.0012702
19 | 0.0018633 | 0.00046698
20 | 0.0030571 | 0.00076618
21 | 0.003045 | 0.00076314
22 | 0.0018724 | 0.00046927
23 | 0.012406 | 0.0031092
24 | 0.0040442 | 0.0010136
25 | 0.0082383 | 0.0020647
26 | 0.0094091 | 0.0023581
27 | 0.0071914 | 0.0018023
28 | 0.012114 | 0.0030361
29 | 0.009024 | 0.0022616
30 | 0.002945 | 0.00073808
31 | 0.0032146 | 0.00080565
32 | 0.0017661 | 0.00044263
33 | 0.0008088 | 0.00020271
34 | 0.0085073 | 0.0021321
35 | 0.0027762 | 0.00069578
36 | 0.0075408 | 0.0018899
37 | 0.01064 | 0.0026667
38 | 0.0025736 | 0.00064501
39 | 0.0034374 | 0.00086149
40 | 0.0033637 | 0.00084303
41 | 0.0021106 | 0.00052896
42 | 0.0068615 | 0.0017196
43 | 0.006251 | 0.0015667
44 | 0.00069974 | 0.00017537
45 | 0.007744 | 0.0019408
46 | 0.0017517 | 0.00043901
47 | 0.0087227 | 0.0021861
48 | 0.0007513 | 0.00018829
49 | 0.0015246 | 0.00038209
50 | 0.00055543 | 0.0001392
51 | 0.0017633 | 0.00044191

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1