## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-168_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-168_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-168_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-168_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-168_0_6_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_261-168_0_6_node_25 | 0.4 | n |  | TRUE
6 | bus_LV_261-168_0_6_node_60 | 0.4 | n |  | TRUE
7 | bus_LV_261-168_0_6_node_59 | 0.4 | n |  | TRUE
8 | bus_LV_261-168_0_6_node_13 | 0.4 | n |  | TRUE
9 | bus_LV_261-168_0_6_node_26 | 0.4 | n |  | TRUE
10 | bus_LV_261-168_0_6_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_261-168_0_6_node_15 | 0.4 | n |  | TRUE
12 | bus_LV_261-168_0_6_node_21 | 0.4 | n |  | TRUE
13 | bus_LV_261-168_0_6_node_133 | 0.4 | n |  | TRUE
14 | bus_LV_261-168_0_6_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_261-168_0_6_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_261-168_0_6_node_27 | 0.4 | n |  | TRUE
17 | bus_LV_261-168_0_6_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_261-168_0_6_node_70 | 0.4 | n |  | TRUE
19 | bus_LV_261-168_0_6_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_261-168_0_6_node_66 | 0.4 | n |  | TRUE
21 | bus_LV_261-168_0_6_node_28 | 0.4 | n |  | TRUE
22 | bus_LV_261-168_0_6_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_261-168_0_6_node_71 | 0.4 | n |  | TRUE
24 | bus_LV_261-168_0_6_node_30 | 0.4 | n |  | TRUE
25 | bus_LV_261-168_0_6_node_128 | 0.4 | n |  | TRUE
26 | bus_LV_261-168_0_6_node_68 | 0.4 | n |  | TRUE
27 | bus_LV_261-168_0_6_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_261-168_0_6_node_69 | 0.4 | n |  | TRUE
29 | bus_LV_261-168_0_6_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_261-168_0_6_node_40 | 0.4 | n |  | TRUE
31 | bus_LV_261-168_0_6_node_36 | 0.4 | n |  | TRUE
32 | bus_LV_261-168_0_6_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_261-168_0_6_node_117 | 0.4 | n |  | TRUE
34 | bus_LV_261-168_0_6_node_116 | 0.4 | n |  | TRUE
35 | bus_LV_261-168_0_6_node_115 | 0.4 | n |  | TRUE
36 | bus_LV_261-168_0_6_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_261-168_0_6_node_63 | 0.4 | n |  | TRUE
38 | bus_LV_261-168_0_6_node_62 | 0.4 | n |  | TRUE
39 | bus_LV_261-168_0_6_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_261-168_0_6_node_61 | 0.4 | n |  | TRUE
41 | bus_LV_261-168_0_6_node_104 | 0.4 | n |  | TRUE
42 | bus_LV_261-168_0_6_node_102 | 0.4 | n |  | TRUE
43 | bus_LV_261-168_0_6_node_119 | 0.4 | n |  | TRUE
44 | bus_LV_261-168_0_6_node_118 | 0.4 | n |  | TRUE
45 | bus_LV_261-168_0_6_node_134 | 0.4 | n |  | TRUE
46 | bus_LV_261-168_0_6_node_64 | 0.4 | n |  | TRUE
47 | bus_LV_261-168_0_6_node_33 | 0.4 | n |  | TRUE
48 | bus_LV_261-168_0_6_node_31 | 0.4 | n |  | TRUE
49 | bus_LV_261-168_0_6_node_72 | 0.4 | n |  | TRUE
50 | bus_LV_261-168_0_6_node_29 | 0.4 | n |  | TRUE
51 | bus_LV_261-168_0_6_node_67 | 0.4 | n |  | TRUE
52 | bus_LV_261-168_0_6_node_51 | 0.4 | n |  | TRUE
53 | bus_LV_261-168_0_6_node_50 | 0.4 | n |  | TRUE
54 | bus_LV_261-168_0_6_node_35 | 0.4 | n |  | TRUE
55 | bus_LV_261-168_0_6_node_32 | 0.4 | n |  | TRUE
56 | bus_LV_261-168_0_6_node_34 | 0.4 | n |  | TRUE
57 | bus_LV_261-168_0_6_node_37 | 0.4 | n |  | TRUE
58 | bus_LV_261-168_0_6_node_38 | 0.4 | n |  | TRUE
59 | bus_LV_261-168_0_6_node_39 | 0.4 | n |  | TRUE
60 | bus_LV_261-168_0_6_node_54 | 0.4 | n |  | TRUE
61 | bus_LV_261-168_0_6_node_136 | 0.4 | n |  | TRUE
62 | bus_LV_261-168_0_6_node_49 | 0.4 | n |  | TRUE
63 | bus_LV_261-168_0_6_node_41 | 0.4 | n |  | TRUE
64 | bus_LV_261-168_0_6_node_42 | 0.4 | n |  | TRUE
65 | bus_LV_261-168_0_6_node_43 | 0.4 | n |  | TRUE
66 | bus_LV_261-168_0_6_node_44 | 0.4 | n |  | TRUE
67 | bus_LV_261-168_0_6_node_46 | 0.4 | n |  | TRUE
68 | bus_LV_261-168_0_6_node_47 | 0.4 | n |  | TRUE
69 | bus_LV_261-168_0_6_node_90 | 0.4 | n |  | TRUE
70 | bus_LV_261-168_0_6_node_45 | 0.4 | n |  | TRUE
71 | bus_LV_261-168_0_6_node_138 | 0.4 | n |  | TRUE
72 | bus_LV_261-168_0_6_node_48 | 0.4 | n |  | TRUE
73 | bus_LV_261-168_0_6_node_127 | 0.4 | n |  | TRUE
74 | bus_LV_261-168_0_6_node_94 | 0.4 | n |  | TRUE
75 | bus_LV_261-168_0_6_node_123 | 0.4 | n |  | TRUE
76 | bus_LV_261-168_0_6_node_124 | 0.4 | n |  | TRUE
77 | bus_LV_261-168_0_6_node_122 | 0.4 | n |  | TRUE
78 | bus_LV_261-168_0_6_node_126 | 0.4 | n |  | TRUE
79 | bus_LV_261-168_0_6_node_55 | 0.4 | n |  | TRUE
80 | bus_LV_261-168_0_6_node_52 | 0.4 | n |  | TRUE
81 | bus_LV_261-168_0_6_node_137 | 0.4 | n |  | TRUE
82 | bus_LV_261-168_0_6_node_53 | 0.4 | n |  | TRUE
83 | bus_LV_261-168_0_6_node_56 | 0.4 | n |  | TRUE
84 | bus_LV_261-168_0_6_node_57 | 0.4 | n |  | TRUE
85 | bus_LV_261-168_0_6_node_58 | 0.4 | n |  | TRUE
86 | bus_LV_261-168_0_6_node_74 | 0.4 | n |  | TRUE
87 | bus_LV_261-168_0_6_node_75 | 0.4 | n |  | TRUE
88 | bus_LV_261-168_0_6_node_65 | 0.4 | n |  | TRUE
89 | bus_LV_261-168_0_6_node_73 | 0.4 | n |  | TRUE
90 | bus_LV_261-168_0_6_node_88 | 0.4 | n |  | TRUE
91 | bus_LV_261-168_0_6_node_87 | 0.4 | n |  | TRUE
92 | bus_LV_261-168_0_6_node_76 | 0.4 | n |  | TRUE
93 | bus_LV_261-168_0_6_node_81 | 0.4 | n |  | TRUE
94 | bus_LV_261-168_0_6_node_79 | 0.4 | n |  | TRUE
95 | bus_LV_261-168_0_6_node_77 | 0.4 | n |  | TRUE
96 | bus_LV_261-168_0_6_node_78 | 0.4 | n |  | TRUE
97 | bus_LV_261-168_0_6_node_80 | 0.4 | n |  | TRUE
98 | bus_LV_261-168_0_6_node_86 | 0.4 | n |  | TRUE
99 | bus_LV_261-168_0_6_node_84 | 0.4 | n |  | TRUE
100 | bus_LV_261-168_0_6_node_82 | 0.4 | n |  | TRUE
101 | bus_LV_261-168_0_6_node_83 | 0.4 | n |  | TRUE
102 | bus_LV_261-168_0_6_node_85 | 0.4 | n |  | TRUE
103 | bus_LV_261-168_0_6_node_89 | 0.4 | n |  | TRUE
104 | bus_LV_261-168_0_6_node_132 | 0.4 | n |  | TRUE
105 | bus_LV_261-168_0_6_node_113 | 0.4 | n |  | TRUE
106 | bus_LV_261-168_0_6_node_91 | 0.4 | n |  | TRUE
107 | bus_LV_261-168_0_6_node_92 | 0.4 | n |  | TRUE
108 | bus_LV_261-168_0_6_node_129 | 0.4 | n |  | TRUE
109 | bus_LV_261-168_0_6_node_130 | 0.4 | n |  | TRUE
110 | bus_LV_261-168_0_6_node_135 | 0.4 | n |  | TRUE
111 | bus_LV_261-168_0_6_node_125 | 0.4 | n |  | TRUE
112 | bus_LV_261-168_0_6_node_131 | 0.4 | n |  | TRUE
113 | bus_LV_261-168_0_6_node_103 | 0.4 | n |  | TRUE
114 | bus_LV_261-168_0_6_node_96 | 0.4 | n |  | TRUE
115 | bus_LV_261-168_0_6_node_97 | 0.4 | n |  | TRUE
116 | bus_LV_261-168_0_6_node_98 | 0.4 | n |  | TRUE
117 | bus_LV_261-168_0_6_node_99 | 0.4 | n |  | TRUE
118 | bus_LV_261-168_0_6_node_100 | 0.4 | n |  | TRUE
119 | bus_LV_261-168_0_6_node_101 | 0.4 | n |  | TRUE
120 | bus_LV_261-168_0_6_node_105 | 0.4 | n |  | TRUE
121 | bus_LV_261-168_0_6_node_106 | 0.4 | n |  | TRUE
122 | bus_LV_261-168_0_6_node_107 | 0.4 | n |  | TRUE
123 | bus_LV_261-168_0_6_node_108 | 0.4 | n |  | TRUE
124 | bus_LV_261-168_0_6_node_109 | 0.4 | n |  | TRUE
125 | bus_LV_261-168_0_6_node_114 | 0.4 | n |  | TRUE
126 | bus_LV_261-168_0_6_node_111 | 0.4 | n |  | TRUE
127 | bus_LV_261-168_0_6_node_121 | 0.4 | n |  | TRUE
128 | bus_LV_261-168_0_6_node_110 | 0.4 | n |  | TRUE
129 | bus_LV_261-168_0_6_node_112 | 0.4 | n |  | TRUE
130 | bus_LV_261-168_0_6_node_120 | 0.4 | n |  | TRUE
131 | bus_MV_518_0_node_40 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-168_0_6_load_0 | 0 | 0.0047553 | 0.0011918 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-168_0_6_load_25 | 5 | 0.0044624 | 0.0011184 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-168_0_6_load_60 | 6 | 0.0392 | 0.0098245 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-168_0_6_load_59 | 7 | 0.0022656 | 0.00056781 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-168_0_6_load_26 | 9 | 0.0070245 | 0.0017605 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-168_0_6_load_133 | 13 | 0.019607 | 0.0049139 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-168_0_6_load_27 | 16 | 0.0080415 | 0.0020154 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-168_0_6_load_70 | 18 | 0.010018 | 0.0025108 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-168_0_6_load_66 | 20 | 0.0044579 | 0.0011173 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-168_0_6_load_28 | 21 | 0.0099703 | 0.0024988 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-168_0_6_load_71 | 23 | 0.015399 | 0.0038593 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-168_0_6_load_30 | 24 | 0.0042166 | 0.0010568 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-168_0_6_load_128 | 25 | 0.0042937 | 0.0010761 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-168_0_6_load_68 | 26 | 0.007881 | 0.0019752 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-168_0_6_load_69 | 28 | 0.0079776 | 0.0019994 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-168_0_6_load_36 | 31 | 0.0043261 | 0.0010842 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-168_0_6_load_117 | 33 | 0.0073479 | 0.0018415 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-168_0_6_load_116 | 34 | 0.0070141 | 0.0017579 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-168_0_6_load_115 | 35 | 0.0075021 | 0.0018802 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-168_0_6_load_63 | 37 | 0.007825 | 0.0019611 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-168_0_6_load_62 | 38 | 0.0033773 | 0.00084642 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-168_0_6_load_61 | 40 | 0.004421 | 0.001108 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-168_0_6_load_104 | 41 | 0.0059909 | 0.0015015 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-168_0_6_load_119 | 43 | 0.0020531 | 0.00051456 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-168_0_6_load_118 | 44 | 0.01306 | 0.0032733 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-168_0_6_load_134 | 45 | 0.0080341 | 0.0020135 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-168_0_6_load_64 | 46 | 0.0051932 | 0.0013015 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-168_0_6_load_33 | 47 | 0.0052427 | 0.0013139 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-168_0_6_load_72 | 49 | 0.0060415 | 0.0015141 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-168_0_6_load_29 | 50 | 0.0038879 | 0.0009744 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-168_0_6_load_67 | 51 | 0.0047121 | 0.001181 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-168_0_6_load_50 | 53 | 0.002128 | 0.00053333 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-168_0_6_load_35 | 54 | 0.0065215 | 0.0016344 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-168_0_6_load_32 | 55 | 0.0038667 | 0.00096908 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-168_0_6_load_34 | 56 | 0.014827 | 0.0037159 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-168_0_6_load_38 | 58 | 0.0060821 | 0.0015243 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-168_0_6_load_39 | 59 | 0.0060855 | 0.0015252 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-168_0_6_load_136 | 61 | 0.0033169 | 0.00083129 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-168_0_6_load_41 | 63 | 0.0058039 | 0.0014546 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-168_0_6_load_46 | 67 | 0.0045354 | 0.0011367 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-168_0_6_load_47 | 68 | 0.004636 | 0.0011619 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-168_0_6_load_90 | 69 | 0.0078896 | 0.0019773 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-168_0_6_load_138 | 71 | 0.036603 | 0.0091737 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-168_0_6_load_48 | 72 | 0.0043766 | 0.0010969 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-168_0_6_load_127 | 73 | 0.005066 | 0.0012697 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-168_0_6_load_123 | 75 | 0.0044179 | 0.0011072 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-168_0_6_load_124 | 76 | 0.0044925 | 0.0011259 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-168_0_6_load_122 | 77 | 0.0037438 | 0.00093829 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-168_0_6_load_55 | 79 | 0.0021367 | 0.00053551 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-168_0_6_load_52 | 80 | 0.0020068 | 0.00050294 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-168_0_6_load_137 | 81 | 0.0032018 | 0.00080245 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-168_0_6_load_53 | 82 | 0.0019066 | 0.00047785 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-168_0_6_load_56 | 83 | 0.0024653 | 0.00061786 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-168_0_6_load_57 | 84 | 0.0011969 | 0.00029998 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-168_0_6_load_58 | 85 | 0.00119 | 0.00029825 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-168_0_6_load_74 | 86 | 0.0015965 | 0.00040011 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-168_0_6_load_75 | 87 | 0.0012797 | 0.00032073 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-168_0_6_load_65 | 88 | 0.004646 | 0.0011644 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-168_0_6_load_73 | 89 | 0.0017775 | 0.00044549 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-168_0_6_load_88 | 90 | 0.0019448 | 0.00048741 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-168_0_6_load_76 | 92 | 0.0013743 | 0.00034444 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-168_0_6_load_81 | 93 | 0.0017642 | 0.00044214 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-168_0_6_load_79 | 94 | 0.0018157 | 0.00045505 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-168_0_6_load_77 | 95 | 0.0019963 | 0.00050031 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-168_0_6_load_78 | 96 | 0.0018011 | 0.00045141 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-168_0_6_load_80 | 97 | 0.0019369 | 0.00048544 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-168_0_6_load_86 | 98 | 0.0024556 | 0.00061543 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-168_0_6_load_84 | 99 | 0.0017615 | 0.00044147 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-168_0_6_load_82 | 100 | 0.0019688 | 0.00049344 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-168_0_6_load_83 | 101 | 0.0022874 | 0.00057328 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-168_0_6_load_85 | 102 | 0.002258 | 0.00056592 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-168_0_6_load_89 | 103 | 0.0023172 | 0.00058074 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-168_0_6_load_132 | 104 | 0.0019338 | 0.00048465 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-168_0_6_load_113 | 105 | 0.0023278 | 0.00058341 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-168_0_6_load_91 | 106 | 0.0077139 | 0.0019333 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-168_0_6_load_129 | 108 | 0.0080121 | 0.002008 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-168_0_6_load_130 | 109 | 0.0069387 | 0.001739 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-168_0_6_load_135 | 110 | 0.0052529 | 0.0013165 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-168_0_6_load_125 | 111 | 0.0053978 | 0.0013528 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-168_0_6_load_131 | 112 | 0.0063925 | 0.0016021 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-168_0_6_load_96 | 114 | 0.0061552 | 0.0015426 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-168_0_6_load_97 | 115 | 0.005104 | 0.0012792 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_261-168_0_6_load_98 | 116 | 0.005432 | 0.0013614 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_261-168_0_6_load_99 | 117 | 0.0070944 | 0.001778 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_261-168_0_6_load_100 | 118 | 0.0058037 | 0.0014545 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_261-168_0_6_load_105 | 120 | 0.0019496 | 0.00048862 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_261-168_0_6_load_106 | 121 | 0.0024427 | 0.00061221 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_261-168_0_6_load_107 | 122 | 0.0019241 | 0.00048222 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_261-168_0_6_load_108 | 123 | 0.0015352 | 0.00038475 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_261-168_0_6_load_109 | 124 | 0.0020137 | 0.00050469 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_261-168_0_6_load_114 | 125 | 0.0024007 | 0.00060166 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_261-168_0_6_load_111 | 126 | 0.0017202 | 0.00043113 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_261-168_0_6_load_121 | 127 | 0.0014927 | 0.0003741 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_261-168_0_6_load_110 | 128 | 0.0018383 | 0.00046073 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_261-168_0_6_load_112 | 129 | 0.0019693 | 0.00049356 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_261-168_0_6_load_120 | 130 | 0.0016546 | 0.00041467 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 98 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-168_0_6_line_0 |  | 0 | 1 | 0.027719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-168_0_6_line_1 |  | 0 | 2 | 0.011657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-168_0_6_line_2 |  | 1 | 3 | 0.004732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-168_0_6_line_3 |  | 2 | 4 | 0.004358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-168_0_6_line_4 |  | 2 | 5 | 0.016672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-168_0_6_line_5 |  | 3 | 6 | 0.046289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-168_0_6_line_6 |  | 3 | 7 | 0.070634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-168_0_6_line_7 |  | 4 | 8 | 0.018711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-168_0_6_line_8 |  | 4 | 9 | 0.019718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-168_0_6_line_9 |  | 5 | 19 | 0.0015692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-168_0_6_line_10 |  | 8 | 21 | 0.0012741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-168_0_6_line_11 |  | 8 | 16 | 0.018076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-168_0_6_line_12 |  | 10 | 11 | 0.024195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-168_0_6_line_13 |  | 10 | 12 | 0.007974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-168_0_6_line_14 |  | 10 | 13 | 0.021709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-168_0_6_line_15 |  | 11 | 22 | 0.023917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_261-168_0_6_line_16 |  | 11 | 23 | 0.040047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_261-168_0_6_line_17 |  | 11 | 17 | 0.022606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-168_0_6_line_18 |  | 12 | 32 | 0.0463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-168_0_6_line_19 |  | 12 | 33 | 0.01597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-168_0_6_line_20 |  | 13 | 45 | 0.022638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-168_0_6_line_21 |  | 14 | 15 | 0.018454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-168_0_6_line_22 |  | 14 | 16 | 0.039361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-168_0_6_line_23 |  | 15 | 24 | 0.0033495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-168_0_6_line_24 |  | 17 | 18 | 0.018452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-168_0_6_line_25 |  | 19 | 20 | 0.0069011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-168_0_6_line_26 |  | 20 | 46 | 0.02326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-168_0_6_line_27 |  | 21 | 27 | 0.01637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-168_0_6_line_28 |  | 22 | 25 | 0.017895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-168_0_6_line_29 |  | 22 | 26 | 0.012188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-168_0_6_line_30 |  | 23 | 49 | 0.0051904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_261-168_0_6_line_31 |  | 24 | 50 | 0.020637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-168_0_6_line_32 |  | 25 | 51 | 0.0092228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-168_0_6_line_33 |  | 26 | 37 | 0.017872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-168_0_6_line_34 |  | 27 | 28 | 0.014778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-168_0_6_line_35 |  | 29 | 30 | 0.046019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-168_0_6_line_36 |  | 29 | 31 | 0.015849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-168_0_6_line_37 |  | 30 | 52 | 0.002384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_261-168_0_6_line_38 |  | 30 | 53 | 0.014568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_261-168_0_6_line_39 |  | 31 | 54 | 5.8771e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-168_0_6_line_40 |  | 32 | 34 | 0.012385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-168_0_6_line_41 |  | 32 | 35 | 0.022812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-168_0_6_line_42 |  | 36 | 37 | 0.017023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-168_0_6_line_43 |  | 36 | 38 | 0.042725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-168_0_6_line_44 |  | 38 | 39 | 0.021938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-168_0_6_line_45 |  | 39 | 40 | 0.037888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-168_0_6_line_46 |  | 41 | 42 | 0.012115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-168_0_6_line_47 |  | 42 | 113 | 0.019133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-168_0_6_line_48 |  | 42 | 118 | 0.008417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-168_0_6_line_49 |  | 43 | 44 | 0.0060157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-168_0_6_line_50 |  | 44 | 130 | 0.012277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-168_0_6_line_51 |  | 46 | 88 | 0.0091788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-168_0_6_line_52 |  | 47 | 48 | 0.021372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-168_0_6_line_53 |  | 48 | 55 | 0.040717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-168_0_6_line_54 |  | 48 | 50 | 0.011498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-168_0_6_line_55 |  | 49 | 89 | 0.038479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
56 | LV_261-168_0_6_line_56 |  | 51 | 88 | 0.0087288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-168_0_6_line_57 |  | 52 | 60 | 0.01255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_261-168_0_6_line_58 |  | 52 | 61 | 0.015661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-168_0_6_line_59 |  | 53 | 62 | 0.038629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
60 | LV_261-168_0_6_line_60 |  | 54 | 57 | 0.016423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-168_0_6_line_61 |  | 55 | 56 | 0.015141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-168_0_6_line_62 |  | 57 | 58 | 0.005429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-168_0_6_line_63 |  | 57 | 59 | 0.014945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-168_0_6_line_64 |  | 60 | 79 | 0.0054512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_261-168_0_6_line_65 |  | 60 | 80 | 0.0073987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-168_0_6_line_66 |  | 61 | 81 | 0.025659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-168_0_6_line_67 |  | 62 | 72 | 0.014642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-168_0_6_line_68 |  | 62 | 70 | 0.020209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-168_0_6_line_69 |  | 63 | 64 | 0.048156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-168_0_6_line_70 |  | 63 | 65 | 0.016535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-168_0_6_line_71 |  | 64 | 66 | 0.00831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-168_0_6_line_72 |  | 65 | 67 | 0.006248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-168_0_6_line_73 |  | 65 | 68 | 0.0097802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-168_0_6_line_74 |  | 66 | 69 | 0.041813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-168_0_6_line_75 |  | 67 | 72 | 0.010857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-168_0_6_line_76 |  | 68 | 73 | 0.017065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-168_0_6_line_77 |  | 70 | 71 | 0.04639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-168_0_6_line_78 |  | 73 | 78 | 0.014917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-168_0_6_line_79 |  | 74 | 75 | 0.016386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-168_0_6_line_80 |  | 74 | 76 | 0.015777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_261-168_0_6_line_81 |  | 74 | 77 | 0.029592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-168_0_6_line_82 |  | 75 | 112 | 0.021974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_261-168_0_6_line_83 |  | 77 | 113 | 0.013591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_261-168_0_6_line_84 |  | 78 | 111 | 0.010838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_261-168_0_6_line_85 |  | 78 | 107 | 0.028694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_261-168_0_6_line_86 |  | 79 | 83 | 0.015982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_261-168_0_6_line_87 |  | 80 | 82 | 0.046184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_261-168_0_6_line_88 |  | 83 | 84 | 0.00080152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
89 | LV_261-168_0_6_line_89 |  | 84 | 85 | 0.0072803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
90 | LV_261-168_0_6_line_90 |  | 85 | 86 | 0.011271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
91 | LV_261-168_0_6_line_91 |  | 86 | 87 | 0.0031159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
92 | LV_261-168_0_6_line_92 |  | 87 | 92 | 0.0061474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
93 | LV_261-168_0_6_line_93 |  | 89 | 90 | 0.00043349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
94 | LV_261-168_0_6_line_94 |  | 90 | 91 | 0.011834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
95 | LV_261-168_0_6_line_95 |  | 91 | 103 | 0.0061807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_261-168_0_6_line_96 |  | 91 | 102 | 0.0043194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
97 | LV_261-168_0_6_line_97 |  | 92 | 93 | 0.0011905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
98 | LV_261-168_0_6_line_98 |  | 93 | 94 | 0.014136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
99 | LV_261-168_0_6_line_99 |  | 94 | 95 | 0.0040038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
100 | LV_261-168_0_6_line_100 |  | 95 | 96 | 0.0033324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
101 | LV_261-168_0_6_line_101 |  | 96 | 97 | 0.0049897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
102 | LV_261-168_0_6_line_102 |  | 97 | 98 | 0.011023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
103 | LV_261-168_0_6_line_103 |  | 98 | 99 | 0.0023823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
104 | LV_261-168_0_6_line_104 |  | 99 | 100 | 0.0073381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
105 | LV_261-168_0_6_line_105 |  | 100 | 101 | 0.0029791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
106 | LV_261-168_0_6_line_106 |  | 101 | 102 | 0.012214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
107 | LV_261-168_0_6_line_107 |  | 103 | 104 | 0.011023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_261-168_0_6_line_108 |  | 104 | 105 | 0.0011882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_261-168_0_6_line_109 |  | 105 | 129 | 0.0089139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-168_0_6_line_110 |  | 106 | 107 | 0.016531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_261-168_0_6_line_111 |  | 107 | 108 | 0.035241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_261-168_0_6_line_112 |  | 107 | 109 | 0.004846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_261-168_0_6_line_113 |  | 109 | 110 | 0.016059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_261-168_0_6_line_114 |  | 110 | 119 | 0.0088268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_261-168_0_6_line_115 |  | 114 | 115 | 0.0090187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_261-168_0_6_line_116 |  | 114 | 116 | 0.0070834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_261-168_0_6_line_117 |  | 115 | 117 | 0.016783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_261-168_0_6_line_118 |  | 116 | 118 | 0.031958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_261-168_0_6_line_119 |  | 117 | 119 | 0.021342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_261-168_0_6_line_120 |  | 120 | 121 | 0.0026281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_261-168_0_6_line_121 |  | 120 | 122 | 0.012195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_261-168_0_6_line_122 |  | 121 | 123 | 0.0059526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_261-168_0_6_line_123 |  | 122 | 124 | 0.0059578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_261-168_0_6_line_124 |  | 123 | 125 | 0.0025922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_261-168_0_6_line_125 |  | 124 | 126 | 0.0031024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_261-168_0_6_line_126 |  | 125 | 127 | 0.011448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_261-168_0_6_line_127 |  | 126 | 128 | 0.0050654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_261-168_0_6_line_128 |  | 127 | 130 | 0.0075824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_261-168_0_6_line_129 |  | 128 | 129 | 0.011358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-168_0_6_trafo_86 | 0.63 MVA 20/0.4 kV | 131 | 98 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2679424.7348 | 1250717.028 | 2679433.1719 | 1250743.4317
1 | 2679436.7107 | 1250754.5383 | 2679434.9868 | 1250749.1112 | 2679433.1719 | 1250743.4317
2 | 2679428.1597 | 1250714.9612 | 2679424.5203 | 1250716.1356 | 2679424.7348 | 1250717.028
3 | 2679436.7107 | 1250754.5383 | 2679432.7014 | 1250756.2748
4 | 2679436.7107 | 1250754.5383 | 2679444.4559 | 1250751.1841 | 2679452.3252 | 1250748.7681
5 | 2679428.1597 | 1250714.9612 | 2679425.757 | 1250707.2345 | 2679422.597 | 1250703.6228 | 2679421.9611 | 1250700.9345 | 2679422.4543 | 1250697.3718 | 2679424.5659 | 1250695.8435 | 2679429.5212 | 1250693.3747 | 2679430.5257 | 1250691.0865 | 2679433.0163 | 1250688.8849 | 2679445.6971 | 1250685.708
6 | 2679428.1597 | 1250714.9612 | 2679435.5211 | 1250713.7701 | 2679438.5661 | 1250714.7005 | 2679442.0375 | 1250717.0488 | 2679446.9523 | 1250718.1599 | 2679452.3443 | 1250716.8979 | 2679458.827 | 1250711.9923 | 2679467.9706 | 1250709.0683 | 2679473.707 | 1250704.086 | 2679477.4641 | 1250702.5797 | 2679483.427 | 1250702.6597 | 2679487.1912 | 1250700.6198 | 2679487.7869 | 1250695.0459
7 | 2679432.7014 | 1250756.2748 | 2679435.8316 | 1250764.9231 | 2679442.8416 | 1250771.3551
8 | 2679432.7014 | 1250756.2748 | 2679422.9366 | 1250760.4915 | 2679414.4306 | 1250763.6731
9 | 2679453.8254 | 1250748.3076 | 2679452.3252 | 1250748.7681
10 | 2679442.8416 | 1250771.3551 | 2679444.0608 | 1250770.985
11 | 2679442.8416 | 1250771.3551 | 2679439.15 | 1250772.4842 | 2679425.6891 | 1250777.054
12 | 2679536.5885 | 1250742.0574 | 2679559.7846 | 1250734.9523
13 | 2679559.7846 | 1250734.9523 | 2679567.5268 | 1250732.9547
14 | 2679559.7846 | 1250734.9523 | 2679565.7867 | 1250755.8148
15 | 2679525.8984 | 1250726.9028 | 2679527.0135 | 1250730.9985 | 2679527.8332 | 1250734.0451 | 2679529.0061 | 1250738.3418 | 2679530.4948 | 1250743.8547 | 2679536.5885 | 1250742.0574
16 | 2679536.5885 | 1250742.0574 | 2679536.6652 | 1250743.0925 | 2679539.2581 | 1250782.0148
17 | 2679514.9694 | 1250748.6611 | 2679530.4948 | 1250743.8547 | 2679536.5885 | 1250742.0574
18 | 2679567.5268 | 1250732.9547 | 2679593.5639 | 1250726.2327 | 2679598.0889 | 1250745.1074
19 | 2679567.5268 | 1250732.9547 | 2679572.0414 | 1250748.2733
20 | 2679572.0458 | 1250777.5705 | 2679565.7867 | 1250755.8148
21 | 2679393.5936 | 1250807.1772 | 2679388.3425 | 1250789.4827
22 | 2679388.3425 | 1250789.4827 | 2679403.7341 | 1250784.5075 | 2679425.6891 | 1250777.054
23 | 2679393.5936 | 1250807.1772 | 2679395.2003 | 1250806.7095 | 2679395.6693 | 1250808.3187
24 | 2679514.9694 | 1250748.6611 | 2679497.3412 | 1250754.1137
25 | 2679453.8254 | 1250748.3076 | 2679460.4221 | 1250746.2808
26 | 2679482.6584 | 1250739.457 | 2679482.1915 | 1250739.5925 | 2679460.4221 | 1250746.2808
27 | 2679459.7226 | 1250766.222 | 2679458.7221 | 1250766.52 | 2679450.1033 | 1250769.1508 | 2679444.0608 | 1250770.985
28 | 2679525.8984 | 1250726.9028 | 2679508.7128 | 1250731.8924
29 | 2679525.8984 | 1250726.9028 | 2679537.8491 | 1250724.5102
30 | 2679539.2581 | 1250782.0148 | 2679539.6032 | 1250787.1937
31 | 2679399.3073 | 1250827.0998 | 2679397.8288 | 1250821.8114 | 2679399.4296 | 1250821.2213 | 2679395.6693 | 1250808.3187
32 | 2679508.7128 | 1250731.8924 | 2679499.8558 | 1250734.4639
33 | 2679555.3733 | 1250721.0018 | 2679537.8491 | 1250724.5102
34 | 2679459.7226 | 1250766.222 | 2679473.7715 | 1250761.6362
35 | 2679392.136 | 1250913.6695 | 2679415.0202 | 1250904.9919 | 2679435.0819 | 1250896.8214
36 | 2679392.136 | 1250913.6695 | 2679386.6939 | 1250898.7844
37 | 2679437.2396 | 1250895.794 | 2679435.0819 | 1250896.8214
38 | 2679435.0819 | 1250896.8214 | 2679440.5152 | 1250910.3378
39 | 2679386.6919 | 1250898.7788 | 2679386.6939 | 1250898.7844
40 | 2679598.0889 | 1250745.1074 | 2679610.0567 | 1250741.9209
41 | 2679598.0889 | 1250745.1074 | 2679603.8747 | 1250767.1738
42 | 2679572.0655 | 1250717.66 | 2679555.3733 | 1250721.0018
43 | 2679572.0655 | 1250717.66 | 2679568.1252 | 1250700.7724 | 2679565.6866 | 1250689.5425 | 2679562.9149 | 1250675.9292
44 | 2679558.5409 | 1250654.4318 | 2679559.0011 | 1250656.7063 | 2679562.9149 | 1250675.9292
45 | 2679558.5409 | 1250654.4318 | 2679547.4914 | 1250655.918 | 2679521.1262 | 1250660.3739
46 | 2679655.7201 | 1250865.2146 | 2679663.5432 | 1250861.1167 | 2679666.6588 | 1250860.0783
47 | 2679644.3707 | 1250880.6067 | 2679650.8334 | 1250871.0087 | 2679655.7201 | 1250865.2146
48 | 2679655.7201 | 1250865.2146 | 2679653.1377 | 1250862.4556 | 2679648.9008 | 1250864.3423
49 | 2679653.1087 | 1250796.7884 | 2679658.5602 | 1250794.2448
50 | 2679653.1087 | 1250796.7884 | 2679643.0871 | 1250801.4645 | 2679641.9479 | 1250801.8972
51 | 2679482.6584 | 1250739.457 | 2679491.4732 | 1250736.8977
52 | 2679402.4032 | 1250838.1736 | 2679394.9338 | 1250845.1787 | 2679384.4637 | 1250848.9598
53 | 2679402.4032 | 1250838.1736 | 2679416.9583 | 1250834.199 | 2679428.0446 | 1250832.7576 | 2679441.6177 | 1250827.8032
54 | 2679402.4032 | 1250838.1736 | 2679399.3073 | 1250827.0998
55 | 2679548.5622 | 1250824.2518 | 2679542.2794 | 1250807.9156 | 2679540.6327 | 1250801.8112 | 2679540.2841 | 1250797.4144 | 2679539.6032 | 1250787.1937
56 | 2679499.8558 | 1250734.4639 | 2679491.4732 | 1250736.8977
57 | 2679437.2396 | 1250895.794 | 2679448.5759 | 1250890.3419
58 | 2679437.2396 | 1250895.794 | 2679433.3312 | 1250880.629
59 | 2679454.9229 | 1250946.1792 | 2679440.5152 | 1250910.3378
60 | 2679381.0527 | 1250883.3543 | 2679386.6919 | 1250898.7788
61 | 2679455.8407 | 1250822.6116 | 2679441.6177 | 1250827.8032
62 | 2679381.0527 | 1250883.3543 | 2679376.5721 | 1250880.2698
63 | 2679381.0527 | 1250883.3543 | 2679386.8858 | 1250877.895 | 2679392.7494 | 1250874.1041
64 | 2679448.5759 | 1250890.3419 | 2679453.4935 | 1250887.9897
65 | 2679448.5759 | 1250890.3419 | 2679445.4195 | 1250883.6502 | 2679445.4195 | 1250883.6502
66 | 2679433.3312 | 1250880.629 | 2679431.0828 | 1250871.905 | 2679429.774 | 1250872.1209 | 2679428.2587 | 1250865.7737 | 2679419.7439 | 1250867.9857
67 | 2679454.9229 | 1250946.1792 | 2679458.2827 | 1250944.4563 | 2679462.2599 | 1250942.8529 | 2679468.4951 | 1250940.7572
68 | 2679454.9229 | 1250946.1792 | 2679463.1982 | 1250964.626
69 | 2679509.2054 | 1250993.5866 | 2679505.1822 | 1250983.9922 | 2679502.6715 | 1250978.1431 | 2679499.4162 | 1250979.3892 | 2679495.0274 | 1250968.3556 | 2679493.1409 | 1250963.8047 | 2679490.6415 | 1250955.4205 | 2679489.9687 | 1250953.1675
70 | 2679485.2377 | 1250937.3236 | 2679489.9687 | 1250953.1675
71 | 2679509.2054 | 1250993.5866 | 2679516.8442 | 1250990.2644
72 | 2679485.2377 | 1250937.3236 | 2679479.101 | 1250938.4977
73 | 2679485.2377 | 1250937.3236 | 2679494.1825 | 1250933.3686
74 | 2679516.8442 | 1250990.2644 | 2679512.991 | 1250981.5062 | 2679510.2534 | 1250975.1203 | 2679508.7106 | 1250972.5199 | 2679505.8572 | 1250971.3919 | 2679497.2266 | 1250954.2352
75 | 2679468.4951 | 1250940.7572 | 2679470.0857 | 1250940.2226 | 2679479.101 | 1250938.4977
76 | 2679494.1825 | 1250933.3686 | 2679505.8859 | 1250928.1938 | 2679504.1991 | 1250924.5129 | 2679504.4024 | 1250924.4305
77 | 2679463.1982 | 1250964.626 | 2679419.6607 | 1250980.6422
78 | 2679518.299 | 1250919.0091 | 2679511.9254 | 1250921.4254 | 2679504.8898 | 1250924.2331 | 2679504.4024 | 1250924.4305
79 | 2679646.0512 | 1250922.9272 | 2679631.8293 | 1250929.074 | 2679631.0573 | 1250929.5217
80 | 2679646.0512 | 1250922.9272 | 2679656.3844 | 1250919.6637 | 2679660.7613 | 1250917.3725
81 | 2679646.0512 | 1250922.9272 | 2679643.8659 | 1250917.0268 | 2679642.0773 | 1250896.2097 | 2679642.0177 | 1250893.8042
82 | 2679612.049 | 1250940.5459 | 2679631.0573 | 1250929.5217
83 | 2679644.3707 | 1250880.6067 | 2679641.8816 | 1250888.3123 | 2679642.0177 | 1250893.8042
84 | 2679518.299 | 1250919.0091 | 2679513.9611 | 1250909.0772
85 | 2679545.4321 | 1250912.1236 | 2679539.6562 | 1250912.1906 | 2679522.4414 | 1250919.7207 | 2679518.299 | 1250919.0091
86 | 2679467.867 | 1250881.0098 | 2679466.6662 | 1250881.6891 | 2679453.4935 | 1250887.9897
87 | 2679445.4195 | 1250883.6502 | 2679437.3778 | 1250885.4882 | 2679435.1365 | 1250876.9852 | 2679428.0821 | 1250848.7105
88 | 2679467.867 | 1250881.0098 | 2679468.5646 | 1250880.6151
89 | 2679474.9011 | 1250877.0302 | 2679468.5646 | 1250880.6151
90 | 2679484.7113 | 1250871.4801 | 2679474.9011 | 1250877.0302
91 | 2679484.7113 | 1250871.4801 | 2679487.4233 | 1250869.9458
92 | 2679492.7738 | 1250866.9187 | 2679487.4233 | 1250869.9458
93 | 2679548.7178 | 1250824.6564 | 2679548.5622 | 1250824.2518
94 | 2679552.9658 | 1250835.7017 | 2679548.7178 | 1250824.6564
95 | 2679552.9658 | 1250835.7017 | 2679558.7436 | 1250833.5067
96 | 2679552.9658 | 1250835.7017 | 2679548.9872 | 1250837.3834
97 | 2679492.7738 | 1250866.9187 | 2679493.8099 | 1250866.3325
98 | 2679506.0457 | 1250859.2538 | 2679495.2146 | 1250865.5378 | 2679493.8099 | 1250866.3325
99 | 2679509.5089 | 1250857.2445 | 2679506.0457 | 1250859.2538
100 | 2679509.5089 | 1250857.2445 | 2679512.3913 | 1250855.5722
101 | 2679516.7072 | 1250853.0682 | 2679512.3913 | 1250855.5722
102 | 2679516.7072 | 1250853.0682 | 2679523.5557 | 1250849.0947 | 2679526.3113 | 1250847.6624
103 | 2679528.4252 | 1250846.5637 | 2679526.3113 | 1250847.6624
104 | 2679534.9925 | 1250843.2989 | 2679533.4614 | 1250843.9461 | 2679528.4252 | 1250846.5637
105 | 2679534.9925 | 1250843.2989 | 2679537.7365 | 1250842.139
106 | 2679548.9872 | 1250837.3834 | 2679537.7365 | 1250842.139
107 | 2679569.048 | 1250829.592 | 2679558.7436 | 1250833.5067
108 | 2679569.048 | 1250829.592 | 2679570.1588 | 1250829.1701
109 | 2679578.4916 | 1250826.0044 | 2679570.1588 | 1250829.1701
110 | 2679545.4321 | 1250912.1236 | 2679535.3092 | 1250919.4043 | 2679531.6656 | 1250921.1997
111 | 2679545.4321 | 1250912.1236 | 2679560.3045 | 1250944.0724
112 | 2679545.4321 | 1250912.1236 | 2679547.4165 | 1250907.7026
113 | 2679547.4165 | 1250907.7026 | 2679547.4165 | 1250907.7026 | 2679561.9472 | 1250900.8659
114 | 2679569.9341 | 1250897.1081 | 2679561.9472 | 1250900.8659
115 | 2679613.236 | 1250880.2237 | 2679604.9973 | 1250883.8924
116 | 2679613.236 | 1250880.2237 | 2679619.7069 | 1250877.3423
117 | 2679604.9973 | 1250883.8924 | 2679601.7758 | 1250885.3269 | 2679589.7476 | 1250890.8989
118 | 2679648.9008 | 1250864.3423 | 2679619.7069 | 1250877.3423
119 | 2679569.9341 | 1250897.1081 | 2679575.0899 | 1250897.6888 | 2679589.7476 | 1250890.8989
120 | 2679613.7136 | 1250812.6235 | 2679616.1704 | 1250811.6902
121 | 2679613.7136 | 1250812.6235 | 2679602.314 | 1250816.9542
122 | 2679616.1704 | 1250811.6902 | 2679621.735 | 1250809.5762
123 | 2679602.314 | 1250816.9542 | 2679596.7446 | 1250819.0701
124 | 2679621.735 | 1250809.5762 | 2679624.1582 | 1250808.6556
125 | 2679593.8444 | 1250820.1718 | 2679596.7446 | 1250819.0701
126 | 2679634.8598 | 1250804.59 | 2679624.1582 | 1250808.6556
127 | 2679589.1092 | 1250821.9708 | 2679593.8444 | 1250820.1718
128 | 2679641.9479 | 1250801.8972 | 2679634.8598 | 1250804.59
129 | 2679589.1092 | 1250821.9708 | 2679578.4916 | 1250826.0044

## bus_geodata
| x | y | coords
0 | 2679433.1719 | 1250743.4317
1 | 2679424.7348 | 1250717.028
2 | 2679436.7107 | 1250754.5383
3 | 2679428.1597 | 1250714.9612
4 | 2679432.7014 | 1250756.2748
5 | 2679452.3252 | 1250748.7681
6 | 2679445.6971 | 1250685.708
7 | 2679487.7869 | 1250695.0459
8 | 2679442.8416 | 1250771.3551
9 | 2679414.4306 | 1250763.6731
10 | 2679559.7846 | 1250734.9523
11 | 2679536.5885 | 1250742.0574
12 | 2679567.5268 | 1250732.9547
13 | 2679565.7867 | 1250755.8148
14 | 2679388.3425 | 1250789.4827
15 | 2679393.5936 | 1250807.1772
16 | 2679425.6891 | 1250777.054
17 | 2679514.9694 | 1250748.6611
18 | 2679497.3412 | 1250754.1137
19 | 2679453.8254 | 1250748.3076
20 | 2679460.4221 | 1250746.2808
21 | 2679444.0608 | 1250770.985
22 | 2679525.8984 | 1250726.9028
23 | 2679539.2581 | 1250782.0148
24 | 2679395.6693 | 1250808.3187
25 | 2679508.7129 | 1250731.8924
26 | 2679537.8491 | 1250724.5102
27 | 2679459.7226 | 1250766.222
28 | 2679473.7715 | 1250761.6362
29 | 2679392.136 | 1250913.6695
30 | 2679435.0819 | 1250896.8214
31 | 2679386.6939 | 1250898.7844
32 | 2679598.0889 | 1250745.1074
33 | 2679572.0414 | 1250748.2733
34 | 2679610.0567 | 1250741.9209
35 | 2679603.8747 | 1250767.1738
36 | 2679572.0655 | 1250717.66
37 | 2679555.3733 | 1250721.0018
38 | 2679562.9149 | 1250675.9292
39 | 2679558.5409 | 1250654.4318
40 | 2679521.1262 | 1250660.3739
41 | 2679666.6588 | 1250860.0783
42 | 2679655.7201 | 1250865.2146
43 | 2679658.5602 | 1250794.2448
44 | 2679653.1087 | 1250796.7884
45 | 2679572.0458 | 1250777.5705
46 | 2679482.6584 | 1250739.457
47 | 2679384.4637 | 1250848.9598
48 | 2679402.4032 | 1250838.1736
49 | 2679539.6032 | 1250787.1937
50 | 2679399.3073 | 1250827.0998
51 | 2679499.8558 | 1250734.4639
52 | 2679437.2396 | 1250895.794
53 | 2679440.5152 | 1250910.3378
54 | 2679386.6919 | 1250898.7788
55 | 2679441.6177 | 1250827.8032
56 | 2679455.8407 | 1250822.6116
57 | 2679381.0527 | 1250883.3543
58 | 2679376.5721 | 1250880.2698
59 | 2679392.7494 | 1250874.1041
60 | 2679448.5759 | 1250890.3419
61 | 2679433.3312 | 1250880.629
62 | 2679454.9229 | 1250946.1792
63 | 2679489.9687 | 1250953.1675
64 | 2679509.2054 | 1250993.5866
65 | 2679485.2377 | 1250937.3236
66 | 2679516.8442 | 1250990.2644
67 | 2679479.101 | 1250938.4977
68 | 2679494.1825 | 1250933.3686
69 | 2679497.2266 | 1250954.2352
70 | 2679463.1982 | 1250964.626
71 | 2679419.6607 | 1250980.6422
72 | 2679468.4952 | 1250940.7572
73 | 2679504.4024 | 1250924.4305
74 | 2679646.0512 | 1250922.9272
75 | 2679631.0573 | 1250929.5217
76 | 2679660.7613 | 1250917.3725
77 | 2679642.0177 | 1250893.8042
78 | 2679518.299 | 1250919.0091
79 | 2679453.4935 | 1250887.9897
80 | 2679445.4195 | 1250883.6502
81 | 2679419.7439 | 1250867.9857
82 | 2679428.0821 | 1250848.7105
83 | 2679467.867 | 1250881.0098
84 | 2679468.5646 | 1250880.6151
85 | 2679474.9011 | 1250877.0302
86 | 2679484.7113 | 1250871.4801
87 | 2679487.4233 | 1250869.9458
88 | 2679491.4732 | 1250736.8977
89 | 2679548.5622 | 1250824.2518
90 | 2679548.7178 | 1250824.6564
91 | 2679552.9658 | 1250835.7017
92 | 2679492.7738 | 1250866.9187
93 | 2679493.8099 | 1250866.3325
94 | 2679506.0457 | 1250859.2538
95 | 2679509.5089 | 1250857.2445
96 | 2679512.3913 | 1250855.5722
97 | 2679516.7072 | 1250853.0682
98 | 2679526.3113 | 1250847.6624
99 | 2679528.4252 | 1250846.5637
100 | 2679534.9925 | 1250843.2989
101 | 2679537.7365 | 1250842.139
102 | 2679548.9872 | 1250837.3834
103 | 2679558.7436 | 1250833.5067
104 | 2679569.048 | 1250829.592
105 | 2679570.1588 | 1250829.1701
106 | 2679531.6656 | 1250921.1997
107 | 2679545.4321 | 1250912.1236
108 | 2679560.3045 | 1250944.0724
109 | 2679547.4165 | 1250907.7026
110 | 2679561.9472 | 1250900.8659
111 | 2679513.9611 | 1250909.0772
112 | 2679612.049 | 1250940.5459
113 | 2679644.3707 | 1250880.6067
114 | 2679613.236 | 1250880.2237
115 | 2679604.9973 | 1250883.8924
116 | 2679619.7069 | 1250877.3423
117 | 2679589.7476 | 1250890.8989
118 | 2679648.9008 | 1250864.3423
119 | 2679569.9341 | 1250897.1081
120 | 2679613.7136 | 1250812.6235
121 | 2679616.1704 | 1250811.6902
122 | 2679602.314 | 1250816.9542
123 | 2679621.735 | 1250809.5762
124 | 2679596.7446 | 1250819.0701
125 | 2679624.1582 | 1250808.6556
126 | 2679593.8444 | 1250820.1718
127 | 2679634.8598 | 1250804.59
128 | 2679589.1092 | 1250821.9708
129 | 2679578.4916 | 1250826.0044
130 | 2679641.9479 | 1250801.8972
131 | 2679526.3113 | 1250847.6624

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97728 | -0.437 | 0.0047553 | 0.0011918
1 | 0.97621 | -0.458 | 0 | 0
2 | 0.97778 | -0.42718 | 0 | 0
3 | 0.97602 | -0.46159 | 0 | 0
4 | 0.97751 | -0.43235 | 0 | 0
5 | 0.9795 | -0.39341 | 0.0044624 | 0.0011184
6 | 0.97434 | -0.49485 | 0.0392 | 0.0098245
7 | 0.97588 | -0.46452 | 0.0022656 | 0.00056781
8 | 0.9765 | -0.45217 | 0 | 0
9 | 0.97739 | -0.43487 | 0.0070245 | 0.0017605
10 | 0.98932 | -0.20383 | 0 | 0
11 | 0.99042 | -0.18252 | 0 | 0
12 | 0.98916 | -0.20693 | 0 | 0
13 | 0.98877 | -0.21452 | 0.019607 | 0.0049139
14 | 0.97465 | -0.48854 | 0 | 0
15 | 0.9741 | -0.4994 | 0 | 0
16 | 0.97583 | -0.46543 | 0.0080415 | 0.0020154
17 | 0.99021 | -0.18654 | 0 | 0
18 | 0.99004 | -0.18983 | 0.010018 | 0.0025108
19 | 0.97967 | -0.39011 | 0 | 0
20 | 0.98042 | -0.37561 | 0.0044579 | 0.0011173
21 | 0.97648 | -0.45259 | 0.0099703 | 0.0024988
22 | 0.98861 | -0.21712 | 0 | 0
23 | 0.99316 | -0.12998 | 0.015399 | 0.0038593
24 | 0.974 | -0.50137 | 0.0042166 | 0.0010568
25 | 0.9863 | -0.26161 | 0.0042937 | 0.0010761
26 | 0.98835 | -0.22224 | 0.007881 | 0.0019752
27 | 0.97636 | -0.45498 | 0 | 0
28 | 0.97625 | -0.45714 | 0.0079776 | 0.0019994
29 | 0.99265 | -0.14007 | 0 | 0
30 | 0.99362 | -0.12136 | 0 | 0
31 | 0.99232 | -0.14653 | 0.0043261 | 0.0010842
32 | 0.98854 | -0.21891 | 0 | 0
33 | 0.98905 | -0.20902 | 0.0073479 | 0.0018415
34 | 0.98846 | -0.22046 | 0.0070141 | 0.0017579
35 | 0.98838 | -0.22197 | 0.0075021 | 0.0018802
36 | 0.98797 | -0.22959 | 0 | 0
37 | 0.98809 | -0.22722 | 0.007825 | 0.0019611
38 | 0.98767 | -0.23554 | 0.0033773 | 0.00084642
39 | 0.98758 | -0.23728 | 0 | 0
40 | 0.98742 | -0.24027 | 0.004421 | 0.001108
41 | 0.97566 | -0.46979 | 0.0059909 | 0.0015015
42 | 0.97572 | -0.46846 | 0 | 0
43 | 0.99463 | -0.10269 | 0.0020531 | 0.00051456
44 | 0.99464 | -0.10248 | 0.01306 | 0.0032733
45 | 0.9886 | -0.21776 | 0.0080341 | 0.0020135
46 | 0.98302 | -0.32505 | 0.0051932 | 0.0013015
47 | 0.97311 | -0.51905 | 0.0052427 | 0.0013139
48 | 0.97321 | -0.51699 | 0 | 0
49 | 0.99354 | -0.12273 | 0.0060415 | 0.0015141
50 | 0.97347 | -0.51193 | 0.0038879 | 0.0009744
51 | 0.98514 | -0.2839 | 0.0047121 | 0.001181
52 | 0.99375 | -0.1188 | 0 | 0
53 | 0.99291 | -0.135 | 0.002128 | 0.00053333
54 | 0.99232 | -0.14653 | 0.0065215 | 0.0016344
55 | 0.9725 | -0.53101 | 0.0038667 | 0.00096908
56 | 0.97229 | -0.53515 | 0.014827 | 0.0037159
57 | 0.99214 | -0.15007 | 0 | 0
58 | 0.99211 | -0.15065 | 0.0060821 | 0.0015243
59 | 0.99205 | -0.15168 | 0.0060855 | 0.0015252
60 | 0.99448 | -0.10489 | 0 | 0
61 | 0.99366 | -0.1206 | 0.0033169 | 0.00083129
62 | 0.99011 | -0.18871 | 0 | 0
63 | 0.98646 | -0.25905 | 0.0058039 | 0.0014546
64 | 0.98611 | -0.26586 | 0 | 0
65 | 0.98667 | -0.25499 | 0 | 0
66 | 0.98605 | -0.26703 | 0 | 0
67 | 0.98731 | -0.24254 | 0.0045354 | 0.0011367
68 | 0.98578 | -0.27211 | 0.004636 | 0.0011619
69 | 0.98575 | -0.27295 | 0.0078896 | 0.0019773
70 | 0.98943 | -0.20188 | 0 | 0
71 | 0.98787 | -0.23216 | 0.036603 | 0.0091737
72 | 0.98848 | -0.22007 | 0.0043766 | 0.0010969
73 | 0.98431 | -0.30062 | 0.005066 | 0.0012697
74 | 0.97472 | -0.48819 | 0 | 0
75 | 0.97456 | -0.49144 | 0.0044179 | 0.0011072
76 | 0.97466 | -0.48949 | 0.0044925 | 0.0011259
77 | 0.97514 | -0.47988 | 0.0037438 | 0.00093829
78 | 0.98309 | -0.32425 | 0 | 0
79 | 0.9948 | -0.098731 | 0.0021367 | 0.00053551
80 | 0.99446 | -0.1054 | 0.0020068 | 0.00050294
81 | 0.99359 | -0.12205 | 0.0032018 | 0.00080245
82 | 0.99438 | -0.10695 | 0.0019066 | 0.00047785
83 | 0.99576 | -0.080491 | 0.0024653 | 0.00061786
84 | 0.99581 | -0.079565 | 0.0011969 | 0.00029998
85 | 0.99625 | -0.071112 | 0.00119 | 0.00029825
86 | 0.99694 | -0.057962 | 0.0015965 | 0.00040011
87 | 0.99714 | -0.054301 | 0.0012797 | 0.00032073
88 | 0.98409 | -0.30431 | 0.004646 | 0.0011644
89 | 0.99643 | -0.06773 | 0.0017775 | 0.00044549
90 | 0.99646 | -0.067107 | 0.0019448 | 0.00048741
91 | 0.99736 | -0.050001 | 0 | 0
92 | 0.99752 | -0.047036 | 0.0013743 | 0.00034444
93 | 0.99759 | -0.04562 | 0.0017642 | 0.00044214
94 | 0.99849 | -0.028679 | 0.0018157 | 0.00045505
95 | 0.99874 | -0.023844 | 0.0019963 | 0.00050031
96 | 0.99896 | -0.019783 | 0.0018011 | 0.00045141
97 | 0.99928 | -0.013653 | 0.0019369 | 0.00048544
98 | 1 | 0 | -0.51999 | -0.13269
99 | 0.99978 | -0.0041281 | 0.0017615 | 0.00044147
100 | 0.99911 | -0.01678 | 0.0019688 | 0.00049344
101 | 0.99884 | -0.021886 | 0.0022874 | 0.00057328
102 | 0.99775 | -0.04269 | 0.002258 | 0.00056592
103 | 0.99712 | -0.05462 | 0.0023172 | 0.00058074
104 | 0.99672 | -0.062414 | 0.0019338 | 0.00048465
105 | 0.99667 | -0.063215 | 0.0023278 | 0.00058341
106 | 0.98078 | -0.36938 | 0.0077139 | 0.0019333
107 | 0.9809 | -0.36707 | 0 | 0
108 | 0.98064 | -0.37219 | 0.0080121 | 0.002008
109 | 0.9806 | -0.37294 | 0.0069387 | 0.001739
110 | 0.9797 | -0.39038 | 0.0052529 | 0.0013165
111 | 0.98304 | -0.32531 | 0.0053978 | 0.0013528
112 | 0.97443 | -0.49402 | 0.0063925 | 0.0016021
113 | 0.97538 | -0.47514 | 0 | 0
114 | 0.97707 | -0.44189 | 0.0061552 | 0.0015426
115 | 0.97743 | -0.43491 | 0.005104 | 0.0012792
116 | 0.97684 | -0.44658 | 0.005432 | 0.0013614
117 | 0.97817 | -0.42036 | 0.0070944 | 0.001778
118 | 0.97592 | -0.46461 | 0.0058037 | 0.0014545
119 | 0.97925 | -0.39915 | 0 | 0
120 | 0.99534 | -0.08888 | 0.0019496 | 0.00048862
121 | 0.99528 | -0.090019 | 0.0024427 | 0.00061221
122 | 0.99564 | -0.083177 | 0.0019241 | 0.00048222
123 | 0.99516 | -0.092345 | 0.0015352 | 0.00038475
124 | 0.99579 | -0.08019 | 0.0020137 | 0.00050469
125 | 0.99512 | -0.093287 | 0.0024007 | 0.00060166
126 | 0.99588 | -0.078526 | 0.0017202 | 0.00043113
127 | 0.99492 | -0.096968 | 0.0014927 | 0.0003741
128 | 0.99603 | -0.075655 | 0.0018383 | 0.00046073
129 | 0.99638 | -0.068856 | 0.0019693 | 0.00049356
130 | 0.99481 | -0.099207 | 0.0016546 | 0.00041467
131 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.041577 | 0.010462 | -0.041535 | -0.010435 | 4.1677e-05 | 2.6327e-05 | 0.063321 | 0.063321 | 0.063321 | 0.97728 | -0.437 | 0.97621 | -0.458 | 17.3958
1 | -0.046332 | -0.011653 | 0.046354 | 0.011667 | 2.1764e-05 | 1.3783e-05 | 0.070561 | 0.070561 | 0.070561 | 0.97728 | -0.437 | 0.97778 | -0.42718 | 19.3849
2 | 0.041535 | 0.010435 | -0.041528 | -0.010431 | 7.1149e-06 | 4.4944e-06 | 0.063321 | 0.063321 | 0.063321 | 0.97621 | -0.458 | 0.97602 | -0.46159 | 17.3958
3 | 0.065245 | 0.016423 | -0.065229 | -0.016412 | 1.612e-05 | 1.0262e-05 | 0.099317 | 0.099317 | 0.099317 | 0.97778 | -0.42718 | 0.97751 | -0.43235 | 27.285
4 | -0.1116 | -0.02809 | 0.11178 | 0.028205 | 0.00018043 | 0.00011526 | 0.16988 | 0.16988 | 0.16988 | 0.97778 | -0.42718 | 0.9795 | -0.39341 | 46.6699
5 | 0.039262 | 0.0098637 | -0.0392 | -0.0098245 | 6.2212e-05 | 3.9238e-05 | 0.059867 | 0.059867 | 0.059867 | 0.97602 | -0.46159 | 0.97434 | -0.49485 | 16.4469
6 | 0.0022659 | 0.00056713 | -0.0022656 | -0.00056781 | 3.1608e-07 | -6.8035e-07 | 0.0034542 | 0.0034546 | 0.0034546 | 0.97602 | -0.46159 | 0.97588 | -0.46452 | 0.94906
7 | 0.058203 | 0.014652 | -0.058148 | -0.014617 | 5.5109e-05 | 3.5035e-05 | 0.088623 | 0.088623 | 0.088623 | 0.97751 | -0.43235 | 0.9765 | -0.45217 | 24.347
8 | 0.0070254 | 0.0017608 | -0.0070245 | -0.0017605 | 8.4568e-07 | 2.9409e-07 | 0.010694 | 0.010694 | 0.010694 | 0.97751 | -0.43235 | 0.97739 | -0.43487 | 2.938
9 | -0.11624 | -0.029324 | 0.11626 | 0.029335 | 1.8365e-05 | 1.1734e-05 | 0.17666 | 0.17666 | 0.17666 | 0.9795 | -0.39341 | 0.97967 | -0.39011 | 48.5322
10 | 0.01795 | 0.0044991 | -0.01795 | -0.0044989 | 3.5747e-07 | 2.1284e-07 | 0.027353 | 0.027353 | 0.027353 | 0.9765 | -0.45217 | 0.97648 | -0.45259 | 7.5145
11 | 0.040198 | 0.010118 | -0.040173 | -0.010101 | 2.5447e-05 | 1.606e-05 | 0.06127 | 0.06127 | 0.06127 | 0.9765 | -0.45217 | 0.97583 | -0.46543 | 16.8325
12 | -0.049534 | -0.012424 | 0.049584 | 0.012456 | 5.0367e-05 | 3.1924e-05 | 0.074507 | 0.074507 | 0.074507 | 0.98932 | -0.20383 | 0.99042 | -0.18252 | 20.4689
13 | 0.021878 | 0.0054872 | -0.021875 | -0.0054852 | 3.2382e-06 | 1.9701e-06 | 0.032908 | 0.032908 | 0.032908 | 0.98932 | -0.20383 | 0.98916 | -0.20693 | 9.0406
14 | 0.027656 | 0.0069367 | -0.027642 | -0.0069279 | 1.4088e-05 | 8.7374e-06 | 0.041599 | 0.041599 | 0.041599 | 0.98932 | -0.20383 | 0.98877 | -0.21452 | 11.4283
15 | 0.16443 | 0.041936 | -0.16416 | -0.041761 | 0.00027427 | 0.00017492 | 0.2473 | 0.2473 | 0.2473 | 0.99042 | -0.18252 | 0.98861 | -0.21712 | 33.9702
16 | -0.22404 | -0.056904 | 0.22461 | 0.057266 | 0.00056805 | 0.000362 | 0.33687 | 0.33687 | 0.33687 | 0.99042 | -0.18252 | 0.99316 | -0.12998 | 30.8485
17 | 0.010022 | 0.0025125 | -0.01002 | -0.0025116 | 1.9219e-06 | 9.3916e-07 | 0.015057 | 0.015057 | 0.015057 | 0.99042 | -0.18252 | 0.99021 | -0.18654 | 4.1366
18 | 0.014526 | 0.0036434 | -0.014518 | -0.0036387 | 8.2917e-06 | 4.7127e-06 | 0.021853 | 0.021853 | 0.021853 | 0.98916 | -0.20693 | 0.98854 | -0.21891 | 6.0036
19 | 0.0073486 | 0.0018418 | -0.0073479 | -0.0018415 | 7.3186e-07 | 2.6342e-07 | 0.011055 | 0.011055 | 0.011055 | 0.98916 | -0.20693 | 0.98905 | -0.20902 | 3.037
20 | 0.0080353 | 0.002014 | -0.0080341 | -0.0020135 | 1.2414e-06 | 5.0419e-07 | 0.012093 | 0.012093 | 0.012093 | 0.98877 | -0.21452 | 0.9886 | -0.21776 | 3.3222
21 | 0.032096 | 0.0080639 | -0.032079 | -0.0080535 | 1.6621e-05 | 1.0408e-05 | 0.049008 | 0.049008 | 0.049008 | 0.97465 | -0.48854 | 0.9741 | -0.4994 | 13.4638
22 | -0.032096 | -0.0080639 | 0.032131 | 0.0080861 | 3.5452e-05 | 2.2198e-05 | 0.049008 | 0.049008 | 0.049008 | 0.97465 | -0.48854 | 0.97583 | -0.46543 | 13.4638
23 | 0.032079 | 0.0080535 | -0.032076 | -0.0080516 | 3.0169e-06 | 1.8891e-06 | 0.049008 | 0.049008 | 0.049008 | 0.9741 | -0.4994 | 0.974 | -0.50137 | 13.4638
24 | 0.01002 | 0.0025116 | -0.010018 | -0.0025108 | 1.5688e-06 | 7.6671e-07 | 0.015057 | 0.015057 | 0.015057 | 0.99021 | -0.18654 | 0.99004 | -0.18983 | 4.1366
25 | -0.11626 | -0.029335 | 0.11634 | 0.029387 | 8.0762e-05 | 5.1601e-05 | 0.17666 | 0.17666 | 0.17666 | 0.97967 | -0.39011 | 0.98042 | -0.37561 | 48.5322
26 | -0.1208 | -0.030504 | 0.12109 | 0.030692 | 0.00029346 | 0.00018752 | 0.18342 | 0.18342 | 0.18342 | 0.98042 | -0.37561 | 0.98302 | -0.32505 | 50.391
27 | 0.0079794 | 0.0020001 | -0.0079785 | -0.0019997 | 9.0764e-07 | 3.7614e-07 | 0.012159 | 0.01216 | 0.01216 | 0.97648 | -0.45259 | 0.97636 | -0.45498 | 3.3405
28 | 0.14064 | 0.035863 | -0.14034 | -0.035671 | 0.00030133 | 0.00019262 | 0.2119 | 0.2119 | 0.2119 | 0.98861 | -0.21712 | 0.9863 | -0.26161 | 58.2155
29 | 0.023518 | 0.0058975 | -0.023512 | -0.005894 | 5.7272e-06 | 3.5092e-06 | 0.035399 | 0.035399 | 0.035399 | 0.98861 | -0.21712 | 0.98835 | -0.22224 | 9.725
30 | -0.24 | -0.061125 | 0.24009 | 0.061179 | 8.4055e-05 | 5.3593e-05 | 0.35994 | 0.35994 | 0.35994 | 0.99316 | -0.12998 | 0.99354 | -0.12273 | 32.9613
31 | 0.02786 | 0.0069948 | -0.027846 | -0.0069861 | 1.4022e-05 | 8.7173e-06 | 0.042567 | 0.042567 | 0.042567 | 0.974 | -0.50137 | 0.97347 | -0.51193 | 11.6941
32 | 0.13604 | 0.034595 | -0.1359 | -0.034501 | 0.00014595 | 9.3291e-05 | 0.20543 | 0.20543 | 0.20543 | 0.9863 | -0.26161 | 0.98514 | -0.2839 | 56.4358
33 | 0.015631 | 0.0039188 | -0.015627 | -0.0039166 | 3.7119e-06 | 2.1466e-06 | 0.023534 | 0.023534 | 0.023534 | 0.98835 | -0.22224 | 0.98809 | -0.22722 | 6.4654
34 | 0.0079785 | 0.0019997 | -0.0079776 | -0.0019994 | 8.1941e-07 | 3.3962e-07 | 0.01216 | 0.01216 | 0.01216 | 0.97636 | -0.45498 | 0.97625 | -0.45714 | 3.3406
35 | -0.023025 | -0.0057737 | 0.023046 | 0.0057863 | 2.056e-05 | 1.2563e-05 | 0.034516 | 0.034516 | 0.034516 | 0.99265 | -0.14007 | 0.99362 | -0.12136 | 9.4825
36 | 0.023025 | 0.0057737 | -0.023018 | -0.0057694 | 7.0807e-06 | 4.3268e-06 | 0.034516 | 0.034516 | 0.034516 | 0.99265 | -0.14007 | 0.99232 | -0.14653 | 9.4825
37 | -0.18374 | -0.046716 | 0.18376 | 0.046731 | 2.2601e-05 | 1.4372e-05 | 0.2754 | 0.2754 | 0.2754 | 0.99362 | -0.12136 | 0.99375 | -0.1188 | 25.2194
38 | 0.16069 | 0.04093 | -0.16059 | -0.040863 | 0.00010566 | 6.7055e-05 | 0.24088 | 0.24088 | 0.24088 | 0.99362 | -0.12136 | 0.99291 | -0.135 | 22.0586
39 | 0.018692 | 0.0046852 | -0.018692 | -0.0046852 | 1.7313e-09 | 1.0215e-09 | 0.028029 | 0.028029 | 0.028029 | 0.99232 | -0.14653 | 0.99232 | -0.14653 | 7.7003
40 | 0.0070146 | 0.0017581 | -0.0070141 | -0.0017579 | 5.1779e-07 | 1.7262e-07 | 0.010559 | 0.010559 | 0.010559 | 0.98854 | -0.21891 | 0.98846 | -0.22046 | 2.9008
41 | 0.0075032 | 0.0018806 | -0.0075021 | -0.0018802 | 1.0913e-06 | 4.0599e-07 | 0.011294 | 0.011294 | 0.011294 | 0.98854 | -0.21891 | 0.98838 | -0.22197 | 3.1029
42 | -0.0078015 | -0.0019552 | 0.0078024 | 0.0019555 | 8.8137e-07 | 3.4605e-07 | 0.01175 | 0.01175 | 0.01175 | 0.98797 | -0.22959 | 0.98809 | -0.22722 | 3.228
43 | 0.0078015 | 0.0019552 | -0.0077993 | -0.0019543 | 2.2121e-06 | 8.6879e-07 | 0.01175 | 0.01175 | 0.01175 | 0.98797 | -0.22959 | 0.98767 | -0.23554 | 3.2281
44 | 0.004422 | 0.0011079 | -0.0044217 | -0.0011079 | 3.6514e-07 | -4.7041e-08 | 0.0066621 | 0.0066622 | 0.0066622 | 0.98767 | -0.23554 | 0.98758 | -0.23728 | 1.8303
45 | 0.0044217 | 0.0011079 | -0.004421 | -0.001108 | 6.3064e-07 | -8.1107e-08 | 0.0066622 | 0.0066624 | 0.0066624 | 0.98758 | -0.23728 | 0.98742 | -0.24027 | 1.8303
46 | -0.0059909 | -0.0015015 | 0.0059913 | 0.0015016 | 3.7929e-07 | 9.1436e-08 | 0.009137 | 0.0091369 | 0.009137 | 0.97566 | -0.46979 | 0.97572 | -0.46846 | 2.5102
47 | 0.019066 | 0.0047844 | -0.01906 | -0.0047807 | 6.0668e-06 | 3.6439e-06 | 0.029078 | 0.029079 | 0.029079 | 0.97572 | -0.46846 | 0.97538 | -0.47514 | 7.9886
48 | -0.025057 | -0.0062859 | 0.025062 | 0.0062888 | 4.6096e-06 | 2.845e-06 | 0.038215 | 0.038215 | 0.038215 | 0.97572 | -0.46846 | 0.97592 | -0.46461 | 10.4987
49 | -0.0020531 | -0.00051456 | 0.0020531 | 0.0005145 | 2.1283e-08 | -6.4456e-08 | 0.0030716 | 0.0030716 | 0.0030716 | 0.99463 | -0.10269 | 0.99464 | -0.10248 | 0.84384
50 | -0.015114 | -0.0037878 | 0.015116 | 0.0037891 | 2.3537e-06 | 1.347e-06 | 0.022611 | 0.02261 | 0.022611 | 0.99464 | -0.10248 | 0.99481 | -0.099207 | 6.2117
51 | -0.12629 | -0.031993 | 0.12641 | 0.032074 | 0.00012594 | 8.0487e-05 | 0.19128 | 0.19128 | 0.19128 | 0.98302 | -0.32505 | 0.98409 | -0.30431 | 52.5506
52 | -0.0052427 | -0.0013139 | 0.0052432 | 0.001314 | 5.1509e-07 | 6.4119e-08 | 0.0080168 | 0.0080167 | 0.0080168 | 0.97311 | -0.51905 | 0.97321 | -0.51699 | 2.2024
53 | 0.018709 | 0.0046941 | -0.018696 | -0.0046866 | 1.2495e-05 | 7.4915e-06 | 0.028607 | 0.028607 | 0.028607 | 0.97321 | -0.51699 | 0.9725 | -0.53101 | 7.8591
54 | -0.023952 | -0.0060081 | 0.023958 | 0.0060117 | 5.7836e-06 | 3.5586e-06 | 0.036624 | 0.036624 | 0.036624 | 0.97321 | -0.51699 | 0.97347 | -0.51193 | 10.0615
55 | -0.24613 | -0.062693 | 0.24678 | 0.063111 | 0.00065487 | 0.00041762 | 0.36899 | 0.36898 | 0.36899 | 0.99354 | -0.12273 | 0.99643 | -0.06773 | 33.7898
56 | 0.13119 | 0.03332 | -0.13106 | -0.033238 | 0.00012873 | 8.2275e-05 | 0.19831 | 0.19831 | 0.19831 | 0.98514 | -0.2839 | 0.98409 | -0.30431 | 54.4805
57 | -0.19028 | -0.048364 | 0.19041 | 0.048445 | 0.00012756 | 8.1152e-05 | 0.28516 | 0.28516 | 0.28516 | 0.99375 | -0.1188 | 0.99448 | -0.10489 | 26.1134
58 | 0.0065195 | 0.0016337 | -0.0065189 | -0.0016336 | 5.5965e-07 | 1.553e-07 | 0.009762 | 0.0097621 | 0.0097621 | 0.99375 | -0.1188 | 0.99366 | -0.1206 | 2.6819
59 | 0.15846 | 0.040329 | -0.15805 | -0.040069 | 0.00040921 | 0.00026089 | 0.23769 | 0.23769 | 0.23769 | 0.99291 | -0.135 | 0.99011 | -0.18871 | 32.65
60 | 0.01217 | 0.0030507 | -0.012168 | -0.0030496 | 2.0512e-06 | 1.1007e-06 | 0.01825 | 0.01825 | 0.01825 | 0.99232 | -0.14653 | 0.99214 | -0.15007 | 5.0138
61 | 0.014829 | 0.0037176 | -0.014827 | -0.0037159 | 2.9234e-06 | 1.6831e-06 | 0.022691 | 0.022691 | 0.022691 | 0.9725 | -0.53101 | 0.97229 | -0.53515 | 6.2338
62 | 0.0060823 | 0.0015244 | -0.0060821 | -0.0015243 | 1.6942e-07 | 3.832e-08 | 0.0091223 | 0.0091223 | 0.0091223 | 0.99214 | -0.15007 | 0.99211 | -0.15065 | 2.5061
63 | 0.006086 | 0.0015253 | -0.0060855 | -0.0015252 | 4.6694e-07 | 1.0586e-07 | 0.0091278 | 0.0091279 | 0.0091279 | 0.99214 | -0.15007 | 0.99205 | -0.15168 | 2.5077
64 | -0.19432 | -0.049426 | 0.19438 | 0.049462 | 5.7707e-05 | 3.672e-05 | 0.29101 | 0.29101 | 0.29101 | 0.99448 | -0.10489 | 0.9948 | -0.098731 | 26.6496
65 | 0.0039136 | 0.00098025 | -0.0039135 | -0.00098028 | 9.5135e-08 | -3.5109e-08 | 0.0058557 | 0.0058557 | 0.0058557 | 0.99448 | -0.10489 | 0.99446 | -0.1054 | 1.6087
66 | 0.003202 | 0.00080226 | -0.0032018 | -0.00080245 | 2.2123e-07 | -1.9075e-07 | 0.004795 | 0.0047951 | 0.0047951 | 0.99366 | -0.1206 | 0.99359 | -0.12205 | 1.3173
67 | 0.12137 | 0.030847 | -0.12119 | -0.03073 | 0.00018299 | 0.00011693 | 0.18256 | 0.18256 | 0.18256 | 0.99011 | -0.18871 | 0.98848 | -0.22007 | 50.153
68 | 0.036679 | 0.0092214 | -0.036656 | -0.0092069 | 2.3037e-05 | 1.4484e-05 | 0.055135 | 0.055135 | 0.055135 | 0.99011 | -0.18871 | 0.98943 | -0.20188 | 15.147
69 | 0.0078948 | 0.0019794 | -0.0078922 | -0.0019784 | 2.5612e-06 | 1.0246e-06 | 0.011909 | 0.011909 | 0.011909 | 0.98646 | -0.25905 | 0.98611 | -0.26586 | 3.2718
70 | -0.013699 | -0.003434 | 0.013701 | 0.0034355 | 2.6477e-06 | 1.4834e-06 | 0.020664 | 0.020664 | 0.020664 | 0.98646 | -0.25905 | 0.98667 | -0.25499 | 5.6769
71 | 0.0078922 | 0.0019784 | -0.0078918 | -0.0019782 | 4.4199e-07 | 1.7686e-07 | 0.011909 | 0.011909 | 0.011909 | 0.98611 | -0.26586 | 0.98605 | -0.26703 | 3.2718
72 | -0.11208 | -0.028373 | 0.11215 | 0.028416 | 6.7024e-05 | 4.2816e-05 | 0.16913 | 0.16913 | 0.16913 | 0.98667 | -0.25499 | 0.98731 | -0.24254 | 46.4652
73 | 0.09838 | 0.024938 | -0.098299 | -0.024886 | 8.0845e-05 | 5.1616e-05 | 0.14847 | 0.14847 | 0.14847 | 0.98667 | -0.25499 | 0.98578 | -0.27211 | 40.7883
74 | 0.0078918 | 0.0019782 | -0.0078896 | -0.0019773 | 2.224e-06 | 8.9015e-07 | 0.011909 | 0.01191 | 0.01191 | 0.98605 | -0.26703 | 0.98575 | -0.27295 | 3.2719
75 | -0.11668 | -0.029553 | 0.11681 | 0.029633 | 0.00012607 | 8.0544e-05 | 0.17597 | 0.17597 | 0.17597 | 0.98731 | -0.24254 | 0.98848 | -0.22007 | 48.343
76 | 0.093663 | 0.023724 | -0.093535 | -0.023643 | 0.00012808 | 8.1752e-05 | 0.14147 | 0.14147 | 0.14147 | 0.98578 | -0.27211 | 0.98431 | -0.30062 | 38.8659
77 | 0.036656 | 0.0092069 | -0.036603 | -0.0091737 | 5.2883e-05 | 3.325e-05 | 0.055135 | 0.055135 | 0.055135 | 0.98943 | -0.20188 | 0.98787 | -0.23216 | 15.1471
78 | 0.088469 | 0.022373 | -0.088369 | -0.022309 | 0.00010017 | 6.3917e-05 | 0.13381 | 0.13381 | 0.13381 | 0.98431 | -0.30062 | 0.98309 | -0.32425 | 36.7619
79 | 0.010813 | 0.0027105 | -0.010811 | -0.0027096 | 1.6744e-06 | 8.6739e-07 | 0.016507 | 0.016507 | 0.016507 | 0.97472 | -0.48819 | 0.97456 | -0.49144 | 4.535
80 | 0.0044928 | 0.0011259 | -0.0044925 | -0.0011259 | 2.7831e-07 | -1.8515e-08 | 0.0068587 | 0.0068587 | 0.0068587 | 0.97472 | -0.48819 | 0.97466 | -0.48949 | 1.8843
81 | -0.015306 | -0.0038364 | 0.015312 | 0.0038399 | 6.0586e-06 | 3.5085e-06 | 0.023366 | 0.023366 | 0.023366 | 0.97472 | -0.48819 | 0.97514 | -0.47988 | 6.4192
82 | 0.0063933 | 0.0016024 | -0.0063925 | -0.0016021 | 7.8523e-07 | 2.2878e-07 | 0.0097617 | 0.0097618 | 0.0097618 | 0.97456 | -0.49144 | 0.97443 | -0.49402 | 2.6818
83 | -0.019056 | -0.0047782 | 0.01906 | 0.0047807 | 4.3096e-06 | 2.5885e-06 | 0.029079 | 0.029079 | 0.029079 | 0.97514 | -0.47988 | 0.97538 | -0.47514 | 7.9886
84 | 0.005398 | 0.0013528 | -0.0053978 | -0.0013528 | 2.7132e-07 | 3.6232e-08 | 0.0081705 | 0.0081705 | 0.0081705 | 0.98309 | -0.32425 | 0.98304 | -0.32531 | 2.2447
85 | 0.082971 | 0.020956 | -0.082801 | -0.020848 | 0.00016986 | 0.00010835 | 0.12564 | 0.12564 | 0.12564 | 0.98309 | -0.32425 | 0.9809 | -0.36707 | 34.5173
86 | -0.19651 | -0.049998 | 0.19669 | 0.050108 | 0.00017292 | 0.00011004 | 0.29421 | 0.29421 | 0.29421 | 0.9948 | -0.098731 | 0.99576 | -0.080491 | 26.9423
87 | 0.0019068 | 0.00047734 | -0.0019066 | -0.00047785 | 1.4098e-07 | -5.0893e-07 | 0.0028529 | 0.0028532 | 0.0028532 | 0.99446 | -0.1054 | 0.99438 | -0.10695 | 0.78384
88 | -0.19915 | -0.050726 | 0.19916 | 0.050731 | 8.8909e-06 | 5.6589e-06 | 0.29789 | 0.29789 | 0.29789 | 0.99576 | -0.080491 | 0.99581 | -0.079565 | 27.2796
89 | -0.20036 | -0.051031 | 0.20044 | 0.051083 | 8.173e-05 | 5.2023e-05 | 0.29968 | 0.29968 | 0.29968 | 0.99581 | -0.079565 | 0.99625 | -0.071112 | 27.4434
90 | -0.20163 | -0.051382 | 0.20176 | 0.051463 | 0.00012804 | 8.1505e-05 | 0.30146 | 0.30146 | 0.30146 | 0.99625 | -0.071112 | 0.99694 | -0.057962 | 27.6061
91 | -0.20336 | -0.051863 | 0.20339 | 0.051886 | 3.5958e-05 | 2.2891e-05 | 0.30384 | 0.30384 | 0.30384 | 0.99694 | -0.057962 | 0.99714 | -0.054301 | 27.8243
92 | -0.20467 | -0.052207 | 0.20474 | 0.052253 | 7.1835e-05 | 4.5734e-05 | 0.30575 | 0.30575 | 0.30575 | 0.99714 | -0.054301 | 0.99752 | -0.047036 | 27.9992
93 | -0.24856 | -0.063556 | 0.24857 | 0.063561 | 7.4839e-06 | 4.7728e-06 | 0.37164 | 0.37164 | 0.37164 | 0.99643 | -0.06773 | 0.99646 | -0.067107 | 34.0329
94 | -0.25051 | -0.064048 | 0.25072 | 0.064181 | 0.00020751 | 0.00013235 | 0.37454 | 0.37454 | 0.37454 | 0.99646 | -0.067107 | 0.99736 | -0.050001 | 34.2988
95 | 0.04271 | 0.010733 | -0.042701 | -0.010727 | 9.4143e-06 | 5.9445e-06 | 0.063732 | 0.063732 | 0.063732 | 0.99736 | -0.050001 | 0.99712 | -0.05462 | 17.5088
96 | -0.29343 | -0.074913 | 0.29354 | 0.07498 | 0.00010371 | 6.6206e-05 | 0.43827 | 0.43827 | 0.43827 | 0.99736 | -0.050001 | 0.99775 | -0.04269 | 40.135
97 | -0.20612 | -0.052597 | 0.20613 | 0.052606 | 1.4098e-05 | 8.9764e-06 | 0.3078 | 0.3078 | 0.3078 | 0.99752 | -0.047036 | 0.99759 | -0.04562 | 28.1869
98 | -0.2079 | -0.053048 | 0.20807 | 0.053157 | 0.00017028 | 0.00010843 | 0.31043 | 0.31043 | 0.31043 | 0.99759 | -0.04562 | 0.99849 | -0.028679 | 28.4279
99 | -0.20988 | -0.053612 | 0.20993 | 0.053643 | 4.9074e-05 | 3.1251e-05 | 0.31314 | 0.31314 | 0.31314 | 0.99849 | -0.028679 | 0.99874 | -0.023844 | 28.6757
100 | -0.21193 | -0.054143 | 0.21197 | 0.05417 | 4.1625e-05 | 2.6509e-05 | 0.31611 | 0.31611 | 0.31611 | 0.99874 | -0.023844 | 0.99896 | -0.019783 | 28.948
101 | -0.21377 | -0.054621 | 0.21383 | 0.054662 | 6.3388e-05 | 4.0372e-05 | 0.3188 | 0.3188 | 0.3188 | 0.99896 | -0.019783 | 0.99928 | -0.013653 | 29.1937
102 | -0.21577 | -0.055147 | 0.21591 | 0.055238 | 0.00014258 | 9.082e-05 | 0.32168 | 0.32168 | 0.32168 | 0.99928 | -0.013653 | 1 | 0 | 29.4578
103 | 0.30243 | 0.077447 | -0.30237 | -0.077409 | 6.0465e-05 | 3.8604e-05 | 0.4506 | 0.4506 | 0.4506 | 1 | 0 | 0.99978 | -0.0041281 | 41.264
104 | 0.30061 | 0.076967 | -0.30042 | -0.07685 | 0.00018408 | 0.00011753 | 0.44798 | 0.44798 | 0.44798 | 0.99978 | -0.0041281 | 0.99911 | -0.01678 | 41.0239
105 | 0.29845 | 0.076356 | -0.29838 | -0.076309 | 7.3758e-05 | 4.7088e-05 | 0.44505 | 0.44505 | 0.44505 | 0.99911 | -0.01678 | 0.99884 | -0.021886 | 40.7554
106 | 0.29609 | 0.075736 | -0.29579 | -0.075546 | 0.0002978 | 0.00019011 | 0.44164 | 0.44164 | 0.44164 | 0.99884 | -0.021886 | 0.99775 | -0.04269 | 40.4434
107 | 0.040384 | 0.010146 | -0.040369 | -0.010137 | 1.5017e-05 | 9.4674e-06 | 0.060274 | 0.060274 | 0.060274 | 0.99712 | -0.05462 | 0.99672 | -0.062414 | 16.5588
108 | 0.038435 | 0.0096519 | -0.038434 | -0.009651 | 1.4674e-06 | 9.2365e-07 | 0.057387 | 0.057387 | 0.057387 | 0.99672 | -0.062414 | 0.99667 | -0.063215 | 15.7657
109 | 0.036106 | 0.0090676 | -0.036096 | -0.0090615 | 9.7155e-06 | 6.1018e-06 | 0.053912 | 0.053912 | 0.053912 | 0.99667 | -0.063215 | 0.99638 | -0.068856 | 14.8109
110 | -0.0077139 | -0.0019333 | 0.0077147 | 0.0019336 | 8.4908e-07 | 3.3477e-07 | 0.011703 | 0.011703 | 0.011703 | 0.98078 | -0.36938 | 0.9809 | -0.36707 | 3.2152
111 | 0.0080141 | 0.0020088 | -0.0080121 | -0.002008 | 1.9533e-06 | 8.0539e-07 | 0.012157 | 0.012158 | 0.012158 | 0.9809 | -0.36707 | 0.98064 | -0.37219 | 3.34
112 | 0.067072 | 0.016905 | -0.067053 | -0.016893 | 1.8826e-05 | 1.1988e-05 | 0.10178 | 0.10178 | 0.10178 | 0.9809 | -0.36707 | 0.9806 | -0.37294 | 27.9622
113 | 0.060115 | 0.015154 | -0.060064 | -0.015123 | 5.0146e-05 | 3.1891e-05 | 0.091253 | 0.091253 | 0.091253 | 0.9806 | -0.37294 | 0.9797 | -0.39038 | 25.0696
114 | 0.054812 | 0.013806 | -0.054789 | -0.013791 | 2.2954e-05 | 1.458e-05 | 0.083275 | 0.083275 | 0.083275 | 0.9797 | -0.39038 | 0.97925 | -0.39915 | 22.8777
115 | -0.042487 | -0.010669 | 0.042502 | 0.010678 | 1.4163e-05 | 8.9513e-06 | 0.064713 | 0.064713 | 0.064713 | 0.97707 | -0.44189 | 0.97743 | -0.43491 | 17.7782
116 | 0.036332 | 0.0091264 | -0.036324 | -0.0091213 | 8.1346e-06 | 5.1174e-06 | 0.055339 | 0.055339 | 0.055339 | 0.97707 | -0.44189 | 0.97684 | -0.44658 | 15.203
117 | -0.047606 | -0.011957 | 0.047639 | 0.011978 | 3.3064e-05 | 2.0951e-05 | 0.072483 | 0.072483 | 0.072483 | 0.97743 | -0.43491 | 0.97817 | -0.42036 | 19.9129
118 | 0.030892 | 0.0077599 | -0.030866 | -0.0077433 | 2.6545e-05 | 1.6589e-05 | 0.047064 | 0.047064 | 0.047064 | 0.97684 | -0.44658 | 0.97592 | -0.46461 | 12.9298
119 | -0.054733 | -0.013756 | 0.054789 | 0.013791 | 5.5501e-05 | 3.5253e-05 | 0.083275 | 0.083275 | 0.083275 | 0.97817 | -0.42036 | 0.97925 | -0.39915 | 22.8778
120 | 0.024652 | 0.0061823 | -0.02465 | -0.0061815 | 1.3386e-06 | 8.2257e-07 | 0.036855 | 0.036855 | 0.036855 | 0.99534 | -0.08888 | 0.99528 | -0.090019 | 10.125
121 | -0.026601 | -0.0066709 | 0.026608 | 0.0066754 | 7.2326e-06 | 4.4703e-06 | 0.03977 | 0.039769 | 0.03977 | 0.99534 | -0.08888 | 0.99564 | -0.083177 | 10.9257
122 | 0.022207 | 0.0055693 | -0.022205 | -0.0055678 | 2.4609e-06 | 1.4976e-06 | 0.033203 | 0.033203 | 0.033203 | 0.99528 | -0.090019 | 0.99516 | -0.092345 | 9.1217
123 | -0.028532 | -0.0071576 | 0.028536 | 0.0071602 | 4.0631e-06 | 2.5229e-06 | 0.042645 | 0.042645 | 0.042645 | 0.99564 | -0.083177 | 0.99579 | -0.08019 | 11.7157
124 | 0.02067 | 0.0051831 | -0.020669 | -0.0051825 | 9.2859e-07 | 5.6062e-07 | 0.030907 | 0.030907 | 0.030907 | 0.99516 | -0.092345 | 0.99512 | -0.093287 | 8.4911
125 | -0.03055 | -0.0076649 | 0.030553 | 0.0076664 | 2.4248e-06 | 1.5115e-06 | 0.045654 | 0.045654 | 0.045654 | 0.99579 | -0.08019 | 0.99588 | -0.078526 | 12.5424
126 | 0.018268 | 0.0045808 | -0.018265 | -0.0045789 | 3.2037e-06 | 1.9016e-06 | 0.027318 | 0.027318 | 0.027318 | 0.99512 | -0.093287 | 0.99492 | -0.096968 | 7.5049
127 | -0.032273 | -0.0080975 | 0.032277 | 0.0081003 | 4.4176e-06 | 2.7613e-06 | 0.048224 | 0.048224 | 0.048224 | 0.99588 | -0.078526 | 0.99603 | -0.075655 | 13.2485
128 | 0.016772 | 0.0042048 | -0.016771 | -0.0042038 | 1.7893e-06 | 1.0467e-06 | 0.025085 | 0.025085 | 0.025085 | 0.99492 | -0.096968 | 0.99481 | -0.099207 | 6.8916
129 | -0.034116 | -0.008561 | 0.034127 | 0.0085679 | 1.1066e-05 | 6.9341e-06 | 0.050971 | 0.050971 | 0.050971 | 0.99603 | -0.075655 | 0.99638 | -0.068856 | 14.003

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.52245 | 0.1333

## res_load
| p_mw | q_mvar
0 | 0.0047553 | 0.0011918
1 | 0.0044624 | 0.0011184
2 | 0.0392 | 0.0098245
3 | 0.0022656 | 0.00056781
4 | 0.0070245 | 0.0017605
5 | 0.019607 | 0.0049139
6 | 0.0080415 | 0.0020154
7 | 0.010018 | 0.0025108
8 | 0.0044579 | 0.0011173
9 | 0.0099703 | 0.0024988
10 | 0.015399 | 0.0038593
11 | 0.0042166 | 0.0010568
12 | 0.0042937 | 0.0010761
13 | 0.007881 | 0.0019752
14 | 0.0079776 | 0.0019994
15 | 0.0043261 | 0.0010842
16 | 0.0073479 | 0.0018415
17 | 0.0070141 | 0.0017579
18 | 0.0075021 | 0.0018802
19 | 0.007825 | 0.0019611
20 | 0.0033773 | 0.00084642
21 | 0.004421 | 0.001108
22 | 0.0059909 | 0.0015015
23 | 0.0020531 | 0.00051456
24 | 0.01306 | 0.0032733
25 | 0.0080341 | 0.0020135
26 | 0.0051932 | 0.0013015
27 | 0.0052427 | 0.0013139
28 | 0.0060415 | 0.0015141
29 | 0.0038879 | 0.0009744
30 | 0.0047121 | 0.001181
31 | 0.002128 | 0.00053333
32 | 0.0065215 | 0.0016344
33 | 0.0038667 | 0.00096908
34 | 0.014827 | 0.0037159
35 | 0.0060821 | 0.0015243
36 | 0.0060855 | 0.0015252
37 | 0.0033169 | 0.00083129
38 | 0.0058039 | 0.0014546
39 | 0.0045354 | 0.0011367
40 | 0.004636 | 0.0011619
41 | 0.0078896 | 0.0019773
42 | 0.036603 | 0.0091737
43 | 0.0043766 | 0.0010969
44 | 0.005066 | 0.0012697
45 | 0.0044179 | 0.0011072
46 | 0.0044925 | 0.0011259
47 | 0.0037438 | 0.00093829
48 | 0.0021367 | 0.00053551
49 | 0.0020068 | 0.00050294
50 | 0.0032018 | 0.00080245
51 | 0.0019066 | 0.00047785
52 | 0.0024653 | 0.00061786
53 | 0.0011969 | 0.00029998
54 | 0.00119 | 0.00029825
55 | 0.0015965 | 0.00040011
56 | 0.0012797 | 0.00032073
57 | 0.004646 | 0.0011644
58 | 0.0017775 | 0.00044549
59 | 0.0019448 | 0.00048741
60 | 0.0013743 | 0.00034444
61 | 0.0017642 | 0.00044214
62 | 0.0018157 | 0.00045505
63 | 0.0019963 | 0.00050031
64 | 0.0018011 | 0.00045141
65 | 0.0019369 | 0.00048544
66 | 0.0024556 | 0.00061543
67 | 0.0017615 | 0.00044147
68 | 0.0019688 | 0.00049344
69 | 0.0022874 | 0.00057328
70 | 0.002258 | 0.00056592
71 | 0.0023172 | 0.00058074
72 | 0.0019338 | 0.00048465
73 | 0.0023278 | 0.00058341
74 | 0.0077139 | 0.0019333
75 | 0.0080121 | 0.002008
76 | 0.0069387 | 0.001739
77 | 0.0052529 | 0.0013165
78 | 0.0053978 | 0.0013528
79 | 0.0063925 | 0.0016021
80 | 0.0061552 | 0.0015426
81 | 0.005104 | 0.0012792
82 | 0.005432 | 0.0013614
83 | 0.0070944 | 0.001778
84 | 0.0058037 | 0.0014545
85 | 0.0019496 | 0.00048862
86 | 0.0024427 | 0.00061221
87 | 0.0019241 | 0.00048222
88 | 0.0015352 | 0.00038475
89 | 0.0020137 | 0.00050469
90 | 0.0024007 | 0.00060166
91 | 0.0017202 | 0.00043113
92 | 0.0014927 | 0.0003741
93 | 0.0018383 | 0.00046073
94 | 0.0019693 | 0.00049356
95 | 0.0016546 | 0.00041467

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1