## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-16_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-16_0_3_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_261-16_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_261-16_0_3_node_7 | 0.4 | n |  | TRUE
4 | bus_LV_261-16_0_3_node_30 | 0.4 | n |  | TRUE
5 | bus_LV_261-16_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-16_0_3_node_20 | 0.4 | n |  | TRUE
7 | bus_LV_261-16_0_3_node_27 | 0.4 | n |  | TRUE
8 | bus_LV_261-16_0_3_node_25 | 0.4 | n |  | TRUE
9 | bus_LV_261-16_0_3_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_261-16_0_3_node_46 | 0.4 | n |  | TRUE
11 | bus_LV_261-16_0_3_node_44 | 0.4 | n |  | TRUE
12 | bus_LV_261-16_0_3_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_261-16_0_3_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_261-16_0_3_node_34 | 0.4 | n |  | TRUE
15 | bus_LV_261-16_0_3_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_261-16_0_3_node_32 | 0.4 | n |  | TRUE
17 | bus_LV_261-16_0_3_node_31 | 0.4 | n |  | TRUE
18 | bus_LV_261-16_0_3_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_261-16_0_3_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_261-16_0_3_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_261-16_0_3_node_41 | 0.4 | n |  | TRUE
22 | bus_LV_261-16_0_3_node_43 | 0.4 | n |  | TRUE
23 | bus_LV_261-16_0_3_node_42 | 0.4 | n |  | TRUE
24 | bus_LV_261-16_0_3_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_261-16_0_3_node_33 | 0.4 | n |  | TRUE
26 | bus_LV_261-16_0_3_node_45 | 0.4 | n |  | TRUE
27 | bus_LV_261-16_0_3_node_38 | 0.4 | n |  | TRUE
28 | bus_LV_261-16_0_3_node_39 | 0.4 | n |  | TRUE
29 | bus_LV_261-16_0_3_node_40 | 0.4 | n |  | TRUE
30 | bus_LV_261-16_0_3_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_261-16_0_3_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_261-16_0_3_node_36 | 0.4 | n |  | TRUE
33 | bus_LV_261-16_0_3_node_35 | 0.4 | n |  | TRUE
34 | bus_LV_261-16_0_3_node_37 | 0.4 | n |  | TRUE
35 | bus_LV_261-16_0_3_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_261-16_0_3_node_24 | 0.4 | n |  | TRUE
37 | bus_LV_261-16_0_3_node_26 | 0.4 | n |  | TRUE
38 | bus_MV_537_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-16_0_3_load_0 | 0 | 0.014175 | 0.0035525 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-16_0_3_load_30 | 4 | 0.0065785 | 0.0016487 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-16_0_3_load_27 | 7 | 0.018131 | 0.0045439 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-16_0_3_load_25 | 8 | 0.013037 | 0.0032674 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-16_0_3_load_46 | 10 | 0.022322 | 0.0055944 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-16_0_3_load_44 | 11 | 0.032981 | 0.0082658 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-16_0_3_load_34 | 14 | 0.011692 | 0.0029303 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-16_0_3_load_32 | 16 | 0.014842 | 0.0037198 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-16_0_3_load_31 | 17 | 0.01873 | 0.0046941 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-16_0_3_load_41 | 21 | 0.015323 | 0.0038402 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-16_0_3_load_43 | 22 | 0.012519 | 0.0031374 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-16_0_3_load_42 | 23 | 0.019358 | 0.0048515 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-16_0_3_load_33 | 25 | 0.010938 | 0.0027413 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-16_0_3_load_45 | 26 | 0.031189 | 0.0078168 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-16_0_3_load_38 | 27 | 0.017217 | 0.004315 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-16_0_3_load_39 | 28 | 0.016378 | 0.0041046 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-16_0_3_load_40 | 29 | 0.012878 | 0.0032274 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-16_0_3_load_29 | 30 | 0.0091442 | 0.0022917 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-16_0_3_load_23 | 31 | 0.0091813 | 0.002301 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-16_0_3_load_36 | 32 | 0.011611 | 0.00291 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-16_0_3_load_35 | 33 | 0.0096199 | 0.002411 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-16_0_3_load_37 | 34 | 0.022464 | 0.00563 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-16_0_3_load_28 | 35 | 0.014318 | 0.0035884 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-16_0_3_load_24 | 36 | 0.011504 | 0.0028832 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 28 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-16_0_3_line_0 |  | 0 | 1 | 0.049265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-16_0_3_line_1 |  | 1 | 2 | 0.051481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-16_0_3_line_2 |  | 2 | 3 | 0.045994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-16_0_3_line_3 |  | 2 | 4 | 0.034096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-16_0_3_line_4 |  | 3 | 8 | 0.044723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-16_0_3_line_5 |  | 5 | 6 | 0.008769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-16_0_3_line_6 |  | 5 | 7 | 0.012329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-16_0_3_line_7 |  | 6 | 26 | 0.02769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-16_0_3_line_8 |  | 7 | 8 | 0.011721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-16_0_3_line_9 |  | 8 | 31 | 0.0089602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-16_0_3_line_10 |  | 9 | 10 | 0.016846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-16_0_3_line_11 |  | 9 | 11 | 0.0033744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-16_0_3_line_12 |  | 10 | 21 | 0.017022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-16_0_3_line_13 |  | 12 | 13 | 0.010102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-16_0_3_line_14 |  | 12 | 14 | 0.023581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-16_0_3_line_15 |  | 13 | 24 | 0.0091543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-16_0_3_line_16 |  | 13 | 25 | 0.014033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-16_0_3_line_17 |  | 14 | 18 | 0.0074208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-16_0_3_line_18 |  | 15 | 16 | 0.027039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-16_0_3_line_19 |  | 15 | 17 | 0.01612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-16_0_3_line_20 |  | 16 | 18 | 0.0056378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-16_0_3_line_21 |  | 19 | 20 | 0.025678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-16_0_3_line_22 |  | 19 | 21 | 0.005231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-16_0_3_line_23 |  | 20 | 22 | 0.0070515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-16_0_3_line_24 |  | 20 | 23 | 0.0095621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-16_0_3_line_25 |  | 21 | 24 | 0.022468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-16_0_3_line_26 |  | 24 | 27 | 0.015089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-16_0_3_line_27 |  | 24 | 28 | 0.013852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_261-16_0_3_line_28 |  | 27 | 34 | 0.023943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-16_0_3_line_29 |  | 28 | 35 | 0.01777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-16_0_3_line_30 |  | 29 | 30 | 0.023398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-16_0_3_line_31 |  | 30 | 37 | 0.028596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-16_0_3_line_32 |  | 31 | 36 | 0.01112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-16_0_3_line_33 |  | 32 | 33 | 0.011489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-16_0_3_line_34 |  | 33 | 34 | 0.020052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-16_0_3_line_35 |  | 35 | 37 | 0.015017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-16_0_3_line_36 |  | 36 | 37 | 0.0092457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-16_0_3_trafo_39 | 0.63 MVA 20/0.4 kV | 38 | 28 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2683281.1289 | 1249132.4449 | 2683290.3878 | 1249120.0324 | 2683307.9025 | 1249128.418 | 2683302.2139 | 1249141.604
1 | 2683238.1665 | 1249112.727 | 2683238.5274 | 1249111.7646 | 2683241.5457 | 1249112.9968 | 2683263.1526 | 1249123.5858 | 2683262.9093 | 1249125.317 | 2683264.274 | 1249127.6157 | 2683266.576 | 1249128.2374 | 2683268.4372 | 1249127.4518 | 2683269.2103 | 1249126.7066 | 2683273.1763 | 1249128.7527 | 2683281.1289 | 1249132.4449
2 | 2683228.6028 | 1249079.1122 | 2683234.6023 | 1249087.4582 | 2683237.1125 | 1249089.3837 | 2683228.0213 | 1249109.2153 | 2683232.8234 | 1249110.8728 | 2683238.1665 | 1249112.727
3 | 2683238.1665 | 1249112.727 | 2683228.1681 | 1249140.1625 | 2683226.8763 | 1249144.8844
4 | 2683200.5575 | 1249109.6968 | 2683211.3783 | 1249107.0356 | 2683217.109 | 1249102.8018 | 2683222.457 | 1249095.1601 | 2683228.6028 | 1249079.1122
5 | 2683197.4406 | 1249142.3662 | 2683198.273 | 1249133.6381
6 | 2683198.273 | 1249133.6381 | 2683199.4441 | 1249121.3651
7 | 2683197.4406 | 1249142.3662 | 2683169.6761 | 1249141.6872
8 | 2683200.5575 | 1249109.6968 | 2683199.4441 | 1249121.3651
9 | 2683200.5575 | 1249109.6968 | 2683201.4072 | 1249100.777
10 | 2683135.1866 | 1249115.473 | 2683142.8157 | 1249100.4534
11 | 2683135.1866 | 1249115.473 | 2683134.1596 | 1249118.6874
12 | 2683150.5245 | 1249085.2768 | 2683142.8157 | 1249100.4534
13 | 2683150.8648 | 1249061.5641 | 2683147.5977 | 1249060.2951 | 2683141.4554 | 1249057.8182
14 | 2683141.4554 | 1249057.8182 | 2683144.0015 | 1249034.3753
15 | 2683159.4048 | 1249064.8529 | 2683154.6937 | 1249063.1634 | 2683150.8648 | 1249061.5641
16 | 2683150.8648 | 1249061.5641 | 2683156.6839 | 1249048.7944
17 | 2683144.8028 | 1249026.9979 | 2683144.0015 | 1249034.3753
18 | 2683148.3322 | 1248994.5122 | 2683145.4117 | 1249021.3931
19 | 2683148.3322 | 1248994.5122 | 2683162.8961 | 1249001.4209
20 | 2683144.8028 | 1249026.9979 | 2683145.4117 | 1249021.3931
21 | 2683124.1468 | 1249076.1558 | 2683128.7311 | 1249076.6537 | 2683130.6236 | 1249076.8582 | 2683131.717 | 1249076.9736 | 2683139.2797 | 1249077.7914 | 2683138.9329 | 1249080.9778 | 2683141.6183 | 1249081.1822 | 2683145.76 | 1249083.0862
22 | 2683145.76 | 1249083.0862 | 2683150.5245 | 1249085.2768
23 | 2683124.1468 | 1249076.1558 | 2683123.5388 | 1249083.1811
24 | 2683124.1468 | 1249076.1558 | 2683125.0867 | 1249066.64
25 | 2683159.4048 | 1249064.8529 | 2683157.8508 | 1249069.5791 | 2683156.2283 | 1249071.113 | 2683150.5245 | 1249085.2768
26 | 2683159.4048 | 1249064.8529 | 2683161.069 | 1249059.8059 | 2683165.049 | 1249050.8783
27 | 2683159.4048 | 1249064.8529 | 2683172.4535 | 1249069.5012
28 | 2683165.049 | 1249050.8783 | 2683173.0842 | 1249032.8544 | 2683174.8168 | 1249029.0188
29 | 2683189.1928 | 1249075.4641 | 2683172.4535 | 1249069.5012
30 | 2683208.2793 | 1249028.7452 | 2683206.0559 | 1249052.0369
31 | 2683203.3386 | 1249080.5031 | 2683206.0559 | 1249052.0369
32 | 2683201.4072 | 1249100.777 | 2683202.4618 | 1249089.7071
33 | 2683187.8011 | 1249000.2738 | 2683183.0713 | 1249010.7446
34 | 2683174.8168 | 1249029.0188 | 2683183.0713 | 1249010.7446
35 | 2683203.3386 | 1249080.5031 | 2683189.1928 | 1249075.4641
36 | 2683203.3386 | 1249080.5031 | 2683202.4618 | 1249089.7071

## bus_geodata
| x | y | coords
0 | 2683302.2139 | 1249141.604
1 | 2683281.1289 | 1249132.4449
2 | 2683238.1665 | 1249112.727
3 | 2683228.6028 | 1249079.1122
4 | 2683226.8763 | 1249144.8844
5 | 2683198.273 | 1249133.6381
6 | 2683197.4406 | 1249142.3662
7 | 2683199.4441 | 1249121.3651
8 | 2683200.5575 | 1249109.6968
9 | 2683135.1866 | 1249115.473
10 | 2683142.8157 | 1249100.4534
11 | 2683134.1596 | 1249118.6874
12 | 2683141.4554 | 1249057.8182
13 | 2683150.8648 | 1249061.5641
14 | 2683144.0015 | 1249034.3753
15 | 2683148.3322 | 1248994.5122
16 | 2683145.4117 | 1249021.3931
17 | 2683162.8961 | 1249001.4209
18 | 2683144.8028 | 1249026.9979
19 | 2683145.76 | 1249083.0862
20 | 2683124.1468 | 1249076.1558
21 | 2683150.5245 | 1249085.2768
22 | 2683123.5388 | 1249083.1811
23 | 2683125.0867 | 1249066.64
24 | 2683159.4047 | 1249064.8529
25 | 2683156.6839 | 1249048.7944
26 | 2683169.6761 | 1249141.6872
27 | 2683165.049 | 1249050.8783
28 | 2683172.4535 | 1249069.5012
29 | 2683208.2793 | 1249028.7452
30 | 2683206.0559 | 1249052.0369
31 | 2683201.4072 | 1249100.777
32 | 2683187.8011 | 1249000.2738
33 | 2683183.0713 | 1249010.7446
34 | 2683174.8168 | 1249029.0188
35 | 2683189.1928 | 1249075.4641
36 | 2683202.4618 | 1249089.7071
37 | 2683203.3386 | 1249080.5031
38 | 2683159.4047 | 1249064.8529

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99048 | -0.1834 | 0.014175 | 0.0035525
1 | 0.99111 | -0.171 | 0 | 0
2 | 0.99178 | -0.15806 | 0 | 0
3 | 0.99266 | -0.14116 | 0 | 0
4 | 0.99158 | -0.16203 | 0.0065785 | 0.0016487
5 | 0.99263 | -0.14176 | 0 | 0
6 | 0.99238 | -0.1466 | 0 | 0
7 | 0.99298 | -0.13496 | 0.018131 | 0.0045439
8 | 0.99351 | -0.12475 | 0.013037 | 0.0032674
9 | 0.99515 | -0.093196 | 0 | 0
10 | 0.99566 | -0.083423 | 0.022322 | 0.0055944
11 | 0.99505 | -0.095155 | 0.032981 | 0.0082658
12 | 0.99773 | -0.043549 | 0 | 0
13 | 0.99815 | -0.035546 | 0 | 0
14 | 0.99676 | -0.062256 | 0.011692 | 0.0029303
15 | 0.9959 | -0.078846 | 0 | 0
16 | 0.99636 | -0.069951 | 0.014842 | 0.0037198
17 | 0.99562 | -0.084154 | 0.01873 | 0.0046941
18 | 0.99653 | -0.066628 | 0 | 0
19 | 0.99637 | -0.069813 | 0 | 0
20 | 0.99562 | -0.084195 | 0 | 0
21 | 0.99652 | -0.066886 | 0.015323 | 0.0038402
22 | 0.99554 | -0.085747 | 0.012519 | 0.0031374
23 | 0.99545 | -0.08745 | 0.019358 | 0.0048515
24 | 0.99862 | -0.026549 | 0 | 0
25 | 0.99801 | -0.038232 | 0.010938 | 0.0027413
26 | 0.99159 | -0.1619 | 0.031189 | 0.0078168
27 | 0.99778 | -0.042627 | 0.017217 | 0.004315
28 | 1 | 0 | -0.36301 | -0.091184
29 | 0.99515 | -0.093018 | 0.012878 | 0.0032274
30 | 0.99543 | -0.087717 | 0.0091442 | 0.0022917
31 | 0.99419 | -0.11161 | 0.0091813 | 0.002301
32 | 0.99632 | -0.070773 | 0.011611 | 0.00291
33 | 0.99644 | -0.068431 | 0.0096199 | 0.002411
34 | 0.99683 | -0.06096 | 0.022464 | 0.00563
35 | 0.99773 | -0.043505 | 0.014318 | 0.0035884
36 | 0.99512 | -0.093523 | 0.011504 | 0.0028832
37 | 0.996 | -0.076646 | 0 | 0
38 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.014175 | -0.0035525 | 0.014183 | 0.0035573 | 8.3777e-06 | 4.7272e-06 | 0.021295 | 0.021295 | 0.021295 | 0.99048 | -0.1834 | 0.99111 | -0.171 | 5.8503
1 | -0.014183 | -0.0035573 | 0.014192 | 0.0035622 | 8.7543e-06 | 4.9389e-06 | 0.021295 | 0.021295 | 0.021295 | 0.99111 | -0.171 | 0.99178 | -0.15806 | 5.8503
2 | -0.020772 | -0.0052113 | 0.020788 | 0.0052214 | 1.6754e-05 | 1.0128e-05 | 0.031167 | 0.031166 | 0.031167 | 0.99178 | -0.15806 | 0.99266 | -0.14116 | 8.5622
3 | 0.0065797 | 0.0016491 | -0.0065785 | -0.0016487 | 1.2461e-06 | 3.5758e-07 | 0.0098719 | 0.009872 | 0.009872 | 0.99178 | -0.15806 | 0.99158 | -0.16203 | 2.7121
4 | -0.020788 | -0.0052214 | 0.020805 | 0.0052313 | 1.629e-05 | 9.8472e-06 | 0.031166 | 0.031166 | 0.031166 | 0.99266 | -0.14116 | 0.99351 | -0.12475 | 8.5622
5 | 0.031219 | 0.0078355 | -0.031212 | -0.007831 | 7.2035e-06 | 4.4969e-06 | 0.046804 | 0.046804 | 0.046804 | 0.99263 | -0.14176 | 0.99238 | -0.1466 | 12.8582
6 | -0.031219 | -0.0078355 | 0.031229 | 0.0078418 | 1.0128e-05 | 6.3223e-06 | 0.046804 | 0.046804 | 0.046804 | 0.99263 | -0.14176 | 0.99298 | -0.13496 | 12.8582
7 | 0.031212 | 0.007831 | -0.031189 | -0.0078168 | 2.2747e-05 | 1.42e-05 | 0.046804 | 0.046804 | 0.046804 | 0.99238 | -0.1466 | 0.99159 | -0.1619 | 12.8582
8 | -0.04936 | -0.012386 | 0.049384 | 0.012401 | 2.4052e-05 | 1.5242e-05 | 0.073973 | 0.073973 | 0.073973 | 0.99298 | -0.13496 | 0.99351 | -0.12475 | 20.3223
9 | -0.083226 | -0.0209 | 0.083278 | 0.020933 | 5.222e-05 | 3.3305e-05 | 0.12467 | 0.12467 | 0.12467 | 0.99351 | -0.12475 | 0.99419 | -0.11161 | 34.2487
10 | -0.032984 | -0.0082677 | 0.032999 | 0.0082773 | 1.5366e-05 | 9.6156e-06 | 0.04932 | 0.04932 | 0.04932 | 0.99515 | -0.093196 | 0.99566 | -0.083423 | 13.5494
11 | 0.032984 | 0.0082677 | -0.032981 | -0.0082658 | 3.0781e-06 | 1.9261e-06 | 0.04932 | 0.04932 | 0.04932 | 0.99515 | -0.093196 | 0.99505 | -0.095155 | 13.5494
12 | -0.055321 | -0.013872 | 0.055365 | 0.013899 | 4.3636e-05 | 2.7705e-05 | 0.08268 | 0.08268 | 0.08268 | 0.99566 | -0.083423 | 0.99652 | -0.066886 | 22.7142
13 | -0.045329 | -0.011385 | 0.045347 | 0.011396 | 1.7318e-05 | 1.0951e-05 | 0.067613 | 0.067613 | 0.067613 | 0.99773 | -0.043549 | 0.99815 | -0.035546 | 18.5749
14 | 0.045329 | 0.011385 | -0.045289 | -0.011359 | 4.0425e-05 | 2.5564e-05 | 0.067613 | 0.067613 | 0.067613 | 0.99773 | -0.043549 | 0.99676 | -0.062256 | 18.5749
15 | -0.056286 | -0.014138 | 0.05631 | 0.014153 | 2.4177e-05 | 1.5353e-05 | 0.083921 | 0.083921 | 0.083921 | 0.99815 | -0.035546 | 0.99862 | -0.026549 | 23.0552
16 | 0.010939 | 0.0027421 | -0.010938 | -0.0027413 | 1.3996e-06 | 7.1236e-07 | 0.016308 | 0.016309 | 0.016309 | 0.99815 | -0.035546 | 0.99801 | -0.038232 | 4.4804
17 | 0.033597 | 0.0084292 | -0.03359 | -0.0084248 | 7.0012e-06 | 4.3841e-06 | 0.050158 | 0.050159 | 0.050159 | 0.99676 | -0.062256 | 0.99653 | -0.066628 | 13.7798
18 | -0.018734 | -0.0046969 | 0.018742 | 0.0047016 | 7.9451e-06 | 4.7329e-06 | 0.027992 | 0.027992 | 0.027992 | 0.9959 | -0.078846 | 0.99636 | -0.069951 | 7.6902
19 | 0.018734 | 0.0046969 | -0.01873 | -0.0046941 | 4.7366e-06 | 2.8217e-06 | 0.027992 | 0.027992 | 0.027992 | 0.9959 | -0.078846 | 0.99562 | -0.084154 | 7.6902
20 | -0.033585 | -0.0084215 | 0.03359 | 0.0084248 | 5.319e-06 | 3.3307e-06 | 0.050159 | 0.050159 | 0.050159 | 0.99636 | -0.069951 | 0.99653 | -0.066628 | 13.7798
21 | 0.031902 | 0.0080049 | -0.03188 | -0.0079912 | 2.1861e-05 | 1.3657e-05 | 0.047647 | 0.047647 | 0.047647 | 0.99637 | -0.069813 | 0.99562 | -0.084195 | 13.0899
22 | -0.031902 | -0.0080049 | 0.031906 | 0.0080076 | 4.4533e-06 | 2.782e-06 | 0.047647 | 0.047647 | 0.047647 | 0.99637 | -0.069813 | 0.99652 | -0.066886 | 13.0898
23 | 0.012519 | 0.0031379 | -0.012519 | -0.0031374 | 9.2581e-07 | 5.0082e-07 | 0.018711 | 0.018711 | 0.018711 | 0.99562 | -0.084195 | 0.99554 | -0.085747 | 5.1404
24 | 0.019361 | 0.0048533 | -0.019358 | -0.0048515 | 3.0023e-06 | 1.7972e-06 | 0.028936 | 0.028936 | 0.028936 | 0.99562 | -0.084195 | 0.99545 | -0.08745 | 7.9494
25 | -0.10259 | -0.025747 | 0.10279 | 0.025874 | 0.00019777 | 0.00012628 | 0.15321 | 0.15321 | 0.15321 | 0.99652 | -0.066886 | 0.99862 | -0.026549 | 42.0898
26 | 0.061006 | 0.015325 | -0.060959 | -0.015295 | 4.677e-05 | 2.9736e-05 | 0.090916 | 0.090916 | 0.090916 | 0.99862 | -0.026549 | 0.99778 | -0.042627 | 24.9768
27 | -0.22011 | -0.055352 | 0.22039 | 0.05553 | 0.0002795 | 0.00017851 | 0.32804 | 0.32804 | 0.32804 | 0.99862 | -0.026549 | 1 | 0 | 45.0609
28 | 0.043742 | 0.01098 | -0.043704 | -0.010956 | 3.8214e-05 | 2.4145e-05 | 0.06524 | 0.06524 | 0.06524 | 0.99778 | -0.042627 | 0.99683 | -0.06096 | 17.923
29 | 0.14098 | 0.035654 | -0.14068 | -0.035466 | 0.00029355 | 0.00018764 | 0.20989 | 0.20989 | 0.20989 | 1 | 0 | 0.99773 | -0.043505 | 57.6612
30 | -0.012878 | -0.0032274 | 0.012881 | 0.0032292 | 3.2531e-06 | 1.7779e-06 | 0.019255 | 0.019255 | 0.019255 | 0.99515 | -0.093018 | 0.99543 | -0.087717 | 5.2899
31 | -0.022025 | -0.0055209 | 0.022037 | 0.005528 | 1.1624e-05 | 7.0676e-06 | 0.032924 | 0.032924 | 0.032924 | 0.99543 | -0.087717 | 0.996 | -0.076646 | 9.0452
32 | -0.092459 | -0.023234 | 0.092539 | 0.023285 | 7.9883e-05 | 5.0981e-05 | 0.13841 | 0.13841 | 0.13841 | 0.99419 | -0.11161 | 0.99512 | -0.093523 | 38.0239
33 | -0.011611 | -0.00291 | 0.011612 | 0.0029107 | 1.2957e-06 | 6.7958e-07 | 0.017341 | 0.017341 | 0.017341 | 0.99632 | -0.070773 | 0.99644 | -0.068431 | 4.7641
34 | -0.021232 | -0.0053217 | 0.02124 | 0.0053262 | 7.5596e-06 | 4.5768e-06 | 0.031707 | 0.031707 | 0.031707 | 0.99644 | -0.068431 | 0.99683 | -0.06096 | 8.7107
35 | 0.12636 | 0.031878 | -0.12616 | -0.03175 | 0.00020016 | 0.00012791 | 0.18853 | 0.18853 | 0.18853 | 0.99773 | -0.043505 | 0.996 | -0.076646 | 51.7949
36 | -0.10404 | -0.026168 | 0.10413 | 0.026222 | 8.3954e-05 | 5.361e-05 | 0.15561 | 0.15561 | 0.15561 | 0.99512 | -0.093523 | 0.996 | -0.076646 | 42.7497

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.37939 | 0.095289

## res_load
| p_mw | q_mvar
0 | 0.014175 | 0.0035525
1 | 0.0065785 | 0.0016487
2 | 0.018131 | 0.0045439
3 | 0.013037 | 0.0032674
4 | 0.022322 | 0.0055944
5 | 0.032981 | 0.0082658
6 | 0.011692 | 0.0029303
7 | 0.014842 | 0.0037198
8 | 0.01873 | 0.0046941
9 | 0.015323 | 0.0038402
10 | 0.012519 | 0.0031374
11 | 0.019358 | 0.0048515
12 | 0.010938 | 0.0027413
13 | 0.031189 | 0.0078168
14 | 0.017217 | 0.004315
15 | 0.016378 | 0.0041046
16 | 0.012878 | 0.0032274
17 | 0.0091442 | 0.0022917
18 | 0.0091813 | 0.002301
19 | 0.011611 | 0.00291
20 | 0.0096199 | 0.002411
21 | 0.022464 | 0.00563
22 | 0.014318 | 0.0035884
23 | 0.011504 | 0.0028832

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1