## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-172_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-172_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-172_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-172_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-172_0_2_node_21 | 0.4 | n |  | TRUE
5 | bus_LV_261-172_0_2_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_261-172_0_2_node_20 | 0.4 | n |  | TRUE
7 | bus_LV_261-172_0_2_node_25 | 0.4 | n |  | TRUE
8 | bus_LV_261-172_0_2_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_261-172_0_2_node_32 | 0.4 | n |  | TRUE
10 | bus_LV_261-172_0_2_node_31 | 0.4 | n |  | TRUE
11 | bus_LV_261-172_0_2_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_261-172_0_2_node_23 | 0.4 | n |  | TRUE
13 | bus_LV_261-172_0_2_node_22 | 0.4 | n |  | TRUE
14 | bus_LV_261-172_0_2_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_261-172_0_2_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_261-172_0_2_node_27 | 0.4 | n |  | TRUE
17 | bus_LV_261-172_0_2_node_42 | 0.4 | n |  | TRUE
18 | bus_LV_261-172_0_2_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_261-172_0_2_node_37 | 0.4 | n |  | TRUE
20 | bus_LV_261-172_0_2_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_261-172_0_2_node_44 | 0.4 | n |  | TRUE
22 | bus_LV_261-172_0_2_node_41 | 0.4 | n |  | TRUE
23 | bus_LV_261-172_0_2_node_34 | 0.4 | n |  | TRUE
24 | bus_LV_261-172_0_2_node_47 | 0.4 | n |  | TRUE
25 | bus_LV_261-172_0_2_node_30 | 0.4 | n |  | TRUE
26 | bus_LV_261-172_0_2_node_28 | 0.4 | n |  | TRUE
27 | bus_LV_261-172_0_2_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_261-172_0_2_node_45 | 0.4 | n |  | TRUE
29 | bus_LV_261-172_0_2_node_43 | 0.4 | n |  | TRUE
30 | bus_LV_261-172_0_2_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_261-172_0_2_node_29 | 0.4 | n |  | TRUE
32 | bus_LV_261-172_0_2_node_33 | 0.4 | n |  | TRUE
33 | bus_LV_261-172_0_2_node_35 | 0.4 | n |  | TRUE
34 | bus_LV_261-172_0_2_node_36 | 0.4 | n |  | TRUE
35 | bus_LV_261-172_0_2_node_46 | 0.4 | n |  | TRUE
36 | bus_LV_261-172_0_2_node_38 | 0.4 | n |  | TRUE
37 | bus_LV_261-172_0_2_node_40 | 0.4 | n |  | TRUE
38 | bus_LV_261-172_0_2_node_39 | 0.4 | n |  | TRUE
39 | bus_LV_261-172_0_2_node_48 | 0.4 | n |  | TRUE
40 | bus_MV_518_0_node_58 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-172_0_2_load_0 | 0 | 0.019688 | 0.0049343 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-172_0_2_load_3 | 3 | 0.024148 | 0.0060521 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-172_0_2_load_25 | 7 | 0.020689 | 0.0051851 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-172_0_2_load_32 | 9 | 0.0046306 | 0.0011605 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-172_0_2_load_31 | 10 | 0.023058 | 0.0057788 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-172_0_2_load_23 | 12 | 0.023249 | 0.0058268 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-172_0_2_load_22 | 13 | 0.0089987 | 0.0022553 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-172_0_2_load_27 | 16 | 0.0047043 | 0.001179 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-172_0_2_load_37 | 19 | 0.01119 | 0.0028044 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-172_0_2_load_44 | 21 | 0.0027768 | 0.00069594 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-172_0_2_load_41 | 22 | 0.012711 | 0.0031857 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-172_0_2_load_47 | 24 | 0.0050455 | 0.0012645 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-172_0_2_load_30 | 25 | 0.0066263 | 0.0016607 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-172_0_2_load_28 | 26 | 0.0068508 | 0.001717 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-172_0_2_load_24 | 27 | 0.007431 | 0.0018624 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-172_0_2_load_43 | 29 | 0.005241 | 0.0013135 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-172_0_2_load_26 | 30 | 0.0051632 | 0.001294 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-172_0_2_load_29 | 31 | 0.011931 | 0.0029902 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-172_0_2_load_33 | 32 | 0.014855 | 0.0037231 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-172_0_2_load_35 | 33 | 0.028593 | 0.0071662 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-172_0_2_load_36 | 34 | 0.010744 | 0.0026926 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-172_0_2_load_46 | 35 | 0.0040711 | 0.0010203 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-172_0_2_load_38 | 36 | 0.0039646 | 0.00099363 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-172_0_2_load_40 | 37 | 0.0039112 | 0.00098025 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-172_0_2_load_39 | 38 | 0.0033877 | 0.00084903 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-172_0_2_load_48 | 39 | 0.0050784 | 0.0012728 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-172_0_2_line_0 |  | 0 | 1 | 0.012543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-172_0_2_line_1 |  | 0 | 2 | 0.013846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-172_0_2_line_2 |  | 1 | 3 | 0.0042394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-172_0_2_line_3 |  | 2 | 4 | 0.007579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-172_0_2_line_4 |  | 4 | 27 | 0.019574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-172_0_2_line_5 |  | 4 | 13 | 0.012816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-172_0_2_line_6 |  | 5 | 6 | 0.013655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-172_0_2_line_7 |  | 5 | 7 | 0.023547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-172_0_2_line_8 |  | 6 | 25 | 0.010003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-172_0_2_line_9 |  | 6 | 26 | 0.01727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-172_0_2_line_10 |  | 6 | 8 | 0.025145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-172_0_2_line_11 |  | 8 | 9 | 0.010122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-172_0_2_line_12 |  | 8 | 10 | 0.022876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-172_0_2_line_13 |  | 9 | 32 | 0.032617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-172_0_2_line_14 |  | 11 | 12 | 0.019415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-172_0_2_line_15 |  | 11 | 13 | 0.016599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-172_0_2_line_16 |  | 14 | 15 | 0.012864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_261-172_0_2_line_17 |  | 14 | 16 | 0.015882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_261-172_0_2_line_18 |  | 14 | 17 | 0.01757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-172_0_2_line_19 |  | 15 | 18 | 0.011033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-172_0_2_line_20 |  | 15 | 19 | 0.023741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-172_0_2_line_21 |  | 16 | 30 | 0.012978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_261-172_0_2_line_22 |  | 17 | 29 | 0.015219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-172_0_2_line_23 |  | 17 | 22 | 0.03258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-172_0_2_line_24 |  | 18 | 23 | 0.004343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-172_0_2_line_25 |  | 18 | 24 | 0.020332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-172_0_2_line_26 |  | 19 | 36 | 0.010862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-172_0_2_line_27 |  | 20 | 21 | 0.017202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-172_0_2_line_28 |  | 20 | 22 | 0.0072513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-172_0_2_line_29 |  | 21 | 35 | 0.010879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-172_0_2_line_30 |  | 23 | 34 | 0.012306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-172_0_2_line_31 |  | 23 | 32 | 0.014385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-172_0_2_line_32 |  | 25 | 39 | 0.010722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-172_0_2_line_33 |  | 26 | 31 | 0.048895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-172_0_2_line_34 |  | 27 | 28 | 0.0076863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-172_0_2_line_35 |  | 28 | 29 | 0.0029608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-172_0_2_line_36 |  | 33 | 34 | 0.0232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-172_0_2_line_37 |  | 36 | 38 | 0.0066988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-172_0_2_line_38 |  | 37 | 38 | 0.0023903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-172_0_2_trafo_26 | 0.63 MVA 20/0.4 kV | 40 | 30 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2679892.9974 | 1250659.1226 | 2679895.1019 | 1250646.7572
1 | 2679897.425 | 1250633.1075 | 2679895.1019 | 1250646.7572
2 | 2679892.9974 | 1250659.1226 | 2679897.1824 | 1250658.4459
3 | 2679897.425 | 1250633.1075 | 2679903.6627 | 1250637.4392
4 | 2679903.6627 | 1250637.4392 | 2679913.8495 | 1250643.9592 | 2679919.4983 | 1250648.861
5 | 2679903.6627 | 1250637.4392 | 2679903.8424 | 1250631.3928 | 2679902.7077 | 1250624.7222
6 | 2679875.3506 | 1250694.1217 | 2679875.4557 | 1250693.0445 | 2679875.8231 | 1250689.3134 | 2679879.3014 | 1250689.4604 | 2679878.9505 | 1250684.1295
7 | 2679878.9505 | 1250684.1295 | 2679855.4123 | 1250683.4838
8 | 2679875.3506 | 1250694.1217 | 2679865.3517 | 1250693.8381
9 | 2679875.3506 | 1250694.1217 | 2679873.6514 | 1250711.3079
10 | 2679900.527 | 1250694.7281 | 2679890.4505 | 1250695.1482 | 2679875.3506 | 1250694.1217
11 | 2679900.527 | 1250694.7281 | 2679908.1688 | 1250693.4635 | 2679910.412 | 1250692.6803
12 | 2679900.527 | 1250694.7281 | 2679903.709 | 1250705.0786 | 2679908.4527 | 1250716.1524
13 | 2679910.412 | 1250692.6803 | 2679916.1407 | 1250690.6801 | 2679920.8364 | 1250688.9977 | 2679927.3575 | 1250686.317 | 2679936.5517 | 1250683.5834 | 2679941.2121 | 1250682.0095
14 | 2679900.523 | 1250608.2754 | 2679881.3535 | 1250611.352
15 | 2679900.523 | 1250608.2754 | 2679901.5901 | 1250618.1526 | 2679902.7077 | 1250624.7222
16 | 2679959.9301 | 1250667.5091 | 2679955.0173 | 1250667.932 | 2679947.2762 | 1250669.829
17 | 2679947.2762 | 1250669.829 | 2679942.1909 | 1250671.8508 | 2679932.4681 | 1250675.5681
18 | 2679943.4454 | 1250652.7314 | 2679944.3264 | 1250659.615 | 2679947.2762 | 1250669.829
19 | 2679959.4868 | 1250678.5334 | 2679959.648 | 1250673.8655 | 2679959.9301 | 1250667.5091
20 | 2679959.9301 | 1250667.5091 | 2679960.0736 | 1250667.4999 | 2679971.2023 | 1250669.1067 | 2679983.4622 | 1250670.6249
21 | 2679932.4681 | 1250675.5681 | 2679925.4203 | 1250678.2627 | 2679920.3453 | 1250680.2015
22 | 2679943.4454 | 1250652.7314 | 2679928.2583 | 1250653.7086
23 | 2679943.4454 | 1250652.7314 | 2679946.2541 | 1250645.9976 | 2679959.0739 | 1250624.2051
24 | 2679959.4868 | 1250678.5334 | 2679955.1307 | 1250678.5413
25 | 2679959.4868 | 1250678.5334 | 2679968.3844 | 1250679.3207 | 2679979.6861 | 1250680.8121
26 | 2679983.4622 | 1250670.6249 | 2679994.2421 | 1250671.9597
27 | 2679962.7506 | 1250617.955 | 2679978.677 | 1250611.454
28 | 2679962.7506 | 1250617.955 | 2679959.0739 | 1250624.2051
29 | 2679978.677 | 1250611.454 | 2679978.677 | 1250611.454 | 2679988.6271 | 1250607.0553
30 | 2679955.1307 | 1250678.5413 | 2679956.3978 | 1250690.7818
31 | 2679955.1307 | 1250678.5413 | 2679951.6436 | 1250679.0502 | 2679947.063 | 1250680.0336 | 2679941.2121 | 1250682.0095
32 | 2679854.6339 | 1250693.5341 | 2679865.3517 | 1250693.8381
33 | 2679873.6514 | 1250711.3079 | 2679873.2789 | 1250715.0759 | 2679874.2618 | 1250717.2018 | 2679873.8851 | 1250726.6593 | 2679879.1314 | 1250739.5728 | 2679883.9836 | 1250738.0371 | 2679888.2921 | 1250751.6445
34 | 2679925.3037 | 1250653.8987 | 2679919.4983 | 1250648.861
35 | 2679925.3037 | 1250653.8987 | 2679928.2583 | 1250653.7086
36 | 2679956.3978 | 1250690.7818 | 2679957.1743 | 1250698.2835 | 2679960.2166 | 1250713.6438
37 | 2680000.89 | 1250672.7829 | 2679994.2421 | 1250671.9597
38 | 2680003.2622 | 1250673.0767 | 2680000.89 | 1250672.7829

## bus_geodata
| x | y | coords
0 | 2679895.1019 | 1250646.7572
1 | 2679892.9974 | 1250659.1226
2 | 2679897.425 | 1250633.1075
3 | 2679897.1824 | 1250658.4459
4 | 2679903.6627 | 1250637.4392
5 | 2679878.9505 | 1250684.1295
6 | 2679875.3506 | 1250694.1217
7 | 2679855.4123 | 1250683.4838
8 | 2679900.527 | 1250694.7281
9 | 2679910.412 | 1250692.6803
10 | 2679908.4527 | 1250716.1524
11 | 2679900.523 | 1250608.2754
12 | 2679881.3535 | 1250611.352
13 | 2679902.7077 | 1250624.7222
14 | 2679947.2762 | 1250669.829
15 | 2679959.9301 | 1250667.5091
16 | 2679932.4681 | 1250675.5681
17 | 2679943.4454 | 1250652.7314
18 | 2679959.4868 | 1250678.5334
19 | 2679983.4622 | 1250670.6249
20 | 2679962.7506 | 1250617.955
21 | 2679978.677 | 1250611.454
22 | 2679959.0739 | 1250624.2051
23 | 2679955.1307 | 1250678.5413
24 | 2679979.6861 | 1250680.8121
25 | 2679865.3517 | 1250693.8381
26 | 2679873.6514 | 1250711.3079
27 | 2679919.4983 | 1250648.861
28 | 2679925.3036 | 1250653.8987
29 | 2679928.2583 | 1250653.7086
30 | 2679920.3453 | 1250680.2015
31 | 2679888.2921 | 1250751.6445
32 | 2679941.2121 | 1250682.0095
33 | 2679960.2166 | 1250713.6438
34 | 2679956.3978 | 1250690.7818
35 | 2679988.6271 | 1250607.0553
36 | 2679994.2421 | 1250671.9597
37 | 2680003.2622 | 1250673.0767
38 | 2680000.89 | 1250672.7829
39 | 2679854.6339 | 1250693.5341
40 | 2679947.2762 | 1250669.829

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9904 | -0.18447 | 0.019688 | 0.0049343
1 | 0.99013 | -0.18985 | 0 | 0
2 | 0.99096 | -0.17369 | 0 | 0
3 | 0.99003 | -0.19167 | 0.024148 | 0.0060521
4 | 0.99126 | -0.1678 | 0 | 0
5 | 0.98782 | -0.23443 | 0 | 0
6 | 0.98808 | -0.22939 | 0 | 0
7 | 0.98737 | -0.24314 | 0.020689 | 0.0051851
8 | 0.98926 | -0.20644 | 0 | 0
9 | 0.98995 | -0.19307 | 0.0046306 | 0.0011605
10 | 0.98878 | -0.21584 | 0.023058 | 0.0057788
11 | 0.99053 | -0.18198 | 0 | 0
12 | 0.99012 | -0.19001 | 0.023249 | 0.0058268
13 | 0.99089 | -0.17513 | 0.0089987 | 0.0022553
14 | 0.99642 | -0.068404 | 0 | 0
15 | 0.99547 | -0.086551 | 0 | 0
16 | 0.99837 | -0.030994 | 0.0047043 | 0.001179
17 | 0.99468 | -0.10187 | 0 | 0
18 | 0.99408 | -0.11339 | 0 | 0
19 | 0.99499 | -0.095932 | 0.01119 | 0.0028044
20 | 0.99405 | -0.11398 | 0 | 0
21 | 0.99394 | -0.11606 | 0.0027768 | 0.00069594
22 | 0.9941 | -0.11311 | 0.012711 | 0.0031857
23 | 0.99355 | -0.12359 | 0 | 0
24 | 0.99398 | -0.1152 | 0.0050455 | 0.0012645
25 | 0.98797 | -0.23148 | 0.0066263 | 0.0016607
26 | 0.98778 | -0.23518 | 0.0068508 | 0.001717
27 | 0.99263 | -0.14142 | 0.007431 | 0.0018624
28 | 0.99322 | -0.13007 | 0 | 0
29 | 0.99344 | -0.1257 | 0.005241 | 0.0013135
30 | 1 | 0 | -0.27748 | -0.070003
31 | 0.98725 | -0.24561 | 0.011931 | 0.0029902
32 | 0.99231 | -0.14742 | 0.014855 | 0.0037231
33 | 0.9925 | -0.14387 | 0.028593 | 0.0071662
34 | 0.99311 | -0.13214 | 0.010744 | 0.0026926
35 | 0.9939 | -0.11684 | 0.0040711 | 0.0010203
36 | 0.99488 | -0.098086 | 0.0039646 | 0.00099363
37 | 0.99482 | -0.099112 | 0.0039112 | 0.00098025
38 | 0.99483 | -0.098947 | 0.0033877 | 0.00084903
39 | 0.98792 | -0.23245 | 0.0050784 | 0.0012728
40 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.024156 | 0.0060572 | -0.02415 | -0.0060534 | 6.1962e-06 | 3.8042e-06 | 0.036295 | 0.036295 | 0.036295 | 0.9904 | -0.18447 | 0.99013 | -0.18985 | 9.971
1 | -0.043844 | -0.010991 | 0.043867 | 0.011006 | 2.2531e-05 | 1.4242e-05 | 0.065874 | 0.065874 | 0.065874 | 0.9904 | -0.18447 | 0.99096 | -0.17369 | 18.0973
2 | 0.02415 | 0.0060534 | -0.024148 | -0.0060521 | 2.0942e-06 | 1.2858e-06 | 0.036295 | 0.036295 | 0.036295 | 0.99013 | -0.18985 | 0.99003 | -0.19167 | 9.971
3 | -0.043867 | -0.011006 | 0.043879 | 0.011013 | 1.2333e-05 | 7.7955e-06 | 0.065874 | 0.065874 | 0.065874 | 0.99096 | -0.17369 | 0.99126 | -0.1678 | 18.0973
4 | -0.076155 | -0.019113 | 0.076251 | 0.019174 | 9.5942e-05 | 6.115e-05 | 0.11433 | 0.11433 | 0.11433 | 0.99126 | -0.1678 | 0.99263 | -0.14142 | 31.4087
5 | 0.032276 | 0.0080992 | -0.032264 | -0.0080922 | 1.1283e-05 | 7.0559e-06 | 0.048453 | 0.048453 | 0.048453 | 0.99126 | -0.1678 | 0.99089 | -0.17513 | 13.3114
6 | -0.020697 | -0.0051903 | 0.020702 | 0.0051933 | 4.9779e-06 | 3.011e-06 | 0.031179 | 0.031179 | 0.031179 | 0.98782 | -0.23443 | 0.98808 | -0.22939 | 8.5656
7 | 0.020697 | 0.0051903 | -0.020689 | -0.0051851 | 8.584e-06 | 5.1924e-06 | 0.031179 | 0.031179 | 0.031179 | 0.98782 | -0.23443 | 0.98737 | -0.24314 | 8.5656
8 | 0.011706 | 0.0029341 | -0.011705 | -0.0029335 | 1.1658e-06 | 6.18e-07 | 0.017629 | 0.017629 | 0.017629 | 0.98808 | -0.22939 | 0.98797 | -0.23148 | 4.8432
9 | 0.018793 | 0.0047134 | -0.018788 | -0.0047103 | 5.1877e-06 | 3.099e-06 | 0.028303 | 0.028303 | 0.028303 | 0.98808 | -0.22939 | 0.98778 | -0.23518 | 7.7755
10 | -0.051201 | -0.012841 | 0.051257 | 0.012876 | 5.6067e-05 | 3.5561e-05 | 0.07711 | 0.07711 | 0.07711 | 0.98808 | -0.22939 | 0.98926 | -0.20644 | 21.1842
11 | -0.074325 | -0.018661 | 0.074373 | 0.018692 | 4.7451e-05 | 3.0239e-05 | 0.11181 | 0.11181 | 0.11181 | 0.98926 | -0.20644 | 0.98995 | -0.19307 | 30.7169
12 | 0.023068 | 0.0057851 | -0.023058 | -0.0057788 | 1.0329e-05 | 6.3169e-06 | 0.034699 | 0.034699 | 0.034699 | 0.98926 | -0.20644 | 0.98878 | -0.21584 | 9.5328
13 | -0.079003 | -0.019852 | 0.079176 | 0.019962 | 0.00017254 | 0.00011001 | 0.11877 | 0.11877 | 0.11877 | 0.98995 | -0.19307 | 0.99231 | -0.14742 | 32.6291
14 | 0.023258 | 0.0058322 | -0.023249 | -0.0058268 | 8.8883e-06 | 5.4387e-06 | 0.03494 | 0.03494 | 0.03494 | 0.99053 | -0.18198 | 0.99012 | -0.19001 | 9.599
15 | -0.023258 | -0.0058322 | 0.023266 | 0.0058369 | 7.599e-06 | 4.6496e-06 | 0.03494 | 0.03494 | 0.03494 | 0.99053 | -0.18198 | 0.99089 | -0.17513 | 9.599
16 | 0.1614 | 0.040776 | -0.16126 | -0.040687 | 0.00014026 | 8.9433e-05 | 0.24115 | 0.24115 | 0.24115 | 0.99642 | -0.068404 | 0.99547 | -0.086551 | 33.1246
17 | -0.27023 | -0.068251 | 0.27072 | 0.068561 | 0.00048541 | 0.00031025 | 0.40374 | 0.40374 | 0.40374 | 0.99642 | -0.068404 | 0.99837 | -0.030994 | 55.4591
18 | 0.10883 | 0.027474 | -0.10866 | -0.027363 | 0.00017419 | 0.00011125 | 0.1626 | 0.1626 | 0.1626 | 0.99642 | -0.068404 | 0.99468 | -0.10187 | 44.6692
19 | 0.1388 | 0.035053 | -0.13862 | -0.034939 | 0.00017826 | 0.00011394 | 0.20757 | 0.20757 | 0.20757 | 0.99547 | -0.086551 | 0.99408 | -0.11339 | 57.0235
20 | 0.022465 | 0.0056342 | -0.022455 | -0.005628 | 1.004e-05 | 6.1172e-06 | 0.033582 | 0.033582 | 0.033582 | 0.99547 | -0.086551 | 0.99499 | -0.095932 | 9.2257
21 | -0.27542 | -0.06974 | 0.27583 | 0.070002 | 0.00041056 | 0.00026242 | 0.41075 | 0.41075 | 0.41075 | 0.99837 | -0.030994 | 1 | 0 | 56.4222
22 | 0.089087 | 0.022455 | -0.088986 | -0.02239 | 0.00010143 | 6.4719e-05 | 0.13332 | 0.13332 | 0.13332 | 0.99468 | -0.10187 | 0.99344 | -0.1257 | 36.6256
23 | 0.019571 | 0.0049085 | -0.01956 | -0.0049022 | 1.0473e-05 | 6.2803e-06 | 0.029279 | 0.029279 | 0.029279 | 0.99468 | -0.10187 | 0.9941 | -0.11311 | 8.0436
24 | 0.13357 | 0.033674 | -0.13351 | -0.033633 | 6.5153e-05 | 4.1642e-05 | 0.20001 | 0.20001 | 0.20001 | 0.99408 | -0.11339 | 0.99355 | -0.12359 | 54.9484
25 | 0.005046 | 0.0012645 | -0.0050455 | -0.0012645 | 4.3498e-07 | 1.4823e-08 | 0.0075532 | 0.0075532 | 0.0075532 | 0.99408 | -0.11339 | 0.99398 | -0.1152 | 2.0751
26 | 0.011265 | 0.0028236 | -0.011264 | -0.002823 | 1.1561e-06 | 5.9885e-07 | 0.016847 | 0.016847 | 0.016847 | 0.99499 | -0.095932 | 0.99488 | -0.098086 | 4.6283
27 | 0.0068488 | 0.0017164 | -0.0068481 | -0.0017162 | 6.7802e-07 | 2.1095e-07 | 0.010252 | 0.010252 | 0.010252 | 0.99405 | -0.11398 | 0.99394 | -0.11606 | 2.8165
28 | -0.0068488 | -0.0017164 | 0.0068491 | 0.0017165 | 2.8581e-07 | 8.8908e-08 | 0.010252 | 0.010252 | 0.010252 | 0.99405 | -0.11398 | 0.9941 | -0.11311 | 2.8165
29 | 0.0040713 | 0.0010203 | -0.0040711 | -0.0010203 | 1.5155e-07 | -4.4e-08 | 0.006095 | 0.006095 | 0.006095 | 0.99394 | -0.11606 | 0.9939 | -0.11684 | 1.6745
30 | 0.039369 | 0.0098788 | -0.039353 | -0.0098687 | 1.6045e-05 | 1.011e-05 | 0.058966 | 0.058966 | 0.058966 | 0.99355 | -0.12359 | 0.99311 | -0.13214 | 16.1996
31 | 0.094138 | 0.023754 | -0.094031 | -0.023685 | 0.00010731 | 6.8494e-05 | 0.14105 | 0.14105 | 0.14105 | 0.99355 | -0.12359 | 0.99231 | -0.14742 | 38.7489
32 | 0.0050786 | 0.0012728 | -0.0050784 | -0.0012728 | 2.3525e-07 | 1.3262e-08 | 0.007649 | 0.0076491 | 0.0076491 | 0.98797 | -0.23148 | 0.98792 | -0.23245 | 2.1014
33 | 0.011937 | 0.0029933 | -0.011931 | -0.0029902 | 5.9292e-06 | 3.1692e-06 | 0.017982 | 0.017983 | 0.017983 | 0.98778 | -0.23518 | 0.98725 | -0.24561 | 4.9403
34 | -0.083682 | -0.021036 | 0.083727 | 0.021065 | 4.5374e-05 | 2.894e-05 | 0.12547 | 0.12547 | 0.12547 | 0.99263 | -0.14142 | 0.99322 | -0.13007 | 34.469
35 | -0.083727 | -0.021065 | 0.083745 | 0.021076 | 1.7478e-05 | 1.1148e-05 | 0.12547 | 0.12547 | 0.12547 | 0.99322 | -0.13007 | 0.99344 | -0.1257 | 34.469
36 | -0.028593 | -0.0071662 | 0.028609 | 0.0071761 | 1.5989e-05 | 9.9327e-06 | 0.042869 | 0.042869 | 0.042869 | 0.9925 | -0.14387 | 0.99311 | -0.13214 | 11.7772
37 | 0.0072992 | 0.0018294 | -0.0072989 | -0.0018293 | 2.994e-07 | 1.0464e-07 | 0.010917 | 0.010917 | 0.010917 | 0.99488 | -0.098086 | 0.99483 | -0.098947 | 2.9993
38 | -0.0039112 | -0.00098025 | 0.0039113 | 0.00098024 | 3.0679e-08 | -1.1401e-08 | 0.0058503 | 0.0058503 | 0.0058503 | 0.99482 | -0.099112 | 0.99483 | -0.098947 | 1.6072

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.28265 | 0.071297

## res_load
| p_mw | q_mvar
0 | 0.019688 | 0.0049343
1 | 0.024148 | 0.0060521
2 | 0.020689 | 0.0051851
3 | 0.0046306 | 0.0011605
4 | 0.023058 | 0.0057788
5 | 0.023249 | 0.0058268
6 | 0.0089987 | 0.0022553
7 | 0.0047043 | 0.001179
8 | 0.01119 | 0.0028044
9 | 0.0027768 | 0.00069594
10 | 0.012711 | 0.0031857
11 | 0.0050455 | 0.0012645
12 | 0.0066263 | 0.0016607
13 | 0.0068508 | 0.001717
14 | 0.007431 | 0.0018624
15 | 0.005241 | 0.0013135
16 | 0.0051632 | 0.001294
17 | 0.011931 | 0.0029902
18 | 0.014855 | 0.0037231
19 | 0.028593 | 0.0071662
20 | 0.010744 | 0.0026926
21 | 0.0040711 | 0.0010203
22 | 0.0039646 | 0.00099363
23 | 0.0039112 | 0.00098025
24 | 0.0033877 | 0.00084903
25 | 0.0050784 | 0.0012728

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1