## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-180_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-180_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-180_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-180_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-180_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-180_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-180_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_261-180_0_4_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_261-180_0_4_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_261-180_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_261-180_0_4_node_50 | 0.4 | n |  | TRUE
11 | bus_LV_261-180_0_4_node_48 | 0.4 | n |  | TRUE
12 | bus_LV_261-180_0_4_node_17 | 0.4 | n |  | TRUE
13 | bus_LV_261-180_0_4_node_114 | 0.4 | n |  | TRUE
14 | bus_LV_261-180_0_4_node_49 | 0.4 | n |  | TRUE
15 | bus_LV_261-180_0_4_node_45 | 0.4 | n |  | TRUE
16 | bus_LV_261-180_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_261-180_0_4_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_261-180_0_4_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_261-180_0_4_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_261-180_0_4_node_23 | 0.4 | n |  | TRUE
21 | bus_LV_261-180_0_4_node_32 | 0.4 | n |  | TRUE
22 | bus_LV_261-180_0_4_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_261-180_0_4_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_261-180_0_4_node_140 | 0.4 | n |  | TRUE
25 | bus_LV_261-180_0_4_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_261-180_0_4_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_261-180_0_4_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_261-180_0_4_node_107 | 0.4 | n |  | TRUE
29 | bus_LV_261-180_0_4_node_36 | 0.4 | n |  | TRUE
30 | bus_LV_261-180_0_4_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_261-180_0_4_node_38 | 0.4 | n |  | TRUE
32 | bus_LV_261-180_0_4_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_261-180_0_4_node_29 | 0.4 | n |  | TRUE
34 | bus_LV_261-180_0_4_node_41 | 0.4 | n |  | TRUE
35 | bus_LV_261-180_0_4_node_66 | 0.4 | n |  | TRUE
36 | bus_LV_261-180_0_4_node_63 | 0.4 | n |  | TRUE
37 | bus_LV_261-180_0_4_node_30 | 0.4 | n |  | TRUE
38 | bus_LV_261-180_0_4_node_37 | 0.4 | n |  | TRUE
39 | bus_LV_261-180_0_4_node_34 | 0.4 | n |  | TRUE
40 | bus_LV_261-180_0_4_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_261-180_0_4_node_139 | 0.4 | n |  | TRUE
42 | bus_LV_261-180_0_4_node_25 | 0.4 | n |  | TRUE
43 | bus_LV_261-180_0_4_node_106 | 0.4 | n |  | TRUE
44 | bus_LV_261-180_0_4_node_108 | 0.4 | n |  | TRUE
45 | bus_LV_261-180_0_4_node_104 | 0.4 | n |  | TRUE
46 | bus_LV_261-180_0_4_node_33 | 0.4 | n |  | TRUE
47 | bus_LV_261-180_0_4_node_132 | 0.4 | n |  | TRUE
48 | bus_LV_261-180_0_4_node_133 | 0.4 | n |  | TRUE
49 | bus_LV_261-180_0_4_node_40 | 0.4 | n |  | TRUE
50 | bus_LV_261-180_0_4_node_127 | 0.4 | n |  | TRUE
51 | bus_LV_261-180_0_4_node_46 | 0.4 | n |  | TRUE
52 | bus_LV_261-180_0_4_node_61 | 0.4 | n |  | TRUE
53 | bus_LV_261-180_0_4_node_26 | 0.4 | n |  | TRUE
54 | bus_LV_261-180_0_4_node_27 | 0.4 | n |  | TRUE
55 | bus_LV_261-180_0_4_node_28 | 0.4 | n |  | TRUE
56 | bus_LV_261-180_0_4_node_35 | 0.4 | n |  | TRUE
57 | bus_LV_261-180_0_4_node_100 | 0.4 | n |  | TRUE
58 | bus_LV_261-180_0_4_node_101 | 0.4 | n |  | TRUE
59 | bus_LV_261-180_0_4_node_42 | 0.4 | n |  | TRUE
60 | bus_LV_261-180_0_4_node_43 | 0.4 | n |  | TRUE
61 | bus_LV_261-180_0_4_node_44 | 0.4 | n |  | TRUE
62 | bus_LV_261-180_0_4_node_47 | 0.4 | n |  | TRUE
63 | bus_LV_261-180_0_4_node_58 | 0.4 | n |  | TRUE
64 | bus_LV_261-180_0_4_node_56 | 0.4 | n |  | TRUE
65 | bus_LV_261-180_0_4_node_51 | 0.4 | n |  | TRUE
66 | bus_LV_261-180_0_4_node_59 | 0.4 | n |  | TRUE
67 | bus_LV_261-180_0_4_node_111 | 0.4 | n |  | TRUE
68 | bus_LV_261-180_0_4_node_60 | 0.4 | n |  | TRUE
69 | bus_LV_261-180_0_4_node_52 | 0.4 | n |  | TRUE
70 | bus_LV_261-180_0_4_node_53 | 0.4 | n |  | TRUE
71 | bus_LV_261-180_0_4_node_54 | 0.4 | n |  | TRUE
72 | bus_LV_261-180_0_4_node_55 | 0.4 | n |  | TRUE
73 | bus_LV_261-180_0_4_node_57 | 0.4 | n |  | TRUE
74 | bus_LV_261-180_0_4_node_67 | 0.4 | n |  | TRUE
75 | bus_LV_261-180_0_4_node_68 | 0.4 | n |  | TRUE
76 | bus_LV_261-180_0_4_node_73 | 0.4 | n |  | TRUE
77 | bus_LV_261-180_0_4_node_74 | 0.4 | n |  | TRUE
78 | bus_LV_261-180_0_4_node_62 | 0.4 | n |  | TRUE
79 | bus_LV_261-180_0_4_node_64 | 0.4 | n |  | TRUE
80 | bus_LV_261-180_0_4_node_65 | 0.4 | n |  | TRUE
81 | bus_LV_261-180_0_4_node_84 | 0.4 | n |  | TRUE
82 | bus_LV_261-180_0_4_node_82 | 0.4 | n |  | TRUE
83 | bus_LV_261-180_0_4_node_128 | 0.4 | n |  | TRUE
84 | bus_LV_261-180_0_4_node_69 | 0.4 | n |  | TRUE
85 | bus_LV_261-180_0_4_node_70 | 0.4 | n |  | TRUE
86 | bus_LV_261-180_0_4_node_71 | 0.4 | n |  | TRUE
87 | bus_LV_261-180_0_4_node_72 | 0.4 | n |  | TRUE
88 | bus_LV_261-180_0_4_node_78 | 0.4 | n |  | TRUE
89 | bus_LV_261-180_0_4_node_79 | 0.4 | n |  | TRUE
90 | bus_LV_261-180_0_4_node_87 | 0.4 | n |  | TRUE
91 | bus_LV_261-180_0_4_node_135 | 0.4 | n |  | TRUE
92 | bus_LV_261-180_0_4_node_75 | 0.4 | n |  | TRUE
93 | bus_LV_261-180_0_4_node_76 | 0.4 | n |  | TRUE
94 | bus_LV_261-180_0_4_node_77 | 0.4 | n |  | TRUE
95 | bus_LV_261-180_0_4_node_90 | 0.4 | n |  | TRUE
96 | bus_LV_261-180_0_4_node_91 | 0.4 | n |  | TRUE
97 | bus_LV_261-180_0_4_node_88 | 0.4 | n |  | TRUE
98 | bus_LV_261-180_0_4_node_134 | 0.4 | n |  | TRUE
99 | bus_LV_261-180_0_4_node_80 | 0.4 | n |  | TRUE
100 | bus_LV_261-180_0_4_node_81 | 0.4 | n |  | TRUE
101 | bus_LV_261-180_0_4_node_83 | 0.4 | n |  | TRUE
102 | bus_LV_261-180_0_4_node_85 | 0.4 | n |  | TRUE
103 | bus_LV_261-180_0_4_node_86 | 0.4 | n |  | TRUE
104 | bus_LV_261-180_0_4_node_122 | 0.4 | n |  | TRUE
105 | bus_LV_261-180_0_4_node_120 | 0.4 | n |  | TRUE
106 | bus_LV_261-180_0_4_node_124 | 0.4 | n |  | TRUE
107 | bus_LV_261-180_0_4_node_121 | 0.4 | n |  | TRUE
108 | bus_LV_261-180_0_4_node_89 | 0.4 | n |  | TRUE
109 | bus_LV_261-180_0_4_node_93 | 0.4 | n |  | TRUE
110 | bus_LV_261-180_0_4_node_95 | 0.4 | n |  | TRUE
111 | bus_LV_261-180_0_4_node_96 | 0.4 | n |  | TRUE
112 | bus_LV_261-180_0_4_node_94 | 0.4 | n |  | TRUE
113 | bus_LV_261-180_0_4_node_98 | 0.4 | n |  | TRUE
114 | bus_LV_261-180_0_4_node_99 | 0.4 | n |  | TRUE
115 | bus_LV_261-180_0_4_node_92 | 0.4 | n |  | TRUE
116 | bus_LV_261-180_0_4_node_112 | 0.4 | n |  | TRUE
117 | bus_LV_261-180_0_4_node_97 | 0.4 | n |  | TRUE
118 | bus_LV_261-180_0_4_node_116 | 0.4 | n |  | TRUE
119 | bus_LV_261-180_0_4_node_119 | 0.4 | n |  | TRUE
120 | bus_LV_261-180_0_4_node_117 | 0.4 | n |  | TRUE
121 | bus_LV_261-180_0_4_node_102 | 0.4 | n |  | TRUE
122 | bus_LV_261-180_0_4_node_103 | 0.4 | n |  | TRUE
123 | bus_LV_261-180_0_4_node_105 | 0.4 | n |  | TRUE
124 | bus_LV_261-180_0_4_node_131 | 0.4 | n |  | TRUE
125 | bus_LV_261-180_0_4_node_109 | 0.4 | n |  | TRUE
126 | bus_LV_261-180_0_4_node_123 | 0.4 | n |  | TRUE
127 | bus_LV_261-180_0_4_node_118 | 0.4 | n |  | TRUE
128 | bus_LV_261-180_0_4_node_130 | 0.4 | n |  | TRUE
129 | bus_LV_261-180_0_4_node_129 | 0.4 | n |  | TRUE
130 | bus_LV_261-180_0_4_node_136 | 0.4 | n |  | TRUE
131 | bus_LV_261-180_0_4_node_137 | 0.4 | n |  | TRUE
132 | bus_LV_261-180_0_4_node_138 | 0.4 | n |  | TRUE
133 | bus_MV_518_0_node_132 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-180_0_4_load_0 | 0 | 0.0022276 | 0.00055829 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-180_0_4_load_1 | 1 | 0.0015436 | 0.00038688 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-180_0_4_load_5 | 5 | 0.0061308 | 0.0015365 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-180_0_4_load_8 | 7 | 0.0052493 | 0.0013156 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-180_0_4_load_9 | 8 | 0.0018907 | 0.00047385 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-180_0_4_load_50 | 10 | 0.0028224 | 0.00070736 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-180_0_4_load_114 | 13 | 0.0028805 | 0.00072193 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-180_0_4_load_49 | 14 | 0.006501 | 0.0016293 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-180_0_4_load_10 | 16 | 0.0065621 | 0.0016446 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-180_0_4_load_23 | 20 | 0.0019264 | 0.00048279 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-180_0_4_load_140 | 24 | 0.0029713 | 0.00074468 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-180_0_4_load_24 | 26 | 0.0017306 | 0.00043373 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-180_0_4_load_107 | 28 | 0.0031967 | 0.00080117 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-180_0_4_load_36 | 29 | 0.0015998 | 0.00040096 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-180_0_4_load_38 | 31 | 0.0015559 | 0.00038995 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-180_0_4_load_41 | 34 | 0.0090256 | 0.002262 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-180_0_4_load_66 | 35 | 0.0016666 | 0.0004177 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-180_0_4_load_30 | 37 | 0.0076771 | 0.0019241 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-180_0_4_load_37 | 38 | 0.001575 | 0.00039472 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-180_0_4_load_34 | 39 | 0.0036838 | 0.00092325 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-180_0_4_load_31 | 40 | 0.003675 | 0.00092104 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-180_0_4_load_25 | 42 | 0.0017191 | 0.00043085 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-180_0_4_load_108 | 44 | 0.0056755 | 0.0014224 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-180_0_4_load_132 | 47 | 0.0043073 | 0.0010795 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-180_0_4_load_133 | 48 | 0.0021225 | 0.00053195 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-180_0_4_load_40 | 49 | 0.0057039 | 0.0014295 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-180_0_4_load_127 | 50 | 0.0016144 | 0.00040461 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-180_0_4_load_46 | 51 | 0.0051734 | 0.0012966 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-180_0_4_load_61 | 52 | 0.0032431 | 0.00081279 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-180_0_4_load_26 | 53 | 0.0019467 | 0.00048788 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-180_0_4_load_27 | 54 | 0.0018387 | 0.00046082 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-180_0_4_load_28 | 55 | 0.0018557 | 0.00046509 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-180_0_4_load_35 | 56 | 0.0067577 | 0.0016937 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-180_0_4_load_100 | 57 | 0.0034015 | 0.00085249 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-180_0_4_load_43 | 60 | 0.0057379 | 0.0014381 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-180_0_4_load_44 | 61 | 0.0025315 | 0.00063446 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-180_0_4_load_47 | 62 | 0.0056848 | 0.0014247 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-180_0_4_load_58 | 63 | 0.0067529 | 0.0016924 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-180_0_4_load_56 | 64 | 0.0031544 | 0.00079056 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-180_0_4_load_51 | 65 | 0.0037224 | 0.00093292 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-180_0_4_load_59 | 66 | 0.0035383 | 0.00088677 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-180_0_4_load_60 | 68 | 0.0036467 | 0.00091396 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-180_0_4_load_52 | 69 | 0.0053351 | 0.0013371 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-180_0_4_load_53 | 70 | 0.0055211 | 0.0013837 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-180_0_4_load_54 | 71 | 0.0016808 | 0.00042124 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-180_0_4_load_55 | 72 | 0.0027908 | 0.00069943 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-180_0_4_load_57 | 73 | 0.0036311 | 0.00091004 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-180_0_4_load_67 | 74 | 0.0047346 | 0.0011866 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-180_0_4_load_68 | 75 | 0.0036188 | 0.00090696 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-180_0_4_load_73 | 76 | 0.003281 | 0.0008223 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-180_0_4_load_62 | 78 | 0.0025753 | 0.00064544 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-180_0_4_load_64 | 79 | 0.0037198 | 0.00093227 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-180_0_4_load_65 | 80 | 0.0036816 | 0.0009227 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-180_0_4_load_84 | 81 | 0.0037706 | 0.00094499 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-180_0_4_load_82 | 82 | 0.0037846 | 0.0009485 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-180_0_4_load_128 | 83 | 0.0017122 | 0.00042912 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-180_0_4_load_69 | 84 | 0.0061125 | 0.0015319 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-180_0_4_load_71 | 86 | 0.0087943 | 0.002204 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-180_0_4_load_72 | 87 | 0.0036852 | 0.0009236 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-180_0_4_load_78 | 88 | 0.0057955 | 0.0014525 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-180_0_4_load_79 | 89 | 0.0050762 | 0.0012722 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-180_0_4_load_87 | 90 | 0.0055101 | 0.001381 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-180_0_4_load_135 | 91 | 0.0051657 | 0.0012947 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-180_0_4_load_75 | 92 | 0.0052193 | 0.0013081 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-180_0_4_load_76 | 93 | 0.003945 | 0.00098872 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-180_0_4_load_77 | 94 | 0.0050996 | 0.0012781 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-180_0_4_load_90 | 95 | 0.007203 | 0.0018052 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-180_0_4_load_91 | 96 | 0.0026595 | 0.00066653 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-180_0_4_load_88 | 97 | 0.0054093 | 0.0013557 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-180_0_4_load_134 | 98 | 0.0053605 | 0.0013435 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-180_0_4_load_80 | 99 | 0.002369 | 0.00059372 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-180_0_4_load_81 | 100 | 0.0027264 | 0.00068331 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-180_0_4_load_85 | 102 | 0.0035241 | 0.00088323 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-180_0_4_load_86 | 103 | 0.0015063 | 0.00037751 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-180_0_4_load_122 | 104 | 0.0019208 | 0.0004814 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-180_0_4_load_120 | 105 | 0.0014995 | 0.0003758 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-180_0_4_load_124 | 106 | 0.0016222 | 0.00040655 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-180_0_4_load_121 | 107 | 0.0051491 | 0.0012905 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-180_0_4_load_95 | 110 | 0.0021311 | 0.00053411 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-180_0_4_load_94 | 112 | 0.0028434 | 0.00071262 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-180_0_4_load_98 | 113 | 0.0035672 | 0.00089402 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-180_0_4_load_99 | 114 | 0.0031975 | 0.00080138 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_261-180_0_4_load_97 | 117 | 0.0052817 | 0.0013237 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_261-180_0_4_load_116 | 118 | 0.0029886 | 0.00074901 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_261-180_0_4_load_119 | 119 | 0.0036065 | 0.00090388 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_261-180_0_4_load_102 | 121 | 0.0047758 | 0.0011969 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_261-180_0_4_load_103 | 122 | 0.0061843 | 0.0015499 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_261-180_0_4_load_105 | 123 | 0.0072639 | 0.0018205 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_261-180_0_4_load_131 | 124 | 0.0047933 | 0.0012013 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_261-180_0_4_load_109 | 125 | 0.0040694 | 0.0010199 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_261-180_0_4_load_123 | 126 | 0.0017076 | 0.00042796 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_261-180_0_4_load_118 | 127 | 0.004611 | 0.0011556 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_261-180_0_4_load_130 | 128 | 0.0029079 | 0.0007288 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_261-180_0_4_load_129 | 129 | 0.0016375 | 0.0004104 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_261-180_0_4_load_136 | 130 | 0.0030177 | 0.0007563 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_261-180_0_4_load_137 | 131 | 0.0030126 | 0.00075504 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_261-180_0_4_load_138 | 132 | 0.0030501 | 0.00076442 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 36 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-180_0_4_line_0 |  | 0 | 1 | 0.013325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-180_0_4_line_1 |  | 0 | 2 | 0.042533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-180_0_4_line_2 |  | 1 | 3 | 0.0139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-180_0_4_line_3 |  | 2 | 4 | 0.015744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-180_0_4_line_4 |  | 2 | 5 | 0.022283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-180_0_4_line_5 |  | 3 | 6 | 0.003956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-180_0_4_line_6 |  | 4 | 7 | 0.011847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-180_0_4_line_7 |  | 6 | 8 | 0.024546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-180_0_4_line_8 |  | 7 | 12 | 0.011227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-180_0_4_line_9 |  | 8 | 11 | 0.023403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-180_0_4_line_10 |  | 9 | 10 | 0.074207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-180_0_4_line_11 |  | 9 | 11 | 0.004528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-180_0_4_line_12 |  | 10 | 13 | 0.008005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-180_0_4_line_13 |  | 11 | 14 | 0.007315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-180_0_4_line_14 |  | 12 | 15 | 0.006258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-180_0_4_line_15 |  | 13 | 67 | 0.015505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-180_0_4_line_16 |  | 14 | 65 | 0.024304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-180_0_4_line_17 |  | 15 | 25 | 0.018583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-180_0_4_line_18 |  | 16 | 17 | 0.011798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-180_0_4_line_19 |  | 17 | 18 | 0.034437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-180_0_4_line_20 |  | 18 | 19 | 0.004512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-180_0_4_line_21 |  | 18 | 20 | 0.030003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-180_0_4_line_22 |  | 19 | 21 | 0.003778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-180_0_4_line_23 |  | 20 | 37 | 0.025311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-180_0_4_line_24 |  | 21 | 39 | 0.011237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-180_0_4_line_25 |  | 21 | 40 | 0.015608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-180_0_4_line_26 |  | 22 | 23 | 0.12483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-180_0_4_line_27 |  | 22 | 24 | 0.021692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-180_0_4_line_28 |  | 23 | 25 | 0.016871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-180_0_4_line_29 |  | 23 | 26 | 0.0018386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-180_0_4_line_30 |  | 24 | 41 | 0.00061262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-180_0_4_line_31 |  | 25 | 34 | 0.026083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-180_0_4_line_32 |  | 26 | 42 | 0.0060379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-180_0_4_line_33 |  | 27 | 28 | 0.004839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-180_0_4_line_34 |  | 27 | 29 | 0.020786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-180_0_4_line_35 |  | 28 | 45 | 0.016245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-180_0_4_line_36 |  | 29 | 46 | 0.045341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-180_0_4_line_37 |  | 30 | 31 | 0.035444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-180_0_4_line_38 |  | 30 | 32 | 0.01702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-180_0_4_line_39 |  | 30 | 33 | 0.005657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-180_0_4_line_40 |  | 31 | 38 | 0.0077984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-180_0_4_line_41 |  | 32 | 35 | 0.10121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-180_0_4_line_42 |  | 32 | 36 | 0.006428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-180_0_4_line_43 |  | 33 | 37 | 0.023825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-180_0_4_line_44 |  | 34 | 49 | 0.031418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-180_0_4_line_45 |  | 35 | 50 | 0.0076499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-180_0_4_line_46 |  | 36 | 51 | 0.015112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-180_0_4_line_47 |  | 36 | 52 | 0.013615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
48 | LV_261-180_0_4_line_48 |  | 39 | 56 | 0.0023749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-180_0_4_line_49 |  | 41 | 132 | 0.010977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-180_0_4_line_50 |  | 42 | 53 | 0.014879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-180_0_4_line_51 |  | 43 | 44 | 0.03938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-180_0_4_line_52 |  | 43 | 45 | 0.016823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-180_0_4_line_53 |  | 44 | 48 | 0.019052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-180_0_4_line_54 |  | 45 | 121 | 0.013429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-180_0_4_line_55 |  | 46 | 56 | 0.03255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-180_0_4_line_56 |  | 47 | 48 | 0.0040291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-180_0_4_line_57 |  | 49 | 59 | 0.014049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-180_0_4_line_58 |  | 50 | 83 | 0.015577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-180_0_4_line_59 |  | 51 | 61 | 0.011708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-180_0_4_line_60 |  | 52 | 78 | 0.0093313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
61 | LV_261-180_0_4_line_61 |  | 53 | 54 | 0.0077555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-180_0_4_line_62 |  | 54 | 55 | 0.016123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-180_0_4_line_63 |  | 57 | 58 | 0.021122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-180_0_4_line_64 |  | 58 | 121 | 0.01135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-180_0_4_line_65 |  | 58 | 122 | 0.019129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-180_0_4_line_66 |  | 59 | 60 | 0.013124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-180_0_4_line_67 |  | 59 | 61 | 0.017497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-180_0_4_line_68 |  | 62 | 63 | 0.0016574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-180_0_4_line_69 |  | 63 | 64 | 0.020385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-180_0_4_line_70 |  | 64 | 71 | 0.0034408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-180_0_4_line_71 |  | 65 | 66 | 0.0099652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-180_0_4_line_72 |  | 66 | 68 | 0.011875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-180_0_4_line_73 |  | 67 | 125 | 0.010294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-180_0_4_line_74 |  | 68 | 76 | 0.024573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-180_0_4_line_75 |  | 69 | 70 | 0.010703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-180_0_4_line_76 |  | 69 | 71 | 0.016967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-180_0_4_line_77 |  | 70 | 72 | 0.0044595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-180_0_4_line_78 |  | 72 | 73 | 0.02241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-180_0_4_line_79 |  | 73 | 74 | 0.024192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-180_0_4_line_80 |  | 74 | 75 | 0.012138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_261-180_0_4_line_81 |  | 75 | 84 | 0.013743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-180_0_4_line_82 |  | 76 | 77 | 0.027273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_261-180_0_4_line_83 |  | 77 | 92 | 0.024141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_261-180_0_4_line_84 |  | 77 | 93 | 0.008761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_261-180_0_4_line_85 |  | 78 | 79 | 0.020882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
86 | LV_261-180_0_4_line_86 |  | 79 | 80 | 0.010934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
87 | LV_261-180_0_4_line_87 |  | 80 | 81 | 0.022126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
88 | LV_261-180_0_4_line_88 |  | 81 | 82 | 0.010858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
89 | LV_261-180_0_4_line_89 |  | 82 | 99 | 0.022067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
90 | LV_261-180_0_4_line_90 |  | 83 | 129 | 0.007845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_261-180_0_4_line_91 |  | 84 | 85 | 0.012571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_261-180_0_4_line_92 |  | 85 | 86 | 0.010139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_261-180_0_4_line_93 |  | 85 | 87 | 0.010881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_261-180_0_4_line_94 |  | 86 | 88 | 0.019677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_261-180_0_4_line_95 |  | 87 | 89 | 0.012383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_261-180_0_4_line_96 |  | 88 | 90 | 0.0091171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_261-180_0_4_line_97 |  | 89 | 91 | 0.013779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_261-180_0_4_line_98 |  | 90 | 97 | 0.019011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_261-180_0_4_line_99 |  | 91 | 98 | 0.013848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_261-180_0_4_line_100 |  | 92 | 94 | 0.024779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_261-180_0_4_line_101 |  | 94 | 95 | 0.024464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_261-180_0_4_line_102 |  | 95 | 96 | 0.023217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_261-180_0_4_line_103 |  | 96 | 115 | 0.028218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_261-180_0_4_line_104 |  | 97 | 108 | 0.0099071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_261-180_0_4_line_105 |  | 98 | 117 | 0.013685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_261-180_0_4_line_106 |  | 99 | 100 | 0.010976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_261-180_0_4_line_107 |  | 100 | 101 | 0.010701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_261-180_0_4_line_108 |  | 101 | 102 | 0.012194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_261-180_0_4_line_109 |  | 101 | 103 | 0.033485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-180_0_4_line_110 |  | 102 | 104 | 0.020828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_261-180_0_4_line_111 |  | 103 | 105 | 0.000127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_261-180_0_4_line_112 |  | 104 | 106 | 0.018059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_261-180_0_4_line_113 |  | 105 | 107 | 0.0054743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_261-180_0_4_line_114 |  | 107 | 111 | 0.017276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_261-180_0_4_line_115 |  | 108 | 109 | 0.008391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_261-180_0_4_line_116 |  | 108 | 110 | 0.0098233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_261-180_0_4_line_117 |  | 109 | 111 | 0.021601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_261-180_0_4_line_118 |  | 110 | 114 | 0.018445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_261-180_0_4_line_119 |  | 112 | 113 | 0.00058237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_261-180_0_4_line_120 |  | 113 | 116 | 0.016652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_261-180_0_4_line_121 |  | 114 | 118 | 0.011006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_261-180_0_4_line_122 |  | 115 | 116 | 0.0076924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_261-180_0_4_line_123 |  | 118 | 120 | 0.011072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_261-180_0_4_line_124 |  | 119 | 120 | 0.0082958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_261-180_0_4_line_125 |  | 120 | 127 | 0.01178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_261-180_0_4_line_126 |  | 122 | 123 | 0.02977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_261-180_0_4_line_127 |  | 123 | 124 | 0.00015341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_261-180_0_4_line_128 |  | 126 | 127 | 0.01048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_261-180_0_4_line_129 |  | 128 | 129 | 0.01954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_261-180_0_4_line_130 |  | 130 | 131 | 0.011251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_261-180_0_4_line_131 |  | 131 | 132 | 0.010921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-180_0_4_trafo_63 | 0.63 MVA 20/0.4 kV | 133 | 36 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2680455.0807 | 1250351.5007 | 2680445.6318 | 1250342.1048
1 | 2680483.1328 | 1250383.4468 | 2680459.998 | 1250356.3905 | 2680455.0807 | 1250351.5007
2 | 2680435.2363 | 1250332.926 | 2680437.2324 | 1250334.3764 | 2680440.0566 | 1250336.5608 | 2680445.6318 | 1250342.1048
3 | 2680483.1328 | 1250383.4468 | 2680492.7247 | 1250395.9529
4 | 2680483.1328 | 1250383.4468 | 2680483.6384 | 1250365.129 | 2680486.2757 | 1250362.1737
5 | 2680432.0906 | 1250330.5149 | 2680434.6832 | 1250332.5182 | 2680435.2363 | 1250332.926
6 | 2680492.7247 | 1250395.9529 | 2680501.6054 | 1250391.3479 | 2680503.2427 | 1250390.5014
7 | 2680432.0906 | 1250330.5149 | 2680442.9169 | 1250313.2936 | 2680445.1546 | 1250309.7336
8 | 2680513.2154 | 1250385.3456 | 2680503.2427 | 1250390.5014
9 | 2680457.6092 | 1250289.9202 | 2680445.1546 | 1250309.7336
10 | 2680453.6453 | 1250287.7092 | 2680467.3592 | 1250264.6783 | 2680480.8702 | 1250246.5817 | 2680481.5161 | 1250245.7232 | 2680495.2766 | 1250229.8316 | 2680497.2953 | 1250228.0049
11 | 2680457.6092 | 1250289.9202 | 2680453.6453 | 1250287.7092
12 | 2680503.2308 | 1250222.6339 | 2680497.2953 | 1250228.0049
13 | 2680457.6092 | 1250289.9202 | 2680461.3834 | 1250283.6541
14 | 2680514.0245 | 1250379.1409 | 2680513.2154 | 1250385.3456
15 | 2680514.7897 | 1250212.3059 | 2680513.9201 | 1250212.9613 | 2680503.2308 | 1250222.6339
16 | 2680461.3834 | 1250283.6541 | 2680464.1128 | 1250279.1227 | 2680471.4082 | 1250267.2908 | 2680471.9795 | 1250266.3645 | 2680474.3528 | 1250263.1125
17 | 2680514.0245 | 1250379.1409 | 2680519.3994 | 1250379.7365 | 2680525.9427 | 1250380.4593 | 2680528.1116 | 1250381.9676 | 2680532.1113 | 1250382.0887
18 | 2680591.3965 | 1250439.459 | 2680585.1935 | 1250442.021 | 2680580.879 | 1250444.715
19 | 2680599.2872 | 1250406.075 | 2680591.6454 | 1250433.369 | 2680591.3965 | 1250439.459
20 | 2680603.6576 | 1250407.2464 | 2680599.2872 | 1250406.075
21 | 2680599.2872 | 1250406.075 | 2680609.1477 | 1250377.7391
22 | 2680603.6576 | 1250407.2464 | 2680607.3132 | 1250408.2413
23 | 2680609.1477 | 1250377.7391 | 2680617.4663 | 1250353.8345
24 | 2680607.3132 | 1250408.2413 | 2680608.939 | 1250408.0521 | 2680618.069 | 1250411.019
25 | 2680607.3132 | 1250408.2413 | 2680604.1524 | 1250419.1508 | 2680602.8859 | 1250423.2075
26 | 2680492.9139 | 1250460.3697 | 2680482.4115 | 1250467.0987 | 2680465.0971 | 1250447.8717 | 2680468.1812 | 1250445.9232 | 2680489.9374 | 1250432.1751 | 2680511.3596 | 1250418.0111 | 2680517.2513 | 1250412.7984 | 2680523.652 | 1250406.7921 | 2680530.5497 | 1250401.9933 | 2680535.1099 | 1250397.5409
27 | 2680492.9139 | 1250460.3697 | 2680511.1717 | 1250448.6576
28 | 2680532.1113 | 1250382.0887 | 2680531.2045 | 1250392.7065 | 2680535.1099 | 1250397.5409
29 | 2680535.1099 | 1250397.5409 | 2680536.4259 | 1250396.2568
30 | 2680511.1717 | 1250448.6576 | 2680511.6874 | 1250448.3269
31 | 2680532.1113 | 1250382.0887 | 2680534.0525 | 1250381.4702 | 2680539.1818 | 1250379.027 | 2680543.7447 | 1250375.4864 | 2680551.6699 | 1250365.7048
32 | 2680536.4259 | 1250396.2568 | 2680539.6394 | 1250393.1214 | 2680540.6718 | 1250391.9677
33 | 2680690.7502 | 1250375.1631 | 2680691.4925 | 1250371.1036 | 2680691.9194 | 1250370.5336
34 | 2680690.7502 | 1250375.1631 | 2680680.0449 | 1250386.7816 | 2680676.8313 | 1250390.5957
35 | 2680701.6582 | 1250357.5319 | 2680691.9194 | 1250370.5336
36 | 2680649.0275 | 1250426.3776 | 2680656.2854 | 1250416.2022 | 2680664.966 | 1250404.6785 | 2680676.8313 | 1250390.5957
37 | 2680617.384 | 1250330.6209 | 2680619.6432 | 1250335.4775 | 2680621.7603 | 1250341.3439 | 2680622.3805 | 1250345.7 | 2680622.3454 | 1250349.9471 | 2680617.6314 | 1250364.4009
38 | 2680617.384 | 1250330.6209 | 2680623.0107 | 1250328.7961 | 2680625.667 | 1250325.0072 | 2680623.1587 | 1250319.0354
39 | 2680617.384 | 1250330.6209 | 2680611.9776 | 1250332.3376
40 | 2680615.2133 | 1250371.815 | 2680617.6314 | 1250364.4009
41 | 2680623.1587 | 1250319.0354 | 2680661.8453 | 1250297.3123 | 2680708.7083 | 1250265.1423
42 | 2680623.1587 | 1250319.0354 | 2680620.6649 | 1250313.1082
43 | 2680611.9776 | 1250332.3376 | 2680615.2502 | 1250335.9625 | 2680617.4891 | 1250339.54 | 2680618.6112 | 1250343.069 | 2680619.0664 | 1250347.345 | 2680618.6547 | 1250350.4195 | 2680617.4663 | 1250353.8345
44 | 2680551.6699 | 1250365.7048 | 2680571.4486 | 1250341.2933
45 | 2680708.7083 | 1250265.1423 | 2680715.0152 | 1250260.8128
46 | 2680620.6649 | 1250313.1082 | 2680606.4085 | 1250318.1217
47 | 2680620.6649 | 1250313.1082 | 2680624.6627 | 1250311.706 | 2680633.1705 | 1250307.7595
48 | 2680620.3276 | 1250411.753 | 2680618.069 | 1250411.019
49 | 2680511.6874 | 1250448.3269 | 2680520.941 | 1250442.3815
50 | 2680550.5614 | 1250380.8525 | 2680550.0501 | 1250381.4876 | 2680540.6718 | 1250391.9677
51 | 2680716.2983 | 1250356.3415 | 2680722.3846 | 1250351.821 | 2680727.5132 | 1250348.3328 | 2680737.7016 | 1250341.4108 | 2680743.3013 | 1250337.6955 | 2680746.9964 | 1250335.244 | 2680748.9568 | 1250334.4268
52 | 2680701.6582 | 1250357.5319 | 2680702.8436 | 1250358.0818 | 2680707.6448 | 1250360.3266 | 2680714.1407 | 1250355.6672 | 2680716.2983 | 1250356.3415
53 | 2680748.9568 | 1250334.4268 | 2680758.8262 | 1250330.3126 | 2680764.9863 | 1250328.1394 | 2680766.7084 | 1250327.5291 | 2680766.7084 | 1250327.5291
54 | 2680701.6582 | 1250357.5319 | 2680691.9885 | 1250348.2132
55 | 2680649.0275 | 1250426.3776 | 2680635.3848 | 1250416.9851 | 2680634.51 | 1250416.3616 | 2680620.3276 | 1250411.753
56 | 2680770.6633 | 1250326.7589 | 2680766.7084 | 1250327.5291
57 | 2680580.1157 | 1250330.2473 | 2680578.7824 | 1250332.2417 | 2680571.4486 | 1250341.2933
58 | 2680727.8577 | 1250251.9969 | 2680715.0152 | 1250260.8128
59 | 2680595.2422 | 1250321.6353 | 2680603.8616 | 1250319.0174 | 2680606.4085 | 1250318.1217
60 | 2680633.1705 | 1250307.7595 | 2680637.1915 | 1250305.8943 | 2680641.3943 | 1250303.3776
61 | 2680555.4247 | 1250374.8114 | 2680550.5614 | 1250380.8525
62 | 2680555.4247 | 1250374.8114 | 2680565.535 | 1250362.2526
63 | 2680682.7722 | 1250342.3081 | 2680669.7859 | 1250339.5849 | 2680662.0177 | 1250338.4339
64 | 2680682.7722 | 1250342.3081 | 2680686.7245 | 1250343.1403 | 2680691.9885 | 1250348.2132
65 | 2680682.7722 | 1250342.3081 | 2680679.4875 | 1250332.9231 | 2680678.7356 | 1250330.4777 | 2680684.2451 | 1250326.7948
66 | 2680580.1157 | 1250330.2473 | 2680571.8437 | 1250320.0588
67 | 2680580.1157 | 1250330.2473 | 2680587.7146 | 1250324.9689 | 2680593.9455 | 1250322.0292 | 2680595.2422 | 1250321.6353
68 | 2680521.7144 | 1250341.3974 | 2680522.166 | 1250339.8027
69 | 2680522.166 | 1250339.8027 | 2680522.3361 | 1250339.2021 | 2680529.1874 | 1250325.0514 | 2680531.378 | 1250321.658
70 | 2680531.378 | 1250321.658 | 2680533.2442 | 1250318.7672
71 | 2680480.2274 | 1250255.063 | 2680474.3528 | 1250263.1125
72 | 2680488.0801 | 1250246.1637 | 2680484.9204 | 1250249.6612 | 2680481.0112 | 1250253.9891 | 2680480.2274 | 1250255.063
73 | 2680514.7897 | 1250212.3059 | 2680516.674 | 1250210.8749 | 2680522.9858 | 1250206.0769
74 | 2680504.7955 | 1250228.1725 | 2680502.3358 | 1250230.3835 | 2680488.0801 | 1250246.1637
75 | 2680543.7874 | 1250305.6127 | 2680551.468 | 1250298.1589
76 | 2680543.7874 | 1250305.6127 | 2680538.2955 | 1250310.9425 | 2680533.2442 | 1250318.7672
77 | 2680551.468 | 1250298.1589 | 2680554.6682 | 1250295.0532 | 2680554.6682 | 1250295.0532
78 | 2680572.7971 | 1250281.879 | 2680554.6682 | 1250295.0532
79 | 2680572.7971 | 1250281.879 | 2680580.5178 | 1250276.2684 | 2680592.1663 | 1250267.3875
80 | 2680601.8188 | 1250260.0283 | 2680592.1663 | 1250267.3875
81 | 2680601.8188 | 1250260.0283 | 2680612.7475 | 1250251.6962
82 | 2680525.7654 | 1250210.7872 | 2680519.7945 | 1250215.1427 | 2680517.1179 | 1250217.0966 | 2680504.7955 | 1250228.1725
83 | 2680525.7654 | 1250210.7872 | 2680533.269 | 1250205.3073 | 2680545.8744 | 1250197.4577
84 | 2680530.9771 | 1250217.841 | 2680525.7654 | 1250210.7872
85 | 2680659.0308 | 1250292.2043 | 2680647.7949 | 1250299.545 | 2680641.3943 | 1250303.3776
86 | 2680659.0308 | 1250292.2043 | 2680668.1846 | 1250286.224
87 | 2680686.6207 | 1250273.9905 | 2680678.6386 | 1250279.3942 | 2680668.1846 | 1250286.224
88 | 2680686.6207 | 1250273.9905 | 2680695.6118 | 1250267.9036
89 | 2680713.8851 | 1250255.5328 | 2680695.6118 | 1250267.9036
90 | 2680727.8577 | 1250251.9969 | 2680734.3254 | 1250247.557
91 | 2680622.7445 | 1250244.0744 | 2680612.7475 | 1250251.6962
92 | 2680622.7445 | 1250244.0744 | 2680630.8669 | 1250238.0054
93 | 2680622.7445 | 1250244.0744 | 2680625.5044 | 1250247.6479 | 2680629.3996 | 1250252.6824 | 2680629.3996 | 1250252.6824
94 | 2680630.8669 | 1250238.0054 | 2680646.6295 | 1250226.2277
95 | 2680639.9483 | 1250248.7563 | 2680633.2879 | 1250253.7805 | 2680629.3996 | 1250252.6824
96 | 2680646.6295 | 1250226.2277 | 2680653.933 | 1250220.7706
97 | 2680650.9482 | 1250240.4585 | 2680639.9483 | 1250248.7563
98 | 2680669.1619 | 1250209.3917 | 2680653.933 | 1250220.7706
99 | 2680662.0035 | 1250232.119 | 2680650.9482 | 1250240.4585
100 | 2680545.8744 | 1250197.4577 | 2680566.9081 | 1250184.3595
101 | 2680566.9081 | 1250184.3595 | 2680575.3998 | 1250179.0716 | 2680587.6762 | 1250171.4294
102 | 2680587.6762 | 1250171.4294 | 2680607.3858 | 1250159.16
103 | 2680631.3362 | 1250144.2398 | 2680621.2849 | 1250150.5077 | 2680607.3858 | 1250159.16
104 | 2680677.0983 | 1250203.4617 | 2680669.1619 | 1250209.3917
105 | 2680672.9282 | 1250223.8779 | 2680662.0035 | 1250232.119
106 | 2680713.8851 | 1250255.5328 | 2680722.974 | 1250249.3797
107 | 2680731.8351 | 1250243.3808 | 2680722.974 | 1250249.3797
108 | 2680731.8351 | 1250243.3808 | 2680742.0031 | 1250236.6505
109 | 2680731.8351 | 1250243.3808 | 2680712.458 | 1250216.0719
110 | 2680759.4816 | 1250225.3241 | 2680748.6571 | 1250232.2461 | 2680742.0031 | 1250236.6505
111 | 2680712.3845 | 1250215.9683 | 2680712.458 | 1250216.0719
112 | 2680774.8899 | 1250215.9301 | 2680771.0111 | 1250217.9512 | 2680759.4816 | 1250225.3241
113 | 2680709.2166 | 1250211.5037 | 2680712.3845 | 1250215.9683
114 | 2680699.2191 | 1250197.4139 | 2680709.2166 | 1250211.5037
115 | 2680681.8816 | 1250210.3652 | 2680679.6158 | 1250207.0986 | 2680677.0983 | 1250203.4617
116 | 2680677.0983 | 1250203.4617 | 2680684.9799 | 1250197.5984
117 | 2680699.2191 | 1250197.4139 | 2680681.8816 | 1250210.3652
118 | 2680699.7786 | 1250186.5893 | 2680684.9799 | 1250197.5984
119 | 2680645.5339 | 1250159.8439 | 2680645.8753 | 1250160.3157
120 | 2680636.5695 | 1250145.8233 | 2680642.7874 | 1250156.0487 | 2680645.5339 | 1250159.8439
121 | 2680699.7786 | 1250186.5893 | 2680708.6091 | 1250180.0201
122 | 2680631.3362 | 1250144.2398 | 2680633.4786 | 1250147.7048 | 2680635.4656 | 1250146.4976 | 2680636.5695 | 1250145.8233
123 | 2680717.4924 | 1250173.4116 | 2680708.6091 | 1250180.0201
124 | 2680717.4924 | 1250173.4116 | 2680718.5452 | 1250174.827 | 2680719.1752 | 1250175.6917 | 2680719.8571 | 1250176.6239 | 2680720.7393 | 1250177.8146 | 2680722.0738 | 1250179.6119 | 2680722.4222 | 1250180.0836
125 | 2680717.4924 | 1250173.4116 | 2680721.5425 | 1250170.3979 | 2680726.9144 | 1250166.3405
126 | 2680684.2451 | 1250326.7948 | 2680690.8806 | 1250322.3593 | 2680692.7976 | 1250319.0829 | 2680707.6439 | 1250308.9183
127 | 2680707.7705 | 1250308.8316 | 2680707.6439 | 1250308.9183
128 | 2680726.9144 | 1250166.3405 | 2680735.2768 | 1250160.0244
129 | 2680750.7324 | 1250236.9448 | 2680734.6197 | 1250247.355 | 2680734.3254 | 1250247.557
130 | 2680539.606 | 1250430.4139 | 2680530.1344 | 1250436.4869
131 | 2680520.941 | 1250442.3815 | 2680530.1344 | 1250436.4869

## bus_geodata
| x | y | coords
0 | 2680455.0807 | 1250351.5007
1 | 2680445.6318 | 1250342.1048
2 | 2680483.1328 | 1250383.4468
3 | 2680435.2363 | 1250332.9261
4 | 2680492.7247 | 1250395.9529
5 | 2680486.2757 | 1250362.1737
6 | 2680432.0906 | 1250330.5149
7 | 2680503.2427 | 1250390.5014
8 | 2680445.1546 | 1250309.7336
9 | 2680453.6453 | 1250287.7092
10 | 2680497.2953 | 1250228.0049
11 | 2680457.6092 | 1250289.9202
12 | 2680513.2154 | 1250385.3456
13 | 2680503.2309 | 1250222.6339
14 | 2680461.3834 | 1250283.6541
15 | 2680514.0245 | 1250379.1409
16 | 2680580.879 | 1250444.715
17 | 2680591.3965 | 1250439.459
18 | 2680599.2872 | 1250406.075
19 | 2680603.6576 | 1250407.2464
20 | 2680609.1477 | 1250377.7391
21 | 2680607.3132 | 1250408.2413
22 | 2680492.9139 | 1250460.3697
23 | 2680535.1099 | 1250397.5409
24 | 2680511.1717 | 1250448.6577
25 | 2680532.1113 | 1250382.0887
26 | 2680536.4259 | 1250396.2568
27 | 2680690.7502 | 1250375.1631
28 | 2680691.9194 | 1250370.5336
29 | 2680676.8313 | 1250390.5957
30 | 2680617.384 | 1250330.6209
31 | 2680617.6314 | 1250364.4009
32 | 2680623.1587 | 1250319.0354
33 | 2680611.9776 | 1250332.3376
34 | 2680551.6699 | 1250365.7048
35 | 2680708.7083 | 1250265.1423
36 | 2680620.6649 | 1250313.1082
37 | 2680617.4663 | 1250353.8345
38 | 2680615.2133 | 1250371.815
39 | 2680618.069 | 1250411.019
40 | 2680602.8859 | 1250423.2075
41 | 2680511.6874 | 1250448.3269
42 | 2680540.6718 | 1250391.9677
43 | 2680716.2983 | 1250356.3415
44 | 2680748.9568 | 1250334.4268
45 | 2680701.6582 | 1250357.5319
46 | 2680649.0275 | 1250426.3776
47 | 2680770.6633 | 1250326.7589
48 | 2680766.7084 | 1250327.5291
49 | 2680571.4486 | 1250341.2933
50 | 2680715.0152 | 1250260.8128
51 | 2680606.4085 | 1250318.1217
52 | 2680633.1705 | 1250307.7595
53 | 2680550.5614 | 1250380.8525
54 | 2680555.4247 | 1250374.8114
55 | 2680565.535 | 1250362.2526
56 | 2680620.3276 | 1250411.753
57 | 2680662.0177 | 1250338.4339
58 | 2680682.7722 | 1250342.3081
59 | 2680580.1157 | 1250330.2473
60 | 2680571.8437 | 1250320.0588
61 | 2680595.2422 | 1250321.6353
62 | 2680521.7144 | 1250341.3974
63 | 2680522.166 | 1250339.8027
64 | 2680531.378 | 1250321.658
65 | 2680474.3528 | 1250263.1125
66 | 2680480.2274 | 1250255.063
67 | 2680514.7897 | 1250212.3059
68 | 2680488.0801 | 1250246.1637
69 | 2680543.7874 | 1250305.6127
70 | 2680551.468 | 1250298.1589
71 | 2680533.2442 | 1250318.7672
72 | 2680554.6682 | 1250295.0532
73 | 2680572.7971 | 1250281.879
74 | 2680592.1663 | 1250267.3875
75 | 2680601.8188 | 1250260.0283
76 | 2680504.7955 | 1250228.1725
77 | 2680525.7654 | 1250210.7872
78 | 2680641.3943 | 1250303.3776
79 | 2680659.0308 | 1250292.2043
80 | 2680668.1846 | 1250286.224
81 | 2680686.6207 | 1250273.9905
82 | 2680695.6118 | 1250267.9036
83 | 2680727.8577 | 1250251.9969
84 | 2680612.7475 | 1250251.6962
85 | 2680622.7445 | 1250244.0744
86 | 2680630.8669 | 1250238.0054
87 | 2680629.3996 | 1250252.6824
88 | 2680646.6295 | 1250226.2277
89 | 2680639.9483 | 1250248.7563
90 | 2680653.933 | 1250220.7706
91 | 2680650.9482 | 1250240.4585
92 | 2680545.8744 | 1250197.4577
93 | 2680530.9771 | 1250217.841
94 | 2680566.9081 | 1250184.3595
95 | 2680587.6762 | 1250171.4294
96 | 2680607.3858 | 1250159.16
97 | 2680669.1619 | 1250209.3917
98 | 2680662.0034 | 1250232.119
99 | 2680713.8851 | 1250255.5328
100 | 2680722.974 | 1250249.3797
101 | 2680731.8351 | 1250243.3808
102 | 2680742.0031 | 1250236.6505
103 | 2680712.458 | 1250216.0719
104 | 2680759.4816 | 1250225.3241
105 | 2680712.3845 | 1250215.9683
106 | 2680774.8899 | 1250215.9301
107 | 2680709.2166 | 1250211.5037
108 | 2680677.0983 | 1250203.4617
109 | 2680681.8816 | 1250210.3652
110 | 2680684.9799 | 1250197.5984
111 | 2680699.2191 | 1250197.4139
112 | 2680645.8753 | 1250160.3157
113 | 2680645.5339 | 1250159.8439
114 | 2680699.7786 | 1250186.5893
115 | 2680631.3362 | 1250144.2398
116 | 2680636.5695 | 1250145.8233
117 | 2680672.9282 | 1250223.8779
118 | 2680708.6091 | 1250180.0201
119 | 2680722.4223 | 1250180.0836
120 | 2680717.4924 | 1250173.4116
121 | 2680691.9885 | 1250348.2132
122 | 2680684.2451 | 1250326.7948
123 | 2680707.6439 | 1250308.9183
124 | 2680707.7705 | 1250308.8316
125 | 2680522.9858 | 1250206.0769
126 | 2680735.2768 | 1250160.0244
127 | 2680726.9144 | 1250166.3405
128 | 2680750.7324 | 1250236.9448
129 | 2680734.3254 | 1250247.557
130 | 2680539.606 | 1250430.4139
131 | 2680530.1344 | 1250436.4869
132 | 2680520.941 | 1250442.3815
133 | 2680623.1587 | 1250319.0354

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98078 | -0.36784 | 0.0022276 | 0.00055829
1 | 0.97998 | -0.38341 | 0.0015436 | 0.00038688
2 | 0.98342 | -0.31659 | 0 | 0
3 | 0.97916 | -0.39929 | 0 | 0
4 | 0.98449 | -0.29595 | 0 | 0
5 | 0.9833 | -0.31905 | 0.0061308 | 0.0015365
6 | 0.97893 | -0.40382 | 0 | 0
7 | 0.98529 | -0.28046 | 0.0052493 | 0.0013156
8 | 0.97749 | -0.43194 | 0.0018907 | 0.00047385
9 | 0.97612 | -0.45883 | 0 | 0
10 | 0.97545 | -0.47211 | 0.0028224 | 0.00070736
11 | 0.97616 | -0.45802 | 0 | 0
12 | 0.98611 | -0.26474 | 0 | 0
13 | 0.9754 | -0.47313 | 0.0028805 | 0.00072193
14 | 0.97581 | -0.46488 | 0.006501 | 0.0016293
15 | 0.98656 | -0.25598 | 0 | 0
16 | 0.99273 | -0.13913 | 0.0065621 | 0.0016446
17 | 0.99281 | -0.13776 | 0 | 0
18 | 0.99301 | -0.13376 | 0 | 0
19 | 0.99277 | -0.13834 | 0 | 0
20 | 0.99477 | -0.099875 | 0.0019264 | 0.00048279
21 | 0.99257 | -0.14218 | 0 | 0
22 | 0.9862 | -0.26335 | 0 | 0
23 | 0.98759 | -0.23642 | 0 | 0
24 | 0.98596 | -0.26804 | 0.0029713 | 0.00074468
25 | 0.98791 | -0.23004 | 0 | 0
26 | 0.98757 | -0.23672 | 0.0017306 | 0.00043373
27 | 0.98801 | -0.23043 | 0 | 0
28 | 0.98783 | -0.23404 | 0.0031967 | 0.00080117
29 | 0.98881 | -0.21496 | 0.0015998 | 0.00040096
30 | 0.99829 | -0.032491 | 0 | 0
31 | 0.99819 | -0.034433 | 0.0015559 | 0.00038995
32 | 0.99949 | -0.009673 | 0 | 0
33 | 0.99791 | -0.039777 | 0 | 0
34 | 0.99032 | -0.18394 | 0.0090256 | 0.002262
35 | 0.99862 | -0.026538 | 0.0016666 | 0.0004177
36 | 1 | 0 | -0.37978 | -0.097103
37 | 0.9963 | -0.070525 | 0.0076771 | 0.0019241
38 | 0.99818 | -0.034647 | 0.001575 | 0.00039472
39 | 0.99202 | -0.15288 | 0.0036838 | 0.00092325
40 | 0.99252 | -0.1432 | 0.003675 | 0.00092104
41 | 0.98596 | -0.26814 | 0 | 0
42 | 0.98753 | -0.23751 | 0.0017191 | 0.00043085
43 | 0.98706 | -0.24887 | 0 | 0
44 | 0.98663 | -0.2574 | 0.0056755 | 0.0014224
45 | 0.98725 | -0.24523 | 0 | 0
46 | 0.99061 | -0.18 | 0 | 0
47 | 0.9865 | -0.25991 | 0.0043073 | 0.0010795
48 | 0.98651 | -0.25959 | 0.0021225 | 0.00053195
49 | 0.99347 | -0.1237 | 0.0057039 | 0.0014295
50 | 0.99856 | -0.02759 | 0.0016144 | 0.00040461
51 | 0.99822 | -0.033613 | 0.0051734 | 0.0012966
52 | 0.999 | -0.01882 | 0.0032431 | 0.00081279
53 | 0.98745 | -0.23901 | 0.0019467 | 0.00048788
54 | 0.98743 | -0.23952 | 0.0018387 | 0.00046082
55 | 0.9874 | -0.24006 | 0.0018557 | 0.00046509
56 | 0.99191 | -0.15499 | 0.0067577 | 0.0016937
57 | 0.98663 | -0.25726 | 0.0034015 | 0.00085249
58 | 0.9867 | -0.25597 | 0 | 0
59 | 0.99495 | -0.095472 | 0 | 0
60 | 0.99488 | -0.096798 | 0.0057379 | 0.0014381
61 | 0.99689 | -0.058675 | 0.0025315 | 0.00063446
62 | 0.97062 | -0.56683 | 0.0056848 | 0.0014247
63 | 0.97062 | -0.56666 | 0.0067529 | 0.0016924
64 | 0.97086 | -0.56197 | 0.0031544 | 0.00079056
65 | 0.9748 | -0.4848 | 0.0037224 | 0.00093292
66 | 0.97442 | -0.4923 | 0.0035383 | 0.00088677
67 | 0.97534 | -0.47428 | 0 | 0
68 | 0.974 | -0.50047 | 0.0036467 | 0.00091396
69 | 0.97118 | -0.55556 | 0.0053351 | 0.0013371
70 | 0.97141 | -0.55109 | 0.0055211 | 0.0013837
71 | 0.97091 | -0.56098 | 0.0016808 | 0.00042124
72 | 0.97153 | -0.54877 | 0.0027908 | 0.00069943
73 | 0.97217 | -0.53599 | 0.0036311 | 0.00091004
74 | 0.97296 | -0.52058 | 0.0047346 | 0.0011866
75 | 0.9734 | -0.51181 | 0.0036188 | 0.00090696
76 | 0.97323 | -0.51575 | 0.003281 | 0.0008223
77 | 0.97245 | -0.53109 | 0 | 0
78 | 0.99833 | -0.031475 | 0.0025753 | 0.00064544
79 | 0.99685 | -0.059385 | 0.0037198 | 0.00093227
80 | 0.99609 | -0.073676 | 0.0036816 | 0.0009227
81 | 0.9946 | -0.10194 | 0.0037706 | 0.00094499
82 | 0.99388 | -0.11548 | 0.0037846 | 0.0009485
83 | 0.99847 | -0.029295 | 0.0017122 | 0.00042912
84 | 0.97395 | -0.50097 | 0.0061125 | 0.0015319
85 | 0.97453 | -0.48965 | 0 | 0
86 | 0.97522 | -0.47596 | 0.0087943 | 0.002204
87 | 0.97428 | -0.49456 | 0.0036852 | 0.0009236
88 | 0.97673 | -0.4463 | 0.0057955 | 0.0014525
89 | 0.97404 | -0.49931 | 0.0050762 | 0.0012722
90 | 0.97748 | -0.43162 | 0.0055101 | 0.001381
91 | 0.97383 | -0.50331 | 0.0051657 | 0.0012947
92 | 0.97185 | -0.54294 | 0.0052193 | 0.0013081
93 | 0.97242 | -0.53173 | 0.003945 | 0.00098872
94 | 0.97136 | -0.55272 | 0.0050996 | 0.0012781
95 | 0.97099 | -0.56007 | 0.007203 | 0.0018052
96 | 0.97079 | -0.56397 | 0.0026595 | 0.00066653
97 | 0.97914 | -0.39919 | 0.0054093 | 0.0013557
98 | 0.9737 | -0.50602 | 0.0053605 | 0.0013435
99 | 0.99247 | -0.14232 | 0.002369 | 0.00059372
100 | 0.99109 | -0.16864 | 0.0027264 | 0.00068331
101 | 0.98977 | -0.19384 | 0 | 0
102 | 0.98969 | -0.19538 | 0.0035241 | 0.00088323
103 | 0.98586 | -0.26891 | 0.0015063 | 0.00037751
104 | 0.98962 | -0.19669 | 0.0019208 | 0.0004814
105 | 0.98584 | -0.26919 | 0.0014995 | 0.0003758
106 | 0.9896 | -0.19721 | 0.0016222 | 0.00040655
107 | 0.98522 | -0.28123 | 0.0051491 | 0.0012905
108 | 0.98006 | -0.38135 | 0 | 0
109 | 0.98097 | -0.3635 | 0 | 0
110 | 0.97989 | -0.38461 | 0.0021311 | 0.00053411
111 | 0.98333 | -0.3177 | 0 | 0
112 | 0.97047 | -0.57023 | 0.0028434 | 0.00071262
113 | 0.97047 | -0.5702 | 0.0035672 | 0.00089402
114 | 0.97962 | -0.39 | 0.0031975 | 0.00080138
115 | 0.97062 | -0.56731 | 0 | 0
116 | 0.97057 | -0.56823 | 0 | 0
117 | 0.97363 | -0.50735 | 0.0052817 | 0.0013237
118 | 0.97948 | -0.39259 | 0.0029886 | 0.00074901
119 | 0.97935 | -0.39513 | 0.0036065 | 0.00090388
120 | 0.97938 | -0.39458 | 0 | 0
121 | 0.98692 | -0.25157 | 0.0047758 | 0.0011969
122 | 0.98638 | -0.26222 | 0.0061843 | 0.0015499
123 | 0.98605 | -0.26865 | 0.0072639 | 0.0018205
124 | 0.98605 | -0.26866 | 0.0047933 | 0.0012013
125 | 0.9753 | -0.47505 | 0.0040694 | 0.0010199
126 | 0.9793 | -0.39626 | 0.0017076 | 0.00042796
127 | 0.97931 | -0.39594 | 0.004611 | 0.0011556
128 | 0.99839 | -0.030912 | 0.0029079 | 0.0007288
129 | 0.99844 | -0.029918 | 0.0016375 | 0.0004104
130 | 0.98577 | -0.27171 | 0.0030177 | 0.0007563
131 | 0.9858 | -0.2711 | 0.0030126 | 0.00075504
132 | 0.98586 | -0.26992 | 0.0030501 | 0.00076442
133 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.064883 | 0.016431 | -0.064834 | -0.0164 | 4.8481e-05 | 3.086e-05 | 0.098499 | 0.098499 | 0.098499 | 0.98078 | -0.36784 | 0.97998 | -0.38341 | 27.0603
1 | -0.06711 | -0.016989 | 0.067276 | 0.017094 | 0.00016555 | 0.00010541 | 0.10188 | 0.10188 | 0.10188 | 0.98078 | -0.36784 | 0.98342 | -0.31659 | 27.9887
2 | 0.063291 | 0.016013 | -0.063242 | -0.015982 | 4.8195e-05 | 3.067e-05 | 0.096155 | 0.096156 | 0.096156 | 0.97998 | -0.38341 | 0.97916 | -0.39929 | 26.4164
3 | -0.073407 | -0.018631 | 0.07348 | 0.018677 | 7.2948e-05 | 4.6487e-05 | 0.11116 | 0.11116 | 0.11116 | 0.98342 | -0.31659 | 0.98449 | -0.29595 | 30.5375
4 | 0.0061315 | 0.0015367 | -0.0061308 | -0.0015365 | 7.1926e-07 | 1.7763e-07 | 0.0092776 | 0.0092777 | 0.0092777 | 0.98342 | -0.31659 | 0.9833 | -0.31905 | 2.5488
5 | 0.063242 | 0.015982 | -0.063229 | -0.015973 | 1.3716e-05 | 8.7287e-06 | 0.096156 | 0.096156 | 0.096156 | 0.97916 | -0.39929 | 0.97893 | -0.40382 | 26.4164
6 | -0.07348 | -0.018677 | 0.073535 | 0.018712 | 5.4891e-05 | 3.498e-05 | 0.11116 | 0.11116 | 0.11116 | 0.98449 | -0.29595 | 0.98529 | -0.28046 | 30.5374
7 | 0.063229 | 0.015973 | -0.063143 | -0.015919 | 8.5108e-05 | 5.4161e-05 | 0.096156 | 0.096156 | 0.096156 | 0.97893 | -0.40382 | 0.97749 | -0.43194 | 26.4164
8 | -0.078785 | -0.020028 | 0.078844 | 0.020066 | 5.9701e-05 | 3.8066e-05 | 0.11908 | 0.11908 | 0.11908 | 0.98529 | -0.28046 | 0.98611 | -0.26474 | 32.7154
9 | 0.061253 | 0.015445 | -0.061176 | -0.015397 | 7.6358e-05 | 4.8576e-05 | 0.093278 | 0.093278 | 0.093278 | 0.97749 | -0.43194 | 0.97616 | -0.45802 | 25.6257
10 | 0.0097792 | 0.0024522 | -0.009773 | -0.0024492 | 6.1848e-06 | 3.0313e-06 | 0.014908 | 0.014908 | 0.014908 | 0.97612 | -0.45883 | 0.97545 | -0.47211 | 4.0957
11 | -0.0097792 | -0.0024522 | 0.0097796 | 0.0024524 | 3.7738e-07 | 1.8492e-07 | 0.014908 | 0.014908 | 0.014908 | 0.97612 | -0.45883 | 0.97616 | -0.45802 | 4.0956
12 | 0.0069506 | 0.0017418 | -0.0069503 | -0.0017417 | 3.3747e-07 | 1.1606e-07 | 0.010603 | 0.010603 | 0.010603 | 0.97545 | -0.47211 | 0.9754 | -0.47313 | 2.9129
13 | 0.051397 | 0.012944 | -0.05138 | -0.012934 | 1.6848e-05 | 1.0691e-05 | 0.07837 | 0.07837 | 0.07837 | 0.97616 | -0.45802 | 0.97581 | -0.46488 | 21.5301
14 | -0.078844 | -0.020066 | 0.078878 | 0.020087 | 3.3279e-05 | 2.1219e-05 | 0.11908 | 0.11908 | 0.11908 | 0.98611 | -0.26474 | 0.98656 | -0.25598 | 32.7153
15 | 0.0040697 | 0.0010198 | -0.0040695 | -0.0010198 | 2.2412e-07 | -5.0078e-08 | 0.0062085 | 0.0062086 | 0.0062086 | 0.9754 | -0.47313 | 0.97534 | -0.47428 | 1.7057
16 | 0.044879 | 0.011304 | -0.044836 | -0.011277 | 4.2711e-05 | 2.7032e-05 | 0.068456 | 0.068456 | 0.068456 | 0.97581 | -0.46488 | 0.9748 | -0.4848 | 18.8067
17 | -0.078878 | -0.020087 | 0.078976 | 0.02015 | 9.8822e-05 | 6.3008e-05 | 0.11908 | 0.11908 | 0.11908 | 0.98656 | -0.25598 | 0.98791 | -0.23004 | 32.7153
18 | -0.0065621 | -0.0016446 | 0.0065625 | 0.0016447 | 4.2802e-07 | 1.2138e-07 | 0.009836 | 0.0098359 | 0.009836 | 0.99273 | -0.13913 | 0.99281 | -0.13776 | 2.7022
19 | -0.0065625 | -0.0016447 | 0.0065638 | 0.0016451 | 1.2493e-06 | 3.5417e-07 | 0.0098359 | 0.0098358 | 0.0098359 | 0.99281 | -0.13776 | 0.99301 | -0.13376 | 2.7022
20 | 0.057706 | 0.014563 | -0.057694 | -0.014555 | 1.2662e-05 | 8.0455e-06 | 0.086508 | 0.086508 | 0.086508 | 0.99301 | -0.13376 | 0.99277 | -0.13834 | 23.7659
21 | -0.06427 | -0.016208 | 0.064374 | 0.016275 | 0.00010443 | 6.6448e-05 | 0.096343 | 0.096343 | 0.096343 | 0.99301 | -0.13376 | 0.99477 | -0.099875 | 26.468
22 | 0.057694 | 0.014555 | -0.057683 | -0.014548 | 1.0602e-05 | 6.7367e-06 | 0.086508 | 0.086508 | 0.086508 | 0.99277 | -0.13834 | 0.99257 | -0.14218 | 23.7659
23 | -0.066301 | -0.016757 | 0.066394 | 0.016817 | 9.3449e-05 | 5.9478e-05 | 0.099225 | 0.099225 | 0.099225 | 0.99477 | -0.099875 | 0.9963 | -0.070525 | 27.2596
24 | 0.054008 | 0.013627 | -0.05398 | -0.01361 | 2.7645e-05 | 1.7548e-05 | 0.080998 | 0.080998 | 0.080998 | 0.99257 | -0.14218 | 0.99202 | -0.15288 | 22.2523
25 | 0.0036752 | 0.00092095 | -0.003675 | -0.00092104 | 1.7767e-07 | -8.8014e-08 | 0.0055096 | 0.0055097 | 0.0055097 | 0.99257 | -0.14218 | 0.99252 | -0.1432 | 1.5136
26 | -0.012056 | -0.0030222 | 0.012071 | 0.0030306 | 1.5489e-05 | 8.3179e-06 | 0.01819 | 0.01819 | 0.01819 | 0.9862 | -0.26335 | 0.98759 | -0.23642 | 4.9973
27 | 0.012056 | 0.0030222 | -0.012053 | -0.0030208 | 2.6915e-06 | 1.4459e-06 | 0.01819 | 0.01819 | 0.01819 | 0.9862 | -0.26335 | 0.98596 | -0.26804 | 4.9973
28 | -0.021163 | -0.0053089 | 0.021169 | 0.0053129 | 6.4334e-06 | 3.9014e-06 | 0.031888 | 0.031888 | 0.031888 | 0.98759 | -0.23642 | 0.98791 | -0.23004 | 8.7605
29 | 0.0090918 | 0.0022784 | -0.0090916 | -0.0022783 | 1.2939e-07 | 5.9281e-08 | 0.013699 | 0.013699 | 0.013699 | 0.98759 | -0.23642 | 0.98757 | -0.23672 | 3.7634
30 | 0.0090816 | 0.0022761 | -0.0090816 | -0.0022761 | 4.3157e-08 | 1.9807e-08 | 0.013706 | 0.013706 | 0.013706 | 0.98596 | -0.26804 | 0.98596 | -0.26814 | 3.7654
31 | -0.10015 | -0.025463 | 0.10037 | 0.025605 | 0.00022294 | 0.00014235 | 0.15097 | 0.15097 | 0.15097 | 0.98791 | -0.23004 | 0.99032 | -0.18394 | 41.4758
32 | 0.007361 | 0.0018446 | -0.0073608 | -0.0018445 | 2.7853e-07 | 1.01e-07 | 0.011091 | 0.011091 | 0.011091 | 0.98757 | -0.23672 | 0.98753 | -0.23751 | 3.047
33 | 0.041778 | 0.01049 | -0.041771 | -0.010486 | 7.1857e-06 | 4.5369e-06 | 0.062928 | 0.062928 | 0.062928 | 0.98801 | -0.23043 | 0.98783 | -0.23404 | 17.2879
34 | -0.041778 | -0.01049 | 0.041809 | 0.01051 | 3.0866e-05 | 1.9488e-05 | 0.062928 | 0.062928 | 0.062928 | 0.98801 | -0.23043 | 0.98881 | -0.21496 | 17.2879
35 | 0.038574 | 0.0096847 | -0.038554 | -0.0096718 | 2.0572e-05 | 1.2958e-05 | 0.058113 | 0.058113 | 0.058113 | 0.98783 | -0.23404 | 0.98725 | -0.24523 | 15.965
36 | -0.043409 | -0.010911 | 0.043481 | 0.010957 | 7.258e-05 | 4.5868e-05 | 0.065335 | 0.065335 | 0.065335 | 0.98881 | -0.21496 | 0.99061 | -0.18 | 17.9492
37 | 0.0031312 | 0.00078431 | -0.0031309 | -0.00078459 | 2.8952e-07 | -2.7807e-07 | 0.0046671 | 0.0046672 | 0.0046672 | 0.99829 | -0.032491 | 0.99819 | -0.034433 | 1.2822
38 | -0.077338 | -0.019612 | 0.077423 | 0.019666 | 8.4933e-05 | 5.4134e-05 | 0.11536 | 0.11536 | 0.11536 | 0.99829 | -0.032491 | 0.99949 | -0.009673 | 31.6916
39 | 0.074207 | 0.018827 | -0.074181 | -0.018811 | 2.5992e-05 | 1.6561e-05 | 0.11069 | 0.11069 | 0.11069 | 0.99829 | -0.032491 | 0.99791 | -0.039777 | 30.4095
40 | 0.001575 | 0.00039463 | -0.001575 | -0.00039472 | 1.612e-08 | -9.1622e-08 | 0.0023478 | 0.0023478 | 0.0023478 | 0.99819 | -0.034433 | 0.99818 | -0.034647 | 0.64501
41 | 0.0095475 | 0.0023943 | -0.0095399 | -0.0023907 | 7.6691e-06 | 3.5829e-06 | 0.014215 | 0.014215 | 0.014215 | 0.99949 | -0.009673 | 0.99862 | -0.026538 | 3.9052
42 | -0.08697 | -0.02206 | 0.087011 | 0.022086 | 4.047e-05 | 2.5816e-05 | 0.12957 | 0.12957 | 0.12957 | 0.99949 | -0.009673 | 1 | 0 | 35.5967
43 | 0.074181 | 0.018811 | -0.074071 | -0.018741 | 0.00010947 | 6.9749e-05 | 0.11069 | 0.11069 | 0.11069 | 0.99791 | -0.039777 | 0.9963 | -0.070525 | 30.4095
44 | -0.10939 | -0.027868 | 0.10971 | 0.028071 | 0.00031895 | 0.00020372 | 0.16453 | 0.16453 | 0.16453 | 0.99032 | -0.18394 | 0.99347 | -0.1237 | 45.2014
45 | 0.0078732 | 0.001973 | -0.0078729 | -0.0019729 | 3.9483e-07 | 1.5261e-07 | 0.011732 | 0.011732 | 0.011732 | 0.99862 | -0.026538 | 0.99856 | -0.02759 | 3.223
46 | 0.1296 | 0.033341 | -0.12939 | -0.033206 | 0.00021142 | 0.00013511 | 0.19315 | 0.19315 | 0.19315 | 1 | 0 | 0.99822 | -0.033613 | 53.0627
47 | 0.16152 | 0.041677 | -0.16138 | -0.041582 | 0.00014799 | 9.4359e-05 | 0.24077 | 0.24077 | 0.24077 | 1 | 0 | 0.999 | -0.01882 | 33.0734
48 | 0.050296 | 0.012687 | -0.050291 | -0.012683 | 5.0728e-06 | 3.2159e-06 | 0.075473 | 0.075473 | 0.075473 | 0.99202 | -0.15288 | 0.99191 | -0.15499 | 20.7342
49 | 0.0090816 | 0.0022761 | -0.0090808 | -0.0022757 | 7.7328e-07 | 3.5492e-07 | 0.013706 | 0.013706 | 0.013706 | 0.98596 | -0.26814 | 0.98586 | -0.26992 | 3.7654
50 | 0.0056416 | 0.0014136 | -0.0056412 | -0.0014136 | 4.032e-07 | 6.7701e-08 | 0.0085008 | 0.0085008 | 0.0085008 | 0.98753 | -0.23751 | 0.98745 | -0.23901 | 2.3354
51 | 0.012111 | 0.0030367 | -0.012106 | -0.0030341 | 4.9228e-06 | 2.6475e-06 | 0.018258 | 0.018258 | 0.018258 | 0.98706 | -0.24887 | 0.98663 | -0.2574 | 5.016
52 | -0.012111 | -0.0030367 | 0.012113 | 0.0030378 | 2.103e-06 | 1.1309e-06 | 0.018258 | 0.018258 | 0.018258 | 0.98706 | -0.24887 | 0.98725 | -0.24523 | 5.0159
53 | 0.0064306 | 0.0016116 | -0.0064299 | -0.0016115 | 6.7202e-07 | 1.8682e-07 | 0.0096985 | 0.0096986 | 0.0096986 | 0.98663 | -0.2574 | 0.98651 | -0.25959 | 2.6644
54 | 0.026441 | 0.0066339 | -0.026433 | -0.006629 | 7.999e-06 | 4.9477e-06 | 0.039855 | 0.039855 | 0.039855 | 0.98725 | -0.24523 | 0.98692 | -0.25157 | 10.9491
55 | -0.043481 | -0.010957 | 0.043533 | 0.01099 | 5.2104e-05 | 3.2927e-05 | 0.065335 | 0.065335 | 0.065335 | 0.99061 | -0.18 | 0.99191 | -0.15499 | 17.9492
56 | -0.0043073 | -0.0010795 | 0.0043074 | 0.0010795 | 6.3779e-08 | -1.0623e-08 | 0.0064971 | 0.0064971 | 0.0064971 | 0.9865 | -0.25991 | 0.98651 | -0.25959 | 1.7849
57 | -0.11542 | -0.029501 | 0.11557 | 0.029602 | 0.00015781 | 0.00010082 | 0.17308 | 0.17308 | 0.17308 | 0.99347 | -0.1237 | 0.99495 | -0.095472 | 47.5484
58 | 0.0062585 | 0.0015683 | -0.0062579 | -0.0015681 | 5.0806e-07 | 1.214e-07 | 0.009326 | 0.0093261 | 0.0093261 | 0.99856 | -0.02759 | 0.99847 | -0.029295 | 2.5621
59 | 0.12421 | 0.031909 | -0.12406 | -0.031813 | 0.00015097 | 9.6471e-05 | 0.18544 | 0.18544 | 0.18544 | 0.99822 | -0.033613 | 0.99689 | -0.058675 | 50.9441
60 | 0.15813 | 0.040769 | -0.15803 | -0.040707 | 9.74e-05 | 6.2092e-05 | 0.23594 | 0.23594 | 0.23594 | 0.999 | -0.01882 | 0.99833 | -0.031475 | 32.4099
61 | 0.0036946 | 0.0009257 | -0.0036945 | -0.00092574 | 9.0145e-08 | -4.1514e-08 | 0.0055674 | 0.0055674 | 0.0055674 | 0.98745 | -0.23901 | 0.98743 | -0.23952 | 1.5295
62 | 0.0018558 | 0.00046491 | -0.0018557 | -0.00046509 | 4.7285e-08 | -1.7597e-07 | 0.0027965 | 0.0027966 | 0.0027966 | 0.98743 | -0.23952 | 0.9874 | -0.24006 | 0.7683
63 | -0.0034015 | -0.00085249 | 0.0034017 | 0.00085235 | 2.0844e-07 | -1.3636e-07 | 0.00513 | 0.0051299 | 0.00513 | 0.98663 | -0.25726 | 0.9867 | -0.25597 | 1.4093
64 | -0.021652 | -0.0054293 | 0.021657 | 0.0054321 | 4.5382e-06 | 2.7595e-06 | 0.032654 | 0.032654 | 0.032654 | 0.9867 | -0.25597 | 0.98692 | -0.25157 | 8.9709
65 | 0.018251 | 0.0045769 | -0.018245 | -0.0045737 | 5.4344e-06 | 3.2337e-06 | 0.027524 | 0.027524 | 0.027524 | 0.9867 | -0.25597 | 0.98638 | -0.26222 | 7.5616
66 | 0.0057383 | 0.0014381 | -0.0057379 | -0.0014381 | 3.6247e-07 | 6.155e-08 | 0.008582 | 0.0085821 | 0.0085821 | 0.99495 | -0.095472 | 0.99488 | -0.096798 | 2.3577
67 | -0.12131 | -0.03104 | 0.12153 | 0.031178 | 0.00021652 | 0.00013835 | 0.18166 | 0.18166 | 0.18166 | 0.99495 | -0.095472 | 0.99689 | -0.058675 | 49.9061
68 | -0.0056848 | -0.0014247 | 0.0056848 | 0.0014247 | 4.7207e-08 | 9.7275e-09 | 0.0087151 | 0.0087151 | 0.0087151 | 0.97062 | -0.56683 | 0.97062 | -0.56666 | 2.3943
69 | -0.012438 | -0.0031172 | 0.012441 | 0.0031187 | 2.7794e-06 | 1.5268e-06 | 0.019068 | 0.019068 | 0.019068 | 0.97062 | -0.56666 | 0.97086 | -0.56197 | 5.2384
70 | -0.015595 | -0.0039093 | 0.015596 | 0.0039097 | 7.3717e-07 | 4.2924e-07 | 0.023902 | 0.023902 | 0.023902 | 0.97086 | -0.56197 | 0.97091 | -0.56098 | 6.5666
71 | 0.041114 | 0.010344 | -0.041099 | -0.010335 | 1.4726e-05 | 9.3003e-06 | 0.062774 | 0.062774 | 0.062774 | 0.9748 | -0.4848 | 0.97442 | -0.4923 | 17.2457
72 | 0.037561 | 0.0094484 | -0.037546 | -0.0094391 | 1.4657e-05 | 9.2327e-06 | 0.057371 | 0.057371 | 0.057371 | 0.97442 | -0.4923 | 0.974 | -0.50047 | 15.7613
73 | 0.0040695 | 0.0010198 | -0.0040694 | -0.0010199 | 1.4881e-07 | -3.3235e-08 | 0.0062086 | 0.0062086 | 0.0062086 | 0.97534 | -0.47428 | 0.9753 | -0.47505 | 1.7057
74 | 0.0339 | 0.0085252 | -0.033875 | -0.0085096 | 2.4726e-05 | 1.5519e-05 | 0.0518 | 0.0518 | 0.0518 | 0.974 | -0.50047 | 0.97323 | -0.51575 | 14.2308
75 | -0.022616 | -0.0056707 | 0.022621 | 0.0056737 | 4.8194e-06 | 2.952e-06 | 0.034652 | 0.034652 | 0.034652 | 0.97118 | -0.55556 | 0.97141 | -0.55109 | 9.5199
76 | 0.017281 | 0.0043336 | -0.017276 | -0.004331 | 4.4607e-06 | 2.645e-06 | 0.026478 | 0.026478 | 0.026478 | 0.97118 | -0.55556 | 0.97091 | -0.56098 | 7.2742
77 | -0.028142 | -0.0070574 | 0.028145 | 0.0070593 | 3.1079e-06 | 1.9338e-06 | 0.04311 | 0.04311 | 0.04311 | 0.97141 | -0.55109 | 0.97153 | -0.54877 | 11.8433
78 | -0.030936 | -0.0077587 | 0.030955 | 0.0077705 | 1.8869e-05 | 1.1798e-05 | 0.047384 | 0.047384 | 0.047384 | 0.97153 | -0.54877 | 0.97217 | -0.53599 | 13.0176
79 | -0.034586 | -0.0086806 | 0.034611 | 0.0086965 | 2.5427e-05 | 1.5973e-05 | 0.052942 | 0.052941 | 0.052942 | 0.97217 | -0.53599 | 0.97296 | -0.52058 | 14.5444
80 | -0.039346 | -0.0098831 | 0.039362 | 0.0098935 | 1.6486e-05 | 1.04e-05 | 0.060183 | 0.060182 | 0.060183 | 0.97296 | -0.52058 | 0.9734 | -0.51181 | 16.5337
81 | -0.042981 | -0.010801 | 0.043003 | 0.010815 | 2.2255e-05 | 1.4072e-05 | 0.065714 | 0.065714 | 0.065714 | 0.9734 | -0.51181 | 0.97395 | -0.50097 | 18.0534
82 | 0.030594 | 0.0076873 | -0.030571 | -0.0076734 | 2.2385e-05 | 1.3988e-05 | 0.046784 | 0.046784 | 0.046784 | 0.97323 | -0.51575 | 0.97245 | -0.53109 | 12.8526
83 | 0.026626 | 0.0066847 | -0.026611 | -0.0066754 | 1.5031e-05 | 9.3204e-06 | 0.040747 | 0.040747 | 0.040747 | 0.97245 | -0.53109 | 0.97185 | -0.54294 | 11.1942
84 | 0.0039452 | 0.00098869 | -0.003945 | -0.00098872 | 1.1973e-07 | -3.2063e-08 | 0.0060367 | 0.0060368 | 0.0060368 | 0.97245 | -0.53109 | 0.97242 | -0.53173 | 1.6585
85 | 0.15546 | 0.040062 | -0.15525 | -0.039927 | 0.00021093 | 0.00013445 | 0.23211 | 0.23211 | 0.23211 | 0.99833 | -0.031475 | 0.99685 | -0.059385 | 31.8826
86 | 0.15153 | 0.038995 | -0.15142 | -0.038928 | 0.00010523 | 6.706e-05 | 0.22655 | 0.22655 | 0.22655 | 0.99685 | -0.059385 | 0.99609 | -0.073676 | 31.1199
87 | 0.14774 | 0.038005 | -0.14754 | -0.037876 | 0.00020273 | 0.00012917 | 0.22105 | 0.22105 | 0.22105 | 0.99609 | -0.073676 | 0.9946 | -0.10194 | 30.3645
88 | 0.14377 | 0.036931 | -0.14367 | -0.036871 | 9.4468e-05 | 6.0178e-05 | 0.21541 | 0.21541 | 0.21541 | 0.9946 | -0.10194 | 0.99388 | -0.11548 | 29.5897
89 | 0.13989 | 0.035923 | -0.13971 | -0.035807 | 0.00018203 | 0.00011593 | 0.20975 | 0.20975 | 0.20975 | 0.99388 | -0.11548 | 0.99247 | -0.14232 | 28.8114
90 | 0.0045457 | 0.001139 | -0.0045456 | -0.001139 | 1.3501e-07 | -1.6196e-08 | 0.0067744 | 0.0067744 | 0.0067744 | 0.99847 | -0.029295 | 0.99844 | -0.029918 | 1.8611
91 | -0.049116 | -0.012347 | 0.049142 | 0.012363 | 2.6555e-05 | 1.6838e-05 | 0.075053 | 0.075053 | 0.075053 | 0.97395 | -0.50097 | 0.97453 | -0.48965 | 20.619
92 | -0.073727 | -0.01853 | 0.073775 | 0.018561 | 4.8202e-05 | 3.0723e-05 | 0.11259 | 0.11259 | 0.11259 | 0.97453 | -0.48965 | 0.97522 | -0.47596 | 30.9323
93 | 0.024585 | 0.0061666 | -0.024579 | -0.0061631 | 5.7502e-06 | 3.5446e-06 | 0.03754 | 0.03754 | 0.03754 | 0.97453 | -0.48965 | 0.97428 | -0.49456 | 10.3133
94 | -0.082569 | -0.020765 | 0.082687 | 0.020839 | 0.00011717 | 7.4741e-05 | 0.12601 | 0.12601 | 0.12601 | 0.97522 | -0.47596 | 0.97673 | -0.4463 | 34.6187
95 | 0.020894 | 0.0052395 | -0.020889 | -0.0052366 | 4.7291e-06 | 2.8724e-06 | 0.031912 | 0.031912 | 0.031912 | 0.97428 | -0.49456 | 0.97404 | -0.49931 | 8.7671
96 | -0.088482 | -0.022292 | 0.088544 | 0.022332 | 6.2163e-05 | 3.967e-05 | 0.13484 | 0.13484 | 0.13484 | 0.97673 | -0.4463 | 0.97748 | -0.43162 | 37.0442
97 | 0.015813 | 0.0039644 | -0.01581 | -0.0039626 | 3.0153e-06 | 1.7583e-06 | 0.024157 | 0.024157 | 0.024157 | 0.97404 | -0.49931 | 0.97383 | -0.50331 | 6.6366
98 | -0.094054 | -0.023713 | 0.094201 | 0.023806 | 0.00014625 | 9.3359e-05 | 0.14323 | 0.14323 | 0.14323 | 0.97748 | -0.43162 | 0.97914 | -0.39919 | 39.3486
99 | 0.010644 | 0.002668 | -0.010643 | -0.0026672 | 1.3737e-06 | 7.0687e-07 | 0.016264 | 0.016264 | 0.016264 | 0.97383 | -0.50331 | 0.9737 | -0.50602 | 4.4682
100 | 0.021392 | 0.0053673 | -0.021382 | -0.0053612 | 9.9697e-06 | 6.0737e-06 | 0.032756 | 0.032756 | 0.032756 | 0.97185 | -0.54294 | 0.97136 | -0.55272 | 8.9988
101 | 0.016282 | 0.0040831 | -0.016277 | -0.0040798 | 5.7081e-06 | 3.3505e-06 | 0.024944 | 0.024944 | 0.024944 | 0.97136 | -0.55272 | 0.97099 | -0.56007 | 6.8527
102 | 0.0090737 | 0.0022745 | -0.009072 | -0.0022737 | 1.6834e-06 | 7.903e-07 | 0.013905 | 0.013905 | 0.013905 | 0.97099 | -0.56007 | 0.97079 | -0.56397 | 3.8202
103 | 0.0064125 | 0.0016072 | -0.0064115 | -0.0016069 | 1.0223e-06 | 3.0545e-07 | 0.009829 | 0.0098292 | 0.0098292 | 0.97079 | -0.56397 | 0.97062 | -0.56731 | 2.7003
104 | -0.09961 | -0.025162 | 0.099695 | 0.025216 | 8.5215e-05 | 5.4413e-05 | 0.15145 | 0.15145 | 0.15145 | 0.97914 | -0.39919 | 0.98006 | -0.38135 | 41.607
105 | 0.0052821 | 0.0013238 | -0.0052817 | -0.0013237 | 3.3438e-07 | 4.3805e-08 | 0.0080721 | 0.0080722 | 0.0080722 | 0.9737 | -0.50602 | 0.97363 | -0.50735 | 2.2176
106 | 0.13734 | 0.035213 | -0.13716 | -0.035101 | 0.000175 | 0.00011186 | 0.2062 | 0.2062 | 0.2062 | 0.99247 | -0.14232 | 0.99109 | -0.16864 | 56.647
107 | 0.13444 | 0.034418 | -0.13427 | -0.034313 | 0.0001639 | 0.00010476 | 0.2021 | 0.2021 | 0.2021 | 0.99109 | -0.16864 | 0.98977 | -0.19384 | 55.5225
108 | 0.0070679 | 0.001771 | -0.0070674 | -0.0017709 | 5.1627e-07 | 1.7371e-07 | 0.010626 | 0.010626 | 0.010626 | 0.98977 | -0.19384 | 0.98969 | -0.19538 | 2.9192
109 | 0.12721 | 0.032542 | -0.12674 | -0.032248 | 0.00046038 | 0.00029421 | 0.19148 | 0.19148 | 0.19148 | 0.98977 | -0.19384 | 0.98586 | -0.26891 | 52.6034
110 | 0.0035432 | 0.00088762 | -0.003543 | -0.00088774 | 2.2166e-07 | -1.2577e-07 | 0.0053271 | 0.0053272 | 0.0053272 | 0.98969 | -0.19538 | 0.98962 | -0.19669 | 1.4635
111 | 0.12524 | 0.03187 | -0.12524 | -0.031869 | 1.7049e-06 | 1.0895e-06 | 0.1892 | 0.1892 | 0.1892 | 0.98586 | -0.26891 | 0.98584 | -0.26919 | 51.9788
112 | 0.0016222 | 0.00040635 | -0.0016222 | -0.00040655 | 4.029e-08 | -2.0624e-07 | 0.0024391 | 0.0024392 | 0.0024392 | 0.98962 | -0.19669 | 0.9896 | -0.19721 | 0.6701
113 | 0.12374 | 0.031493 | -0.12367 | -0.031447 | 7.174e-05 | 4.5844e-05 | 0.18694 | 0.18694 | 0.18694 | 0.98584 | -0.26919 | 0.98522 | -0.28123 | 51.3571
114 | 0.11852 | 0.030157 | -0.11831 | -0.030024 | 0.00020796 | 0.00013288 | 0.17916 | 0.17916 | 0.17916 | 0.98522 | -0.28123 | 0.98333 | -0.3177 | 49.2206
115 | -0.11795 | -0.029793 | 0.11805 | 0.029858 | 0.000101 | 6.4537e-05 | 0.17916 | 0.17916 | 0.17916 | 0.98006 | -0.38135 | 0.98097 | -0.3635 | 49.2206
116 | 0.018252 | 0.0045774 | -0.01825 | -0.0045757 | 2.8293e-06 | 1.687e-06 | 0.027714 | 0.027714 | 0.027714 | 0.98006 | -0.38135 | 0.97989 | -0.38461 | 7.6137
117 | -0.11805 | -0.029858 | 0.11831 | 0.030024 | 0.00026002 | 0.00016614 | 0.17916 | 0.17916 | 0.17916 | 0.98097 | -0.3635 | 0.98333 | -0.3177 | 49.2206
118 | 0.016118 | 0.0040416 | -0.016114 | -0.0040392 | 4.1441e-06 | 2.42e-06 | 0.024477 | 0.024478 | 0.024478 | 0.97989 | -0.38461 | 0.97962 | -0.39 | 6.7246
119 | -0.0028434 | -0.00071262 | 0.0028434 | 0.00071262 | 4.1511e-09 | -4.5392e-09 | 0.0043598 | 0.0043598 | 0.0043598 | 0.97047 | -0.57023 | 0.97047 | -0.5702 | 1.1977
120 | -0.0064106 | -0.0016066 | 0.0064112 | 0.0016068 | 6.0332e-07 | 1.8035e-07 | 0.0098293 | 0.0098292 | 0.0098293 | 0.97047 | -0.5702 | 0.97057 | -0.56823 | 2.7003
121 | 0.012917 | 0.0032378 | -0.012915 | -0.0032369 | 1.5889e-06 | 8.7833e-07 | 0.019621 | 0.019621 | 0.019621 | 0.97962 | -0.39 | 0.97948 | -0.39259 | 5.3903
122 | 0.0064115 | 0.0016069 | -0.0064112 | -0.0016068 | 2.7869e-07 | 8.3293e-08 | 0.0098292 | 0.0098292 | 0.0098292 | 0.97062 | -0.56731 | 0.97057 | -0.56823 | 2.7003
123 | 0.0099266 | 0.0024879 | -0.0099257 | -0.0024874 | 9.4422e-07 | 4.6496e-07 | 0.01508 | 0.01508 | 0.01508 | 0.97948 | -0.39259 | 0.97938 | -0.39458 | 4.143
124 | -0.0036065 | -0.00090388 | 0.0036066 | 0.00090383 | 9.3411e-08 | -4.4608e-08 | 0.0054797 | 0.0054796 | 0.0054797 | 0.97935 | -0.39513 | 0.97938 | -0.39458 | 1.5054
125 | 0.0063191 | 0.0015836 | -0.0063187 | -0.0015835 | 4.072e-07 | 1.1237e-07 | 0.0096008 | 0.0096008 | 0.0096008 | 0.97938 | -0.39458 | 0.97931 | -0.39594 | 2.6376
126 | 0.012061 | 0.0030238 | -0.012057 | -0.0030218 | 3.6959e-06 | 1.9855e-06 | 0.018195 | 0.018195 | 0.018195 | 0.98638 | -0.26222 | 0.98605 | -0.26865 | 4.9987
127 | 0.0047933 | 0.0012013 | -0.0047933 | -0.0012013 | 3.0099e-09 | -3.0372e-11 | 0.0072334 | 0.0072334 | 0.0072334 | 0.98605 | -0.26865 | 0.98605 | -0.26866 | 1.9872
128 | -0.0017076 | -0.00042796 | 0.0017076 | 0.00042785 | 2.6456e-08 | -1.1492e-07 | 0.0025946 | 0.0025946 | 0.0025946 | 0.9793 | -0.39626 | 0.97931 | -0.39594 | 0.71281
129 | -0.0029079 | -0.0007288 | 0.0029081 | 0.00072863 | 1.3764e-07 | -1.6745e-07 | 0.004334 | 0.004334 | 0.004334 | 0.99839 | -0.030912 | 0.99844 | -0.029918 | 1.1907
130 | -0.0030177 | -0.0007563 | 0.0030177 | 0.00075621 | 8.7545e-08 | -8.7415e-08 | 0.0045551 | 0.0045551 | 0.0045551 | 0.98577 | -0.27171 | 0.9858 | -0.2711 | 1.2514
131 | -0.0060304 | -0.0015112 | 0.0060307 | 0.0015113 | 3.3932e-07 | 7.792e-08 | 0.0091025 | 0.0091024 | 0.0091025 | 0.9858 | -0.2711 | 0.98586 | -0.26992 | 2.5007

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.37978 | 0.097103

## res_load
| p_mw | q_mvar
0 | 0.0022276 | 0.00055829
1 | 0.0015436 | 0.00038688
2 | 0.0061308 | 0.0015365
3 | 0.0052493 | 0.0013156
4 | 0.0018907 | 0.00047385
5 | 0.0028224 | 0.00070736
6 | 0.0028805 | 0.00072193
7 | 0.006501 | 0.0016293
8 | 0.0065621 | 0.0016446
9 | 0.0019264 | 0.00048279
10 | 0.0029713 | 0.00074468
11 | 0.0017306 | 0.00043373
12 | 0.0031967 | 0.00080117
13 | 0.0015998 | 0.00040096
14 | 0.0015559 | 0.00038995
15 | 0.0090256 | 0.002262
16 | 0.0016666 | 0.0004177
17 | 0.0076771 | 0.0019241
18 | 0.001575 | 0.00039472
19 | 0.0036838 | 0.00092325
20 | 0.003675 | 0.00092104
21 | 0.0017191 | 0.00043085
22 | 0.0056755 | 0.0014224
23 | 0.0043073 | 0.0010795
24 | 0.0021225 | 0.00053195
25 | 0.0057039 | 0.0014295
26 | 0.0016144 | 0.00040461
27 | 0.0051734 | 0.0012966
28 | 0.0032431 | 0.00081279
29 | 0.0019467 | 0.00048788
30 | 0.0018387 | 0.00046082
31 | 0.0018557 | 0.00046509
32 | 0.0067577 | 0.0016937
33 | 0.0034015 | 0.00085249
34 | 0.0057379 | 0.0014381
35 | 0.0025315 | 0.00063446
36 | 0.0056848 | 0.0014247
37 | 0.0067529 | 0.0016924
38 | 0.0031544 | 0.00079056
39 | 0.0037224 | 0.00093292
40 | 0.0035383 | 0.00088677
41 | 0.0036467 | 0.00091396
42 | 0.0053351 | 0.0013371
43 | 0.0055211 | 0.0013837
44 | 0.0016808 | 0.00042124
45 | 0.0027908 | 0.00069943
46 | 0.0036311 | 0.00091004
47 | 0.0047346 | 0.0011866
48 | 0.0036188 | 0.00090696
49 | 0.003281 | 0.0008223
50 | 0.0025753 | 0.00064544
51 | 0.0037198 | 0.00093227
52 | 0.0036816 | 0.0009227
53 | 0.0037706 | 0.00094499
54 | 0.0037846 | 0.0009485
55 | 0.0017122 | 0.00042912
56 | 0.0061125 | 0.0015319
57 | 0.0087943 | 0.002204
58 | 0.0036852 | 0.0009236
59 | 0.0057955 | 0.0014525
60 | 0.0050762 | 0.0012722
61 | 0.0055101 | 0.001381
62 | 0.0051657 | 0.0012947
63 | 0.0052193 | 0.0013081
64 | 0.003945 | 0.00098872
65 | 0.0050996 | 0.0012781
66 | 0.007203 | 0.0018052
67 | 0.0026595 | 0.00066653
68 | 0.0054093 | 0.0013557
69 | 0.0053605 | 0.0013435
70 | 0.002369 | 0.00059372
71 | 0.0027264 | 0.00068331
72 | 0.0035241 | 0.00088323
73 | 0.0015063 | 0.00037751
74 | 0.0019208 | 0.0004814
75 | 0.0014995 | 0.0003758
76 | 0.0016222 | 0.00040655
77 | 0.0051491 | 0.0012905
78 | 0.0021311 | 0.00053411
79 | 0.0028434 | 0.00071262
80 | 0.0035672 | 0.00089402
81 | 0.0031975 | 0.00080138
82 | 0.0052817 | 0.0013237
83 | 0.0029886 | 0.00074901
84 | 0.0036065 | 0.00090388
85 | 0.0047758 | 0.0011969
86 | 0.0061843 | 0.0015499
87 | 0.0072639 | 0.0018205
88 | 0.0047933 | 0.0012013
89 | 0.0040694 | 0.0010199
90 | 0.0017076 | 0.00042796
91 | 0.004611 | 0.0011556
92 | 0.0029079 | 0.0007288
93 | 0.0016375 | 0.0004104
94 | 0.0030177 | 0.0007563
95 | 0.0030126 | 0.00075504
96 | 0.0030501 | 0.00076442

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1