## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-197_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-197_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-197_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-197_0_5_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_261-197_0_5_node_49 | 0.4 | n |  | TRUE
5 | bus_LV_261-197_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-197_0_5_node_146 | 0.4 | n |  | TRUE
7 | bus_LV_261-197_0_5_node_70 | 0.4 | n |  | TRUE
8 | bus_LV_261-197_0_5_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_261-197_0_5_node_43 | 0.4 | n |  | TRUE
10 | bus_LV_261-197_0_5_node_42 | 0.4 | n |  | TRUE
11 | bus_LV_261-197_0_5_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_261-197_0_5_node_19 | 0.4 | n |  | TRUE
13 | bus_LV_261-197_0_5_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_261-197_0_5_node_103 | 0.4 | n |  | TRUE
15 | bus_LV_261-197_0_5_node_33 | 0.4 | n |  | TRUE
16 | bus_LV_261-197_0_5_node_39 | 0.4 | n |  | TRUE
17 | bus_LV_261-197_0_5_node_95 | 0.4 | n |  | TRUE
18 | bus_LV_261-197_0_5_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_261-197_0_5_node_117 | 0.4 | n |  | TRUE
20 | bus_LV_261-197_0_5_node_81 | 0.4 | n |  | TRUE
21 | bus_LV_261-197_0_5_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_261-197_0_5_node_114 | 0.4 | n |  | TRUE
23 | bus_LV_261-197_0_5_node_112 | 0.4 | n |  | TRUE
24 | bus_LV_261-197_0_5_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_261-197_0_5_node_100 | 0.4 | n |  | TRUE
26 | bus_LV_261-197_0_5_node_98 | 0.4 | n |  | TRUE
27 | bus_LV_261-197_0_5_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_261-197_0_5_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_261-197_0_5_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_261-197_0_5_node_113 | 0.4 | n |  | TRUE
31 | bus_LV_261-197_0_5_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_261-197_0_5_node_38 | 0.4 | n |  | TRUE
33 | bus_LV_261-197_0_5_node_125 | 0.4 | n |  | TRUE
34 | bus_LV_261-197_0_5_node_129 | 0.4 | n |  | TRUE
35 | bus_LV_261-197_0_5_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_261-197_0_5_node_109 | 0.4 | n |  | TRUE
37 | bus_LV_261-197_0_5_node_118 | 0.4 | n |  | TRUE
38 | bus_LV_261-197_0_5_node_34 | 0.4 | n |  | TRUE
39 | bus_LV_261-197_0_5_node_80 | 0.4 | n |  | TRUE
40 | bus_LV_261-197_0_5_node_22 | 0.4 | n |  | TRUE
41 | bus_LV_261-197_0_5_node_29 | 0.4 | n |  | TRUE
42 | bus_LV_261-197_0_5_node_124 | 0.4 | n |  | TRUE
43 | bus_LV_261-197_0_5_node_99 | 0.4 | n |  | TRUE
44 | bus_LV_261-197_0_5_node_25 | 0.4 | n |  | TRUE
45 | bus_LV_261-197_0_5_node_90 | 0.4 | n |  | TRUE
46 | bus_LV_261-197_0_5_node_88 | 0.4 | n |  | TRUE
47 | bus_LV_261-197_0_5_node_26 | 0.4 | n |  | TRUE
48 | bus_LV_261-197_0_5_node_79 | 0.4 | n |  | TRUE
49 | bus_LV_261-197_0_5_node_71 | 0.4 | n |  | TRUE
50 | bus_LV_261-197_0_5_node_85 | 0.4 | n |  | TRUE
51 | bus_LV_261-197_0_5_node_28 | 0.4 | n |  | TRUE
52 | bus_LV_261-197_0_5_node_136 | 0.4 | n |  | TRUE
53 | bus_LV_261-197_0_5_node_102 | 0.4 | n |  | TRUE
54 | bus_LV_261-197_0_5_node_30 | 0.4 | n |  | TRUE
55 | bus_LV_261-197_0_5_node_35 | 0.4 | n |  | TRUE
56 | bus_LV_261-197_0_5_node_91 | 0.4 | n |  | TRUE
57 | bus_LV_261-197_0_5_node_111 | 0.4 | n |  | TRUE
58 | bus_LV_261-197_0_5_node_40 | 0.4 | n |  | TRUE
59 | bus_LV_261-197_0_5_node_74 | 0.4 | n |  | TRUE
60 | bus_LV_261-197_0_5_node_36 | 0.4 | n |  | TRUE
61 | bus_LV_261-197_0_5_node_92 | 0.4 | n |  | TRUE
62 | bus_LV_261-197_0_5_node_145 | 0.4 | n |  | TRUE
63 | bus_LV_261-197_0_5_node_94 | 0.4 | n |  | TRUE
64 | bus_LV_261-197_0_5_node_105 | 0.4 | n |  | TRUE
65 | bus_LV_261-197_0_5_node_41 | 0.4 | n |  | TRUE
66 | bus_LV_261-197_0_5_node_135 | 0.4 | n |  | TRUE
67 | bus_LV_261-197_0_5_node_141 | 0.4 | n |  | TRUE
68 | bus_LV_261-197_0_5_node_58 | 0.4 | n |  | TRUE
69 | bus_LV_261-197_0_5_node_48 | 0.4 | n |  | TRUE
70 | bus_LV_261-197_0_5_node_53 | 0.4 | n |  | TRUE
71 | bus_LV_261-197_0_5_node_56 | 0.4 | n |  | TRUE
72 | bus_LV_261-197_0_5_node_54 | 0.4 | n |  | TRUE
73 | bus_LV_261-197_0_5_node_51 | 0.4 | n |  | TRUE
74 | bus_LV_261-197_0_5_node_55 | 0.4 | n |  | TRUE
75 | bus_LV_261-197_0_5_node_59 | 0.4 | n |  | TRUE
76 | bus_LV_261-197_0_5_node_142 | 0.4 | n |  | TRUE
77 | bus_LV_261-197_0_5_node_61 | 0.4 | n |  | TRUE
78 | bus_LV_261-197_0_5_node_68 | 0.4 | n |  | TRUE
79 | bus_LV_261-197_0_5_node_44 | 0.4 | n |  | TRUE
80 | bus_LV_261-197_0_5_node_93 | 0.4 | n |  | TRUE
81 | bus_LV_261-197_0_5_node_106 | 0.4 | n |  | TRUE
82 | bus_LV_261-197_0_5_node_104 | 0.4 | n |  | TRUE
83 | bus_LV_261-197_0_5_node_96 | 0.4 | n |  | TRUE
84 | bus_LV_261-197_0_5_node_97 | 0.4 | n |  | TRUE
85 | bus_LV_261-197_0_5_node_137 | 0.4 | n |  | TRUE
86 | bus_LV_261-197_0_5_node_120 | 0.4 | n |  | TRUE
87 | bus_LV_261-197_0_5_node_123 | 0.4 | n |  | TRUE
88 | bus_LV_261-197_0_5_node_130 | 0.4 | n |  | TRUE
89 | bus_LV_261-197_0_5_node_107 | 0.4 | n |  | TRUE
90 | bus_LV_261-197_0_5_node_122 | 0.4 | n |  | TRUE
91 | bus_LV_261-197_0_5_node_89 | 0.4 | n |  | TRUE
92 | bus_LV_261-197_0_5_node_78 | 0.4 | n |  | TRUE
93 | bus_LV_261-197_0_5_node_69 | 0.4 | n |  | TRUE
94 | bus_LV_261-197_0_5_node_86 | 0.4 | n |  | TRUE
95 | bus_LV_261-197_0_5_node_128 | 0.4 | n |  | TRUE
96 | bus_LV_261-197_0_5_node_127 | 0.4 | n |  | TRUE
97 | bus_LV_261-197_0_5_node_126 | 0.4 | n |  | TRUE
98 | bus_LV_261-197_0_5_node_101 | 0.4 | n |  | TRUE
99 | bus_LV_261-197_0_5_node_73 | 0.4 | n |  | TRUE
100 | bus_LV_261-197_0_5_node_144 | 0.4 | n |  | TRUE
101 | bus_LV_261-197_0_5_node_143 | 0.4 | n |  | TRUE
102 | bus_LV_261-197_0_5_node_75 | 0.4 | n |  | TRUE
103 | bus_LV_261-197_0_5_node_138 | 0.4 | n |  | TRUE
104 | bus_LV_261-197_0_5_node_139 | 0.4 | n |  | TRUE
105 | bus_LV_261-197_0_5_node_134 | 0.4 | n |  | TRUE
106 | bus_LV_261-197_0_5_node_140 | 0.4 | n |  | TRUE
107 | bus_LV_261-197_0_5_node_45 | 0.4 | n |  | TRUE
108 | bus_LV_261-197_0_5_node_46 | 0.4 | n |  | TRUE
109 | bus_LV_261-197_0_5_node_67 | 0.4 | n |  | TRUE
110 | bus_LV_261-197_0_5_node_64 | 0.4 | n |  | TRUE
111 | bus_LV_261-197_0_5_node_47 | 0.4 | n |  | TRUE
112 | bus_LV_261-197_0_5_node_72 | 0.4 | n |  | TRUE
113 | bus_LV_261-197_0_5_node_65 | 0.4 | n |  | TRUE
114 | bus_LV_261-197_0_5_node_50 | 0.4 | n |  | TRUE
115 | bus_LV_261-197_0_5_node_52 | 0.4 | n |  | TRUE
116 | bus_LV_261-197_0_5_node_62 | 0.4 | n |  | TRUE
117 | bus_LV_261-197_0_5_node_63 | 0.4 | n |  | TRUE
118 | bus_LV_261-197_0_5_node_82 | 0.4 | n |  | TRUE
119 | bus_LV_261-197_0_5_node_83 | 0.4 | n |  | TRUE
120 | bus_LV_261-197_0_5_node_66 | 0.4 | n |  | TRUE
121 | bus_LV_261-197_0_5_node_77 | 0.4 | n |  | TRUE
122 | bus_LV_261-197_0_5_node_76 | 0.4 | n |  | TRUE
123 | bus_LV_261-197_0_5_node_84 | 0.4 | n |  | TRUE
124 | bus_LV_261-197_0_5_node_87 | 0.4 | n |  | TRUE
125 | bus_LV_261-197_0_5_node_108 | 0.4 | n |  | TRUE
126 | bus_LV_261-197_0_5_node_110 | 0.4 | n |  | TRUE
127 | bus_LV_261-197_0_5_node_115 | 0.4 | n |  | TRUE
128 | bus_LV_261-197_0_5_node_116 | 0.4 | n |  | TRUE
129 | bus_LV_261-197_0_5_node_121 | 0.4 | n |  | TRUE
130 | bus_LV_261-197_0_5_node_131 | 0.4 | n |  | TRUE
131 | bus_LV_261-197_0_5_node_132 | 0.4 | n |  | TRUE
132 | bus_MV_530_0_node_16 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-197_0_5_load_0 | 0 | 0.00078648 | 0.00019711 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-197_0_5_load_1 | 1 | 0.0041044 | 0.0010287 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-197_0_5_load_2 | 2 | 0.00096172 | 0.00024103 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-197_0_5_load_146 | 6 | 0.010948 | 0.0027437 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-197_0_5_load_43 | 9 | 0.0029283 | 0.0007339 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-197_0_5_load_42 | 10 | 0.0021458 | 0.00053779 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-197_0_5_load_103 | 14 | 0.0063533 | 0.0015923 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-197_0_5_load_95 | 17 | 0.007536 | 0.0018887 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-197_0_5_load_117 | 19 | 0.016732 | 0.0041934 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-197_0_5_load_81 | 20 | 0.0097072 | 0.0024329 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-197_0_5_load_114 | 22 | 0.010752 | 0.0026948 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-197_0_5_load_112 | 23 | 0.0097117 | 0.002434 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-197_0_5_load_100 | 25 | 0.0094657 | 0.0023723 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-197_0_5_load_98 | 26 | 0.0051846 | 0.0012994 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-197_0_5_load_113 | 30 | 0.0058789 | 0.0014734 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-197_0_5_load_125 | 33 | 0.0074987 | 0.0018794 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-197_0_5_load_129 | 34 | 0.0050789 | 0.0012729 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-197_0_5_load_118 | 37 | 0.012809 | 0.0032103 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-197_0_5_load_80 | 39 | 0.0077157 | 0.0019337 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-197_0_5_load_124 | 42 | 0.010689 | 0.0026788 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-197_0_5_load_99 | 43 | 0.0051037 | 0.0012791 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-197_0_5_load_90 | 45 | 0.0039948 | 0.0010012 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-197_0_5_load_88 | 46 | 0.009393 | 0.0023541 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-197_0_5_load_85 | 50 | 0.0048238 | 0.001209 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-197_0_5_load_136 | 52 | 0.017626 | 0.0044176 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-197_0_5_load_102 | 53 | 0.0028163 | 0.00070584 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-197_0_5_load_91 | 56 | 0.0074238 | 0.0018606 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-197_0_5_load_111 | 57 | 0.0061382 | 0.0015384 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-197_0_5_load_74 | 59 | 0.019309 | 0.0048393 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-197_0_5_load_92 | 61 | 0.0077344 | 0.0019384 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-197_0_5_load_145 | 62 | 0.0047654 | 0.0011943 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-197_0_5_load_94 | 63 | 0.0053004 | 0.0013284 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-197_0_5_load_105 | 64 | 0.0054547 | 0.0013671 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-197_0_5_load_135 | 66 | 0.0080644 | 0.0020211 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-197_0_5_load_141 | 67 | 0.0067154 | 0.001683 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-197_0_5_load_48 | 69 | 0.0051787 | 0.0012979 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-197_0_5_load_56 | 71 | 0.0059848 | 0.0014999 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-197_0_5_load_54 | 72 | 0.0077703 | 0.0019474 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-197_0_5_load_142 | 76 | 0.0050928 | 0.0012764 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-197_0_5_load_61 | 77 | 0.0028696 | 0.00071918 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-197_0_5_load_68 | 78 | 0.0077036 | 0.0019307 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-197_0_5_load_93 | 80 | 0.0058627 | 0.0014693 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-197_0_5_load_106 | 81 | 0.0077898 | 0.0019523 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-197_0_5_load_104 | 82 | 0.005432 | 0.0013614 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-197_0_5_load_96 | 83 | 0.0066079 | 0.0016561 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-197_0_5_load_97 | 84 | 0.0042119 | 0.0010556 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-197_0_5_load_137 | 85 | 0.018032 | 0.0045192 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-197_0_5_load_123 | 87 | 0.0078013 | 0.0019552 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-197_0_5_load_130 | 88 | 0.0041644 | 0.0010437 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-197_0_5_load_107 | 89 | 0.0036311 | 0.00091005 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-197_0_5_load_122 | 90 | 0.0072771 | 0.0018238 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-197_0_5_load_78 | 92 | 0.008461 | 0.0021205 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-197_0_5_load_69 | 93 | 0.0080403 | 0.0020151 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-197_0_5_load_86 | 94 | 0.0045525 | 0.001141 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-197_0_5_load_127 | 96 | 0.01217 | 0.00305 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-197_0_5_load_126 | 97 | 0.01104 | 0.002767 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-197_0_5_load_101 | 98 | 0.0063274 | 0.0015858 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-197_0_5_load_73 | 99 | 0.0025168 | 0.00063077 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-197_0_5_load_144 | 100 | 0.0061578 | 0.0015433 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-197_0_5_load_143 | 101 | 0.0062003 | 0.0015539 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-197_0_5_load_75 | 102 | 0.0094511 | 0.0023687 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-197_0_5_load_138 | 103 | 0.010999 | 0.0027565 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-197_0_5_load_139 | 104 | 0.0063715 | 0.0015968 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-197_0_5_load_134 | 105 | 0.0056236 | 0.0014094 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-197_0_5_load_140 | 106 | 0.0053243 | 0.0013344 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-197_0_5_load_46 | 108 | 0.002467 | 0.0006183 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-197_0_5_load_67 | 109 | 0.0082129 | 0.0020584 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-197_0_5_load_64 | 110 | 0.0040896 | 0.0010249 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-197_0_5_load_47 | 111 | 0.0032579 | 0.0008165 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-197_0_5_load_72 | 112 | 0.0057388 | 0.0014383 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-197_0_5_load_65 | 113 | 0.0034157 | 0.00085606 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-197_0_5_load_50 | 114 | 0.0061902 | 0.0015514 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-197_0_5_load_52 | 115 | 0.0028854 | 0.00072314 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-197_0_5_load_62 | 116 | 0.0034839 | 0.00087314 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-197_0_5_load_63 | 117 | 0.003623 | 0.000908 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-197_0_5_load_82 | 118 | 0.0045571 | 0.0011421 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-197_0_5_load_83 | 119 | 0.0026539 | 0.00066512 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-197_0_5_load_66 | 120 | 0.0034136 | 0.00085553 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-197_0_5_load_77 | 121 | 0.0092197 | 0.0023107 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-197_0_5_load_76 | 122 | 0.0072833 | 0.0018254 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-197_0_5_load_84 | 123 | 0.0026539 | 0.00066512 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-197_0_5_load_108 | 125 | 0.0036599 | 0.00091726 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_261-197_0_5_load_110 | 126 | 0.0036309 | 0.00090999 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_261-197_0_5_load_115 | 127 | 0.0036599 | 0.00091726 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_261-197_0_5_load_116 | 128 | 0.0083327 | 0.0020884 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_261-197_0_5_load_121 | 129 | 0.019869 | 0.0049795 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_261-197_0_5_load_131 | 130 | 0.0035323 | 0.00088528 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_261-197_0_5_load_132 | 131 | 0.0055062 | 0.00138 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-197_0_5_line_0 |  | 0 | 1 | 0.012607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-197_0_5_line_1 |  | 0 | 2 | 0.00056834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-197_0_5_line_2 |  | 2 | 3 | 0.015997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-197_0_5_line_3 |  | 3 | 4 | 0.024897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-197_0_5_line_4 |  | 4 | 68 | 0.021832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_261-197_0_5_line_5 |  | 4 | 69 | 0.017288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_261-197_0_5_line_6 |  | 5 | 6 | 0.002933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-197_0_5_line_7 |  | 5 | 7 | 0.021204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-197_0_5_line_8 |  | 7 | 78 | 0.019959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-197_0_5_line_9 |  | 8 | 9 | 0.015708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-197_0_5_line_10 |  | 8 | 10 | 0.022351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-197_0_5_line_11 |  | 9 | 79 | 0.0070397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-197_0_5_line_12 |  | 11 | 12 | 0.007765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-197_0_5_line_13 |  | 11 | 13 | 0.0086033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-197_0_5_line_14 |  | 11 | 14 | 0.024273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-197_0_5_line_15 |  | 12 | 34 | 0.0025984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-197_0_5_line_16 |  | 13 | 15 | 0.013276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-197_0_5_line_17 |  | 13 | 16 | 0.039291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-197_0_5_line_18 |  | 13 | 17 | 0.016374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-197_0_5_line_19 |  | 14 | 82 | 0.015247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-197_0_5_line_20 |  | 15 | 57 | 0.029111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-197_0_5_line_21 |  | 15 | 51 | 0.01022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-197_0_5_line_22 |  | 16 | 63 | 0.023562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-197_0_5_line_23 |  | 16 | 64 | 0.01191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-197_0_5_line_24 |  | 17 | 83 | 0.018337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-197_0_5_line_25 |  | 18 | 19 | 0.018598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_261-197_0_5_line_26 |  | 18 | 20 | 0.014843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_261-197_0_5_line_27 |  | 19 | 85 | 0.020818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_261-197_0_5_line_28 |  | 20 | 29 | 0.010175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_261-197_0_5_line_29 |  | 21 | 22 | 0.018706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-197_0_5_line_30 |  | 21 | 23 | 0.013818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-197_0_5_line_31 |  | 22 | 86 | 0.017043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-197_0_5_line_32 |  | 23 | 30 | 0.018077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-197_0_5_line_33 |  | 24 | 25 | 0.0082506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-197_0_5_line_34 |  | 24 | 26 | 0.039115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-197_0_5_line_35 |  | 26 | 43 | 0.016099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-197_0_5_line_36 |  | 27 | 28 | 0.022011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-197_0_5_line_37 |  | 27 | 29 | 0.013436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_261-197_0_5_line_38 |  | 27 | 30 | 0.026881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_261-197_0_5_line_39 |  | 28 | 43 | 0.0095809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-197_0_5_line_40 |  | 29 | 38 | 0.0074704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-197_0_5_line_41 |  | 29 | 39 | 0.041497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_261-197_0_5_line_42 |  | 31 | 32 | 0.048178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-197_0_5_line_43 |  | 31 | 33 | 0.023944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-197_0_5_line_44 |  | 32 | 62 | 0.0114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-197_0_5_line_45 |  | 33 | 87 | 0.035908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-197_0_5_line_46 |  | 34 | 88 | 0.013491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-197_0_5_line_47 |  | 35 | 36 | 0.004272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-197_0_5_line_48 |  | 35 | 37 | 0.016956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-197_0_5_line_49 |  | 36 | 57 | 0.010866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-197_0_5_line_50 |  | 36 | 89 | 0.029677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-197_0_5_line_51 |  | 38 | 58 | 0.015634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-197_0_5_line_52 |  | 39 | 49 | 0.013083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_261-197_0_5_line_53 |  | 40 | 41 | 0.001861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-197_0_5_line_54 |  | 40 | 42 | 0.014173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-197_0_5_line_55 |  | 41 | 53 | 0.029898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-197_0_5_line_56 |  | 41 | 51 | 0.0095519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-197_0_5_line_57 |  | 42 | 90 | 0.035244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-197_0_5_line_58 |  | 44 | 45 | 0.018742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-197_0_5_line_59 |  | 44 | 46 | 0.012653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-197_0_5_line_60 |  | 46 | 91 | 0.032865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-197_0_5_line_61 |  | 47 | 48 | 0.031909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_261-197_0_5_line_62 |  | 47 | 49 | 0.009429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_261-197_0_5_line_63 |  | 47 | 50 | 0.010356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-197_0_5_line_64 |  | 48 | 92 | 0.008718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_261-197_0_5_line_65 |  | 49 | 93 | 0.041692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-197_0_5_line_66 |  | 50 | 94 | 0.013754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-197_0_5_line_67 |  | 51 | 52 | 0.0073438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
68 | LV_261-197_0_5_line_68 |  | 52 | 85 | 0.024236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_261-197_0_5_line_69 |  | 53 | 98 | 0.021196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-197_0_5_line_70 |  | 54 | 55 | 0.11394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-197_0_5_line_71 |  | 54 | 56 | 0.013689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-197_0_5_line_72 |  | 55 | 59 | 0.0768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-197_0_5_line_73 |  | 56 | 60 | 0.014741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-197_0_5_line_74 |  | 58 | 65 | 0.0093769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-197_0_5_line_75 |  | 58 | 66 | 0.0065705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-197_0_5_line_76 |  | 59 | 102 | 0.03506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-197_0_5_line_77 |  | 60 | 61 | 0.011137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-197_0_5_line_78 |  | 63 | 80 | 0.02675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-197_0_5_line_79 |  | 64 | 81 | 0.039435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-197_0_5_line_80 |  | 65 | 67 | 0.039544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_261-197_0_5_line_81 |  | 66 | 105 | 0.013556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-197_0_5_line_82 |  | 67 | 106 | 0.014276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_261-197_0_5_line_83 |  | 68 | 75 | 0.026304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_261-197_0_5_line_84 |  | 68 | 76 | 0.031018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_261-197_0_5_line_85 |  | 69 | 111 | 0.02481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_261-197_0_5_line_86 |  | 70 | 71 | 0.034982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_261-197_0_5_line_87 |  | 70 | 72 | 0.076564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_261-197_0_5_line_88 |  | 70 | 73 | 0.087538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_261-197_0_5_line_89 |  | 71 | 99 | 0.02371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_261-197_0_5_line_90 |  | 72 | 74 | 0.060632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_261-197_0_5_line_91 |  | 73 | 115 | 0.0043294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_261-197_0_5_line_92 |  | 73 | 114 | 0.014796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_261-197_0_5_line_93 |  | 74 | 75 | 0.014598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_261-197_0_5_line_94 |  | 75 | 77 | 0.023415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
95 | LV_261-197_0_5_line_95 |  | 77 | 116 | 0.023615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_261-197_0_5_line_96 |  | 78 | 93 | 0.031614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_261-197_0_5_line_97 |  | 79 | 107 | 0.028289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_261-197_0_5_line_98 |  | 79 | 108 | 0.024219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_261-197_0_5_line_99 |  | 83 | 84 | 0.014047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_261-197_0_5_line_100 |  | 86 | 129 | 0.015516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_261-197_0_5_line_101 |  | 87 | 90 | 0.015512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_261-197_0_5_line_102 |  | 88 | 95 | 0.01512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_261-197_0_5_line_103 |  | 89 | 125 | 0.0014517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_261-197_0_5_line_104 |  | 91 | 124 | 0.012307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_261-197_0_5_line_105 |  | 92 | 121 | 0.033937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
106 | LV_261-197_0_5_line_106 |  | 94 | 124 | 0.014392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_261-197_0_5_line_107 |  | 95 | 96 | 0.021091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_261-197_0_5_line_108 |  | 96 | 97 | 0.031347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_261-197_0_5_line_109 |  | 100 | 101 | 0.023404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-197_0_5_line_110 |  | 101 | 129 | 0.024316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_261-197_0_5_line_111 |  | 102 | 122 | 0.02424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_261-197_0_5_line_112 |  | 103 | 104 | 0.032506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_261-197_0_5_line_113 |  | 104 | 106 | 0.017666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_261-197_0_5_line_114 |  | 105 | 131 | 0.014045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_261-197_0_5_line_115 |  | 107 | 109 | 0.019575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_261-197_0_5_line_116 |  | 107 | 110 | 0.0047644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
117 | LV_261-197_0_5_line_117 |  | 108 | 111 | 0.0065567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
118 | LV_261-197_0_5_line_118 |  | 109 | 112 | 0.022654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_261-197_0_5_line_119 |  | 110 | 113 | 0.018541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_261-197_0_5_line_120 |  | 113 | 120 | 0.0074945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
121 | LV_261-197_0_5_line_121 |  | 116 | 117 | 0.0084206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_261-197_0_5_line_122 |  | 117 | 118 | 0.023392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_261-197_0_5_line_123 |  | 118 | 119 | 0.027362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_261-197_0_5_line_124 |  | 119 | 123 | 0.007497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_261-197_0_5_line_125 |  | 120 | 121 | 0.014798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
126 | LV_261-197_0_5_line_126 |  | 122 | 123 | 0.019172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_261-197_0_5_line_127 |  | 125 | 126 | 0.0048053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_261-197_0_5_line_128 |  | 126 | 127 | 0.0013169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_261-197_0_5_line_129 |  | 127 | 128 | 0.011342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_261-197_0_5_line_130 |  | 130 | 131 | 0.011019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-197_0_5_trafo_113 | 0.63 MVA 20/0.4 kV | 132 | 30 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2682208.5385 | 1250204.5962 | 2682203.6309 | 1250199.1749 | 2682200.7044 | 1250194.7632
1 | 2682208.5385 | 1250204.5962 | 2682208.9199 | 1250205.0175
2 | 2682219.6556 | 1250216.877 | 2682208.9199 | 1250205.0175
3 | 2682239.1692 | 1250232.3258 | 2682221.9161 | 1250219.3769 | 2682219.6556 | 1250216.877
4 | 2682251.9089 | 1250247.8919 | 2682248.4207 | 1250247.899 | 2682245.815 | 1250245.7946 | 2682239.1692 | 1250232.3258
5 | 2682239.1692 | 1250232.3258 | 2682248.8405 | 1250217.9957
6 | 2682297.2742 | 1250107.3172 | 2682298.4291 | 1250104.6202
7 | 2682317.9033 | 1250113.1413 | 2682299.3374 | 1250104.9997 | 2682298.4291 | 1250104.6202
8 | 2682317.9033 | 1250113.1413 | 2682336.1791 | 1250121.1628
9 | 2682251.7647 | 1250164.2056 | 2682267.1699 | 1250167.2758
10 | 2682251.7647 | 1250164.2056 | 2682251.5259 | 1250156.3965 | 2682237.7267 | 1250151.8217
11 | 2682274.0739 | 1250168.6518 | 2682267.1699 | 1250167.2758
12 | 2682393.4868 | 1250003.5657 | 2682394.0964 | 1250005.331 | 2682395.5637 | 1250007.3195 | 2682397.8251 | 1250008.6742 | 2682398.592 | 1250008.9072
13 | 2682384.9547 | 1250004.6701 | 2682389.3038 | 1250004.119 | 2682393.4868 | 1250003.5657
14 | 2682393.4868 | 1250003.5657 | 2682393.1311 | 1250002.5377 | 2682389.1404 | 1249979.6982
15 | 2682398.592 | 1250008.9072 | 2682401.0799 | 1250009.6567
16 | 2682384.9547 | 1250004.6701 | 2682384.6269 | 1250006.5225 | 2682383.4938 | 1250007.652 | 2682383.4388 | 1250013.2332 | 2682383.4028 | 1250017.4469
17 | 2682384.9547 | 1250004.6701 | 2682384.6269 | 1250006.5225 | 2682383.4938 | 1250007.652 | 2682378.4127 | 1250007.0921 | 2682359.2477 | 1250004.5462 | 2682347.8898 | 1250004.1659
18 | 2682384.9547 | 1250004.6701 | 2682383.663 | 1249997.1132 | 2682382.2436 | 1249988.5222
19 | 2682389.1404 | 1249979.6982 | 2682386.5162 | 1249964.6791
20 | 2682383.4028 | 1250017.4469 | 2682366.6051 | 1250015.1562 | 2682354.5099 | 1250013.9225
21 | 2682383.4028 | 1250017.4469 | 2682385.7659 | 1250018.5472 | 2682387.7178 | 1250020.9762 | 2682389.0396 | 1250025.2866
22 | 2682347.8898 | 1250004.1659 | 2682335.7074 | 1250004.4413 | 2682324.365 | 1250005.3277
23 | 2682347.8898 | 1250004.1659 | 2682347.4751 | 1249992.2631
24 | 2682382.2436 | 1249988.5222 | 2682379.2545 | 1249970.431
25 | 2682401.6279 | 1250095.1579 | 2682398.2595 | 1250076.8672
26 | 2682401.6279 | 1250095.1579 | 2682404.4212 | 1250109.7358
27 | 2682394.5336 | 1250056.3852 | 2682395.6188 | 1250062.5279 | 2682398.2595 | 1250076.8672
28 | 2682407.004 | 1250119.5507 | 2682405.4219 | 1250114.9586 | 2682404.4212 | 1250109.7358
29 | 2682350.2617 | 1250108.365 | 2682333.1865 | 1250100.7268
30 | 2682350.2617 | 1250108.365 | 2682362.8754 | 1250114.0066
31 | 2682317.6289 | 1250093.7676 | 2682333.1865 | 1250100.7268
32 | 2682362.8754 | 1250114.0066 | 2682379.3774 | 1250121.3873
33 | 2682485.172 | 1250162.8255 | 2682487.8913 | 1250162.7299 | 2682493.2468 | 1250161.3534
34 | 2682485.172 | 1250162.8255 | 2682462.0074 | 1250153.6742 | 2682448.7481 | 1250148.5697
35 | 2682448.7481 | 1250148.5697 | 2682433.724 | 1250142.7857
36 | 2682404.1384 | 1250131.7866 | 2682414.252 | 1250135.2965 | 2682424.929 | 1250139.0143
37 | 2682404.1384 | 1250131.7866 | 2682408.3527 | 1250122.4605 | 2682407.004 | 1250119.5507
38 | 2682404.1384 | 1250131.7866 | 2682398.4489 | 1250129.9172 | 2682379.3774 | 1250121.3873
39 | 2682424.929 | 1250139.0143 | 2682428.1154 | 1250140.6265 | 2682433.724 | 1250142.7857
40 | 2682407.004 | 1250119.5507 | 2682410.0375 | 1250118.581 | 2682414.1177 | 1250117.2701
41 | 2682407.004 | 1250119.5507 | 2682404.925 | 1250120.289 | 2682401.9709 | 1250127.4866 | 2682398.1838 | 1250153.3198 | 2682396.0536 | 1250158.2828
42 | 2682509.0131 | 1250051.8527 | 2682510.6339 | 1250049.3178 | 2682512.2567 | 1250046.6496 | 2682515.5386 | 1250039.779 | 2682517.9293 | 1250031.8398 | 2682519.7045 | 1250024.1921 | 2682521.7799 | 1250013.413 | 2682522.131 | 1250006.1014
43 | 2682522.131 | 1250006.1014 | 2682518.9209 | 1250006.1901 | 2682511.2432 | 1250007.2062 | 2682501.4425 | 1250009.4048 | 2682498.5989 | 1250010.1678
44 | 2682503.322 | 1250041.9662 | 2682509.0131 | 1250051.8527
45 | 2682464.0023 | 1250019.7279 | 2682467.112 | 1250019.1232 | 2682471.5991 | 1250017.8736 | 2682483.5191 | 1250014.2145 | 2682498.5989 | 1250010.1678
46 | 2682401.0799 | 1250009.6567 | 2682403.8551 | 1250010.4927 | 2682414.4361 | 1250010.9926
47 | 2682343.6588 | 1250013.603 | 2682343.5747 | 1250009.332
48 | 2682343.5747 | 1250009.332 | 2682333.4171 | 1250009.5133 | 2682326.6386 | 1250010.0085
49 | 2682343.6588 | 1250013.603 | 2682351.5863 | 1250013.6242 | 2682354.5099 | 1250013.9225
50 | 2682343.6588 | 1250013.603 | 2682344.2562 | 1250043.2737
51 | 2682426.6059 | 1250112.3734 | 2682425.8163 | 1250113.2298 | 2682422.0258 | 1250117.5914 | 2682420.1971 | 1250118.7891 | 2682418.14 | 1250119.0384 | 2682415.973 | 1250118.5079 | 2682414.1177 | 1250117.2701
52 | 2682403.0844 | 1250151.1085 | 2682401.5592 | 1250154.9123 | 2682399.4837 | 1250159.7426 | 2682396.0536 | 1250158.2828
53 | 2682398.4615 | 1250023.7164 | 2682399.6965 | 1250022.3214
54 | 2682399.6965 | 1250022.3214 | 2682401.2842 | 1250021.0759 | 2682403.6541 | 1250020.5974 | 2682413.388 | 1250020.8407
55 | 2682398.4615 | 1250023.7164 | 2682397.6667 | 1250026.0293 | 2682397.5301 | 1250028.7961 | 2682401.8423 | 1250053.0987
56 | 2682398.4615 | 1250023.7164 | 2682392.7023 | 1250024.6815 | 2682389.0396 | 1250025.2866
57 | 2682448.5991 | 1250021.3192 | 2682441.2907 | 1250021.7882 | 2682429.7312 | 1250021.2493 | 2682413.388 | 1250020.8407
58 | 2682496.2138 | 1250200.5182 | 2682491.5586 | 1250207.3363 | 2682485.8189 | 1250216.1296
59 | 2682496.2138 | 1250200.5182 | 2682492.3883 | 1250198.7192 | 2682484.8106 | 1250195.0358
60 | 2682456.6366 | 1250178.2733 | 2682462.5723 | 1250182.5146 | 2682473.0776 | 1250189.3325 | 2682484.8106 | 1250195.0358
61 | 2682388.0024 | 1250174.772 | 2682397.4549 | 1250169.8997 | 2682402.1447 | 1250167.0962 | 2682404.6876 | 1250165.5748 | 2682408.8468 | 1250160.7513 | 2682411.7445 | 1250154.8984
62 | 2682403.0844 | 1250151.1085 | 2682411.7445 | 1250154.8984
63 | 2682411.7445 | 1250154.8984 | 2682420.0967 | 1250158.5616 | 2682421.2323 | 1250159.0494
64 | 2682388.0024 | 1250174.772 | 2682380.0252 | 1250178.3415
65 | 2682403.0844 | 1250151.1085 | 2682396.2526 | 1250147.7777 | 2682365.0928 | 1250133.9463
66 | 2682421.2323 | 1250159.0494 | 2682433.8701 | 1250164.4777
67 | 2682389.0396 | 1250025.2866 | 2682390.3172 | 1250032.5184
68 | 2682390.3172 | 1250032.5184 | 2682394.5336 | 1250056.3852
69 | 2682405.5419 | 1250073.9695 | 2682404.055 | 1250065.5919 | 2682403.0682 | 1250060.0074 | 2682401.8423 | 1250053.0987
70 | 2682491.7348 | 1250259.7443 | 2682547.2338 | 1250271.7147 | 2682548.3468 | 1250268.2387 | 2682544.289 | 1250266.859 | 2682557.4148 | 1250266.5749 | 2682565.5797 | 1250266.3328 | 2682563.1005 | 1250261.1167 | 2682560.8852 | 1250261.8864 | 2682558.7745 | 1250262.1905 | 2682554.2771 | 1250261.4829 | 2682543.0643 | 1250259.3919 | 2682541.3938 | 1250258.9906
71 | 2682491.7348 | 1250259.7443 | 2682478.3543 | 1250256.8558
72 | 2682541.3938 | 1250258.9906 | 2682531.9576 | 1250256.7353 | 2682517.6375 | 1250253.3223 | 2682514.4244 | 1250252.5548 | 2682512.2497 | 1250252.0352 | 2682502.7285 | 1250249.9122 | 2682498.6792 | 1250249.0108 | 2682477.1532 | 1250244.2077 | 2682466.5347 | 1250241.8414
73 | 2682463.9437 | 1250253.7532 | 2682472.1336 | 1250255.5129 | 2682478.3543 | 1250256.8558
74 | 2682426.6059 | 1250112.3734 | 2682430.3174 | 1250114.7713 | 2682434.5086 | 1250117.4204
75 | 2682426.6059 | 1250112.3734 | 2682431.0597 | 1250107.5429
76 | 2682466.5347 | 1250241.8414 | 2682456.9818 | 1250239.7126 | 2682452.5937 | 1250238.7397 | 2682432.2785 | 1250234.3786
77 | 2682453.837 | 1250254.1018 | 2682455.8894 | 1250252.0176 | 2682463.9437 | 1250253.7532
78 | 2682298.038 | 1250009.9764 | 2682308.3887 | 1250007.8311 | 2682322.0567 | 1250005.5081 | 2682324.365 | 1250005.3277
79 | 2682347.4751 | 1249992.2631 | 2682347.2583 | 1249986.0437 | 2682345.5059 | 1249980.6709 | 2682330.8226 | 1249978.8879 | 2682325.4143 | 1249967.3201
80 | 2682434.5086 | 1250117.4204 | 2682461.2659 | 1250128.8343 | 2682465.3111 | 1250119.1946
81 | 2682441.9962 | 1250099.554 | 2682437.1516 | 1250102.7352 | 2682431.0597 | 1250107.5429 | 2682431.0597 | 1250107.5429
82 | 2682479.3412 | 1250116.5554 | 2682465.3111 | 1250119.1946
83 | 2682277.4492 | 1250244.1769 | 2682261.0213 | 1250249.008 | 2682251.9089 | 1250247.8919
84 | 2682251.9089 | 1250247.8919 | 2682243.7438 | 1250254.6725 | 2682225.0564 | 1250262.8667
85 | 2682261.0951 | 1250196.5425 | 2682257.1611 | 1250205.6668 | 2682248.8405 | 1250217.9957
86 | 2682407.5012 | 1250306.8633 | 2682412.5487 | 1250308.19 | 2682439.9218 | 1250315.9875 | 2682441.1885 | 1250316.2855
87 | 2682407.5012 | 1250306.8633 | 2682405.0775 | 1250300.9029 | 2682372.9934 | 1250287.1134 | 2682366.1263 | 1250284.1603 | 2682353.5366 | 1250280.1045 | 2682339.7322 | 1250275.649
88 | 2682407.5012 | 1250306.8633 | 2682376.6018 | 1250303.9761 | 2682350.0684 | 1250304.1965 | 2682327.1658 | 1250307.7254 | 2682320.4962 | 1250309.0338
89 | 2682441.1885 | 1250316.2855 | 2682460.6162 | 1250320.8567 | 2682464.3023 | 1250321.5548
90 | 2682281.6869 | 1250258.1461 | 2682299.3436 | 1250263.2283 | 2682320.4652 | 1250269.4373 | 2682335.8961 | 1250274.4108 | 2682339.7322 | 1250275.649
91 | 2682320.4962 | 1250309.0338 | 2682316.2466 | 1250309.8613
92 | 2682320.4962 | 1250309.0338 | 2682318.6253 | 1250294.3566
93 | 2682277.4492 | 1250244.1769 | 2682279.6006 | 1250251.2676 | 2682281.6869 | 1250258.1461
94 | 2682277.4492 | 1250244.1769 | 2682292.3717 | 1250239.5584 | 2682299.8981 | 1250237.5322
95 | 2682322.8356 | 1250232.1519 | 2682314.2847 | 1250233.3691 | 2682303.3299 | 1250236.6083 | 2682299.8981 | 1250237.5322
96 | 2682336.1791 | 1250121.1628 | 2682347.4405 | 1250126.1056 | 2682354.1263 | 1250129.0785 | 2682365.0928 | 1250133.9463
97 | 2682301.9185 | 1250174.0868 | 2682274.0739 | 1250168.6518
98 | 2682274.0739 | 1250168.6518 | 2682267.412 | 1250181.8914 | 2682263.691 | 1250190.5216
99 | 2682376.9647 | 1249956.5715 | 2682379.2545 | 1249970.431
100 | 2682317.6289 | 1250093.7676 | 2682304.6102 | 1250087.9492 | 2682303.4471 | 1250087.4755
101 | 2682448.5991 | 1250021.3192 | 2682459.3746 | 1250020.6278 | 2682464.0023 | 1250019.7279
102 | 2682429.5393 | 1250011.7062 | 2682414.4361 | 1250010.9926
103 | 2682344.2562 | 1250043.2737 | 2682344.2854 | 1250044.7251
104 | 2682446.6504 | 1250171.0402 | 2682453.6244 | 1250176.0853 | 2682456.6366 | 1250178.2733
105 | 2682380.0252 | 1250178.3415 | 2682376.8724 | 1250179.7432 | 2682373.6905 | 1250180.5218 | 2682365.4933 | 1250182.5427 | 2682355.5607 | 1250182.8494 | 2682346.7566 | 1250182.1663
106 | 2682446.6504 | 1250171.0402 | 2682440.6736 | 1250167.5767 | 2682439.5203 | 1250166.9046 | 2682433.8701 | 1250164.4777
107 | 2682429.5393 | 1250011.7062 | 2682446.1107 | 1250011.2697 | 2682450.5908 | 1250010.7157
108 | 2682481.2594 | 1250004.5269 | 2682475.101 | 1250005.502 | 2682465.5417 | 1250008.2599 | 2682457.9927 | 1250009.8005 | 2682450.5908 | 1250010.7157
109 | 2682280.9271 | 1250078.3049 | 2682264.7218 | 1250071.7057 | 2682259.1999 | 1250069.6082
110 | 2682303.4471 | 1250087.4755 | 2682280.9271 | 1250078.3049
111 | 2682408.3797 | 1250230.3857 | 2682417.7579 | 1250231.6945 | 2682424.9743 | 1250232.8846 | 2682426.4507 | 1250233.1275 | 2682432.2785 | 1250234.3786
112 | 2682519.5182 | 1250095.8687 | 2682513.3577 | 1250110.1565 | 2682496.7031 | 1250113.2894
113 | 2682496.7031 | 1250113.2894 | 2682479.3412 | 1250116.5554
114 | 2682453.7365 | 1250091.8448 | 2682441.9962 | 1250099.554
115 | 2682301.9185 | 1250174.0868 | 2682305.7041 | 1250154.8815
116 | 2682301.9185 | 1250174.0868 | 2682306.593 | 1250175.0081
117 | 2682261.0951 | 1250196.5425 | 2682263.691 | 1250190.5216
118 | 2682294.2485 | 1250144.6807 | 2682295.2865 | 1250142.7826 | 2682297.6214 | 1250142.1034 | 2682300.7561 | 1250142.5473 | 2682303.5789 | 1250143.6984 | 2682305.3631 | 1250146.2473 | 2682306.1217 | 1250149.7938 | 2682305.7524 | 1250154.6367 | 2682305.7041 | 1250154.8815
119 | 2682306.593 | 1250175.0081 | 2682324.7838 | 1250178.5935
120 | 2682332.1366 | 1250180.0445 | 2682327.8348 | 1250179.1949 | 2682324.7838 | 1250178.5935
121 | 2682331.1877 | 1250231.0815 | 2682328.1049 | 1250231.4708 | 2682324.2477 | 1250231.9509 | 2682322.8356 | 1250232.1519
122 | 2682354.4629 | 1250228.7983 | 2682353.6077 | 1250228.8342 | 2682338.6556 | 1250230.1385 | 2682331.1877 | 1250231.0815
123 | 2682354.4629 | 1250228.7983 | 2682363.3755 | 1250228.4251 | 2682370.8771 | 1250228.1069 | 2682381.8075 | 1250228.3739
124 | 2682381.8075 | 1250228.3739 | 2682388.8475 | 1250228.5458 | 2682389.3022 | 1250228.5567
125 | 2682346.7566 | 1250182.1663 | 2682340.3713 | 1250181.6708 | 2682332.1366 | 1250180.0445
126 | 2682408.3797 | 1250230.3857 | 2682405.6335 | 1250230.0025 | 2682391.074 | 1250228.599 | 2682389.3022 | 1250228.5567
127 | 2682344.2854 | 1250044.7251 | 2682344.3822 | 1250049.5295
128 | 2682344.4087 | 1250050.8461 | 2682344.3822 | 1250049.5295
129 | 2682344.637 | 1250062.1859 | 2682344.4087 | 1250050.8461
130 | 2682462.9475 | 1250085.7964 | 2682453.7365 | 1250091.8448

## bus_geodata
| x | y | coords
0 | 2682208.5385 | 1250204.5962
1 | 2682200.7044 | 1250194.7632
2 | 2682208.9199 | 1250205.0175
3 | 2682219.6556 | 1250216.877
4 | 2682239.1692 | 1250232.3258
5 | 2682298.4291 | 1250104.6202
6 | 2682297.2742 | 1250107.3172
7 | 2682317.9033 | 1250113.1413
8 | 2682251.7647 | 1250164.2056
9 | 2682267.1699 | 1250167.2758
10 | 2682237.7267 | 1250151.8217
11 | 2682393.4868 | 1250003.5657
12 | 2682398.592 | 1250008.9072
13 | 2682384.9547 | 1250004.6701
14 | 2682389.1404 | 1249979.6982
15 | 2682383.4028 | 1250017.4469
16 | 2682347.8898 | 1250004.1659
17 | 2682382.2436 | 1249988.5222
18 | 2682401.6279 | 1250095.1579
19 | 2682398.2595 | 1250076.8672
20 | 2682404.4212 | 1250109.7358
21 | 2682350.2617 | 1250108.365
22 | 2682333.1865 | 1250100.7268
23 | 2682362.8754 | 1250114.0066
24 | 2682485.172 | 1250162.8255
25 | 2682493.2468 | 1250161.3534
26 | 2682448.7481 | 1250148.5697
27 | 2682404.1384 | 1250131.7866
28 | 2682424.929 | 1250139.0143
29 | 2682407.004 | 1250119.5507
30 | 2682379.3774 | 1250121.3873
31 | 2682522.131 | 1250006.1014
32 | 2682509.0131 | 1250051.8527
33 | 2682498.5989 | 1250010.1678
34 | 2682401.0799 | 1250009.6567
35 | 2682343.5747 | 1250009.332
36 | 2682343.6588 | 1250013.603
37 | 2682326.6386 | 1250010.0085
38 | 2682414.1177 | 1250117.2701
39 | 2682396.0536 | 1250158.2828
40 | 2682399.6965 | 1250022.3214
41 | 2682398.4615 | 1250023.7164
42 | 2682413.388 | 1250020.8407
43 | 2682433.724 | 1250142.7857
44 | 2682496.2138 | 1250200.5182
45 | 2682485.8189 | 1250216.1296
46 | 2682484.8106 | 1250195.0358
47 | 2682411.7445 | 1250154.8984
48 | 2682388.0024 | 1250174.772
49 | 2682403.0844 | 1250151.1085
50 | 2682421.2323 | 1250159.0494
51 | 2682389.0396 | 1250025.2866
52 | 2682390.3172 | 1250032.5184
53 | 2682401.8423 | 1250053.0987
54 | 2682491.7348 | 1250259.7443
55 | 2682541.3938 | 1250258.9906
56 | 2682478.3543 | 1250256.8558
57 | 2682354.5099 | 1250013.9225
58 | 2682426.6059 | 1250112.3734
59 | 2682466.5347 | 1250241.8414
60 | 2682463.9437 | 1250253.7532
61 | 2682453.837 | 1250254.1018
62 | 2682503.322 | 1250041.9662
63 | 2682324.365 | 1250005.3277
64 | 2682347.4751 | 1249992.2631
65 | 2682434.5086 | 1250117.4204
66 | 2682431.0597 | 1250107.5429
67 | 2682465.3111 | 1250119.1946
68 | 2682251.9089 | 1250247.8919
69 | 2682248.8405 | 1250217.9957
70 | 2682407.5012 | 1250306.8633
71 | 2682441.1885 | 1250316.2855
72 | 2682339.7322 | 1250275.649
73 | 2682320.4962 | 1250309.0338
74 | 2682281.6869 | 1250258.1461
75 | 2682277.4492 | 1250244.1769
76 | 2682225.0564 | 1250262.8667
77 | 2682299.8981 | 1250237.5322
78 | 2682336.1791 | 1250121.1628
79 | 2682274.0739 | 1250168.6518
80 | 2682298.038 | 1250009.9764
81 | 2682325.4143 | 1249967.3201
82 | 2682386.5162 | 1249964.6791
83 | 2682379.2545 | 1249970.431
84 | 2682376.9647 | 1249956.5715
85 | 2682394.5336 | 1250056.3852
86 | 2682317.6289 | 1250093.7676
87 | 2682464.0023 | 1250019.7279
88 | 2682414.4361 | 1250010.9926
89 | 2682344.2562 | 1250043.2737
90 | 2682448.5991 | 1250021.3192
91 | 2682456.6366 | 1250178.2733
92 | 2682380.0252 | 1250178.3415
93 | 2682365.0928 | 1250133.9463
94 | 2682433.8701 | 1250164.4777
95 | 2682429.5393 | 1250011.7062
96 | 2682450.5908 | 1250010.7157
97 | 2682481.2594 | 1250004.5269
98 | 2682405.5419 | 1250073.9695
99 | 2682464.3022 | 1250321.5548
100 | 2682259.1999 | 1250069.6082
101 | 2682280.9271 | 1250078.3049
102 | 2682432.2785 | 1250234.3786
103 | 2682519.5182 | 1250095.8687
104 | 2682496.7031 | 1250113.2894
105 | 2682441.9962 | 1250099.554
106 | 2682479.3412 | 1250116.5554
107 | 2682301.9185 | 1250174.0868
108 | 2682263.691 | 1250190.5216
109 | 2682305.7041 | 1250154.8815
110 | 2682306.593 | 1250175.0081
111 | 2682261.0951 | 1250196.5425
112 | 2682294.2485 | 1250144.6807
113 | 2682324.7838 | 1250178.5935
114 | 2682318.6253 | 1250294.3566
115 | 2682316.2466 | 1250309.8613
116 | 2682322.8356 | 1250232.1519
117 | 2682331.1877 | 1250231.0815
118 | 2682354.4629 | 1250228.7983
119 | 2682381.8075 | 1250228.3739
120 | 2682332.1366 | 1250180.0445
121 | 2682346.7566 | 1250182.1663
122 | 2682408.3797 | 1250230.3857
123 | 2682389.3022 | 1250228.5567
124 | 2682446.6504 | 1250171.0402
125 | 2682344.2854 | 1250044.7251
126 | 2682344.3822 | 1250049.5295
127 | 2682344.4087 | 1250050.8461
128 | 2682344.637 | 1250062.1859
129 | 2682303.4471 | 1250087.4755
130 | 2682462.9475 | 1250085.7964
131 | 2682453.7365 | 1250091.8448
132 | 2682404.1384 | 1250131.7866

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98467 | -0.29408 | 0.00078648 | 0.00019711
1 | 0.98462 | -0.29501 | 0.0041044 | 0.0010287
2 | 0.98467 | -0.29403 | 0.00096172 | 0.00024103
3 | 0.98476 | -0.29235 | 0 | 0
4 | 0.98489 | -0.28973 | 0 | 0
5 | 0.99037 | -0.18444 | 0 | 0
6 | 0.99034 | -0.18501 | 0.010948 | 0.0027437
7 | 0.99058 | -0.18032 | 0 | 0
8 | 0.98675 | -0.25388 | 0 | 0
9 | 0.98678 | -0.25328 | 0.0029283 | 0.0007339
10 | 0.9867 | -0.25474 | 0.0021458 | 0.00053779
11 | 0.98751 | -0.24001 | 0 | 0
12 | 0.98728 | -0.24452 | 0 | 0
13 | 0.98786 | -0.23321 | 0 | 0
14 | 0.98725 | -0.24513 | 0.0063533 | 0.0015923
15 | 0.98892 | -0.2126 | 0 | 0
16 | 0.98698 | -0.25036 | 0 | 0
17 | 0.98758 | -0.23858 | 0.007536 | 0.0018887
18 | 0.99379 | -0.11858 | 0 | 0
19 | 0.99281 | -0.13735 | 0.016732 | 0.0041934
20 | 0.99457 | -0.10363 | 0.0097072 | 0.0024329
21 | 0.99859 | -0.026993 | 0 | 0
22 | 0.99786 | -0.041056 | 0.010752 | 0.0026948
23 | 0.99913 | -0.016617 | 0.0097117 | 0.002434
24 | 0.99559 | -0.084269 | 0 | 0
25 | 0.99552 | -0.085642 | 0.0094657 | 0.0023723
26 | 0.99592 | -0.07776 | 0.0051846 | 0.0012994
27 | 0.99671 | -0.062659 | 0 | 0
28 | 0.99631 | -0.070292 | 0 | 0
29 | 0.99512 | -0.092965 | 0 | 0
30 | 1 | 0 | -0.5938 | -0.15085
31 | 0.98748 | -0.24068 | 0 | 0
32 | 0.98727 | -0.24479 | 0 | 0
33 | 0.98758 | -0.23864 | 0.0074987 | 0.0018794
34 | 0.9872 | -0.24603 | 0.0050789 | 0.0012729
35 | 0.98739 | -0.24226 | 0 | 0
36 | 0.98744 | -0.24129 | 0 | 0
37 | 0.98719 | -0.24615 | 0.012809 | 0.0032103
38 | 0.99477 | -0.099824 | 0 | 0
39 | 0.99299 | -0.13379 | 0.0077157 | 0.0019337
40 | 0.98965 | -0.19843 | 0 | 0
41 | 0.98972 | -0.19717 | 0 | 0
42 | 0.98916 | -0.20803 | 0.010689 | 0.0026788
43 | 0.99614 | -0.073616 | 0.0051037 | 0.0012791
44 | 0.99071 | -0.17773 | 0 | 0
45 | 0.99064 | -0.17906 | 0.0039948 | 0.0010012
46 | 0.99076 | -0.17683 | 0.009393 | 0.0023541
47 | 0.99193 | -0.15413 | 0 | 0
48 | 0.9907 | -0.17761 | 0 | 0
49 | 0.99234 | -0.14625 | 0 | 0
50 | 0.99171 | -0.15831 | 0.0048238 | 0.001209
51 | 0.99013 | -0.18916 | 0 | 0
52 | 0.99072 | -0.17767 | 0.017626 | 0.0044176
53 | 0.98947 | -0.20204 | 0.0028163 | 0.00070584
54 | 0.97214 | -0.53915 | 0 | 0
55 | 0.97375 | -0.50734 | 0 | 0
56 | 0.97195 | -0.54298 | 0.0074238 | 0.0018606
57 | 0.9878 | -0.23435 | 0.0061382 | 0.0015384
58 | 0.99402 | -0.11419 | 0 | 0
59 | 0.97484 | -0.48596 | 0.019309 | 0.0048393
60 | 0.97184 | -0.54508 | 0 | 0
61 | 0.97176 | -0.54667 | 0.0077344 | 0.0019384
62 | 0.98722 | -0.24576 | 0.0047654 | 0.0011943
63 | 0.98674 | -0.25507 | 0.0053004 | 0.0013284
64 | 0.98683 | -0.25318 | 0.0054547 | 0.0013671
65 | 0.99377 | -0.11906 | 0 | 0
66 | 0.99389 | -0.11683 | 0.0080644 | 0.0020211
67 | 0.99271 | -0.13961 | 0.0067154 | 0.001683
68 | 0.98438 | -0.29969 | 0 | 0
69 | 0.98532 | -0.2814 | 0.0051787 | 0.0012979
70 | 0.98078 | -0.36988 | 0 | 0
71 | 0.98051 | -0.37527 | 0.0059848 | 0.0014999
72 | 0.98203 | -0.34552 | 0.0077703 | 0.0019474
73 | 0.98005 | -0.38429 | 0 | 0
74 | 0.98345 | -0.31777 | 0 | 0
75 | 0.98379 | -0.3111 | 0 | 0
76 | 0.98423 | -0.30253 | 0.0050928 | 0.0012764
77 | 0.98302 | -0.32609 | 0.0028696 | 0.00071918
78 | 0.99078 | -0.17644 | 0.0077036 | 0.0019307
79 | 0.98681 | -0.25264 | 0 | 0
80 | 0.98659 | -0.25788 | 0.0058627 | 0.0014693
81 | 0.98655 | -0.25868 | 0.0077898 | 0.0019523
82 | 0.98717 | -0.24661 | 0.005432 | 0.0013614
83 | 0.9874 | -0.24213 | 0.0066079 | 0.0016561
84 | 0.98735 | -0.24319 | 0.0042119 | 0.0010556
85 | 0.9918 | -0.15685 | 0.018032 | 0.0045192
86 | 0.99736 | -0.050675 | 0 | 0
87 | 0.98799 | -0.23077 | 0.0078013 | 0.0019552
88 | 0.98686 | -0.25264 | 0.0041644 | 0.0010437
89 | 0.98682 | -0.25345 | 0.0036311 | 0.00091005
90 | 0.98827 | -0.22522 | 0.0072771 | 0.0018238
91 | 0.99116 | -0.16902 | 0 | 0
92 | 0.99037 | -0.18403 | 0.008461 | 0.0021205
93 | 0.99132 | -0.16597 | 0.0080403 | 0.0020151
94 | 0.99149 | -0.16268 | 0.0045525 | 0.001141
95 | 0.98654 | -0.25892 | 0 | 0
96 | 0.98609 | -0.26769 | 0.01217 | 0.00305
97 | 0.98577 | -0.2739 | 0.01104 | 0.002767
98 | 0.98934 | -0.20443 | 0.0063274 | 0.0015858
99 | 0.98045 | -0.37635 | 0.0025168 | 0.00063077
100 | 0.9965 | -0.067242 | 0.0061578 | 0.0015433
101 | 0.99664 | -0.064713 | 0.0062003 | 0.0015539
102 | 0.97597 | -0.46381 | 0.0094511 | 0.0023687
103 | 0.9918 | -0.15711 | 0.010999 | 0.0027565
104 | 0.99213 | -0.15077 | 0.0063715 | 0.0015968
105 | 0.9937 | -0.12033 | 0.0056236 | 0.0014094
106 | 0.99241 | -0.14534 | 0.0053243 | 0.0013344
107 | 0.98762 | -0.23704 | 0 | 0
108 | 0.98615 | -0.26547 | 0.002467 | 0.0006183
109 | 0.98737 | -0.24192 | 0.0082129 | 0.0020584
110 | 0.98777 | -0.23412 | 0.0040896 | 0.0010249
111 | 0.98597 | -0.26887 | 0.0032579 | 0.0008165
112 | 0.98725 | -0.24424 | 0.0057388 | 0.0014383
113 | 0.98838 | -0.22241 | 0.0034157 | 0.00085606
114 | 0.97996 | -0.38595 | 0.0061902 | 0.0015514
115 | 0.98004 | -0.38451 | 0.0028854 | 0.00072314
116 | 0.98152 | -0.35518 | 0.0034839 | 0.00087314
117 | 0.98101 | -0.36504 | 0.003623 | 0.000908
118 | 0.97969 | -0.39095 | 0.0045571 | 0.0011421
119 | 0.97825 | -0.41908 | 0.0026539 | 0.00066512
120 | 0.98863 | -0.21757 | 0.0034136 | 0.00085553
121 | 0.98913 | -0.2078 | 0.0092197 | 0.0023107
122 | 0.97696 | -0.44435 | 0.0072833 | 0.0018254
123 | 0.97787 | -0.42644 | 0.0026539 | 0.00066512
124 | 0.99131 | -0.1661 | 0 | 0
125 | 0.98679 | -0.25395 | 0.0036599 | 0.00091726
126 | 0.98672 | -0.25529 | 0.0036309 | 0.00090999
127 | 0.98671 | -0.25558 | 0.0036599 | 0.00091726
128 | 0.98662 | -0.25727 | 0.0083327 | 0.0020884
129 | 0.99691 | -0.059441 | 0.019869 | 0.0049795
130 | 0.99355 | -0.12326 | 0.0035323 | 0.00088528
131 | 0.99359 | -0.12258 | 0.0055062 | 0.00138
132 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0041046 | 0.0010286 | -0.0041044 | -0.0010287 | 1.8189e-07 | -4.3942e-08 | 0.0062028 | 0.0062028 | 0.0062028 | 0.98467 | -0.29408 | 0.98462 | -0.29501 | 1.7041
1 | -0.0048911 | -0.0012257 | 0.0048911 | 0.0012257 | 1.1644e-08 | 2.2241e-10 | 0.0073913 | 0.0073913 | 0.0073913 | 0.98467 | -0.29408 | 0.98467 | -0.29403 | 2.0306
2 | -0.0058528 | -0.0014668 | 0.0058533 | 0.0014669 | 4.6927e-07 | 9.6831e-08 | 0.0088446 | 0.0088446 | 0.0088446 | 0.98467 | -0.29403 | 0.98476 | -0.29235 | 2.4298
3 | -0.0058533 | -0.0014669 | 0.005854 | 0.001467 | 7.3034e-07 | 1.5062e-07 | 0.0088446 | 0.0088444 | 0.0088446 | 0.98476 | -0.29235 | 0.98489 | -0.28973 | 2.4298
4 | 0.10217 | 0.025862 | -0.10212 | -0.025831 | 4.8828e-05 | 3.0139e-05 | 0.15445 | 0.15446 | 0.15446 | 0.98489 | -0.28973 | 0.98438 | -0.29969 | 10.6082
5 | -0.10802 | -0.027329 | 0.10807 | 0.027355 | 4.3221e-05 | 2.6781e-05 | 0.1633 | 0.1633 | 0.1633 | 0.98489 | -0.28973 | 0.98532 | -0.2814 | 11.2156
6 | 0.010948 | 0.0027439 | -0.010948 | -0.0027437 | 2.9759e-07 | 1.5272e-07 | 0.016449 | 0.016449 | 0.016449 | 0.99037 | -0.18444 | 0.99034 | -0.18501 | 4.519
7 | -0.010948 | -0.0027439 | 0.01095 | 0.002745 | 2.1514e-06 | 1.104e-06 | 0.016449 | 0.016449 | 0.016449 | 0.99037 | -0.18444 | 0.99058 | -0.18032 | 4.519
8 | -0.01095 | -0.002745 | 0.010952 | 0.002746 | 2.0251e-06 | 1.039e-06 | 0.016449 | 0.016449 | 0.016449 | 0.99058 | -0.18032 | 0.99078 | -0.17644 | 4.5189
9 | -0.0021459 | -0.00053756 | 0.0021459 | 0.0005374 | 6.1679e-08 | -1.6118e-07 | 0.0032359 | 0.0032358 | 0.0032359 | 0.98675 | -0.25388 | 0.98678 | -0.25328 | 0.88899
10 | 0.0021459 | 0.00053756 | -0.0021458 | -0.00053779 | 8.7766e-08 | -2.2932e-07 | 0.0032359 | 0.003236 | 0.003236 | 0.98675 | -0.25388 | 0.9867 | -0.25474 | 0.88901
11 | -0.0050742 | -0.0012713 | 0.0050744 | 0.0012713 | 1.5456e-07 | 8.9832e-09 | 0.0076516 | 0.0076515 | 0.0076516 | 0.98678 | -0.25328 | 0.98681 | -0.25264 | 2.1021
12 | 0.032491 | 0.0081566 | -0.032484 | -0.0081523 | 6.9811e-06 | 4.3686e-06 | 0.048964 | 0.048964 | 0.048964 | 0.98751 | -0.24001 | 0.98728 | -0.24452 | 13.4516
13 | -0.04428 | -0.011112 | 0.044294 | 0.011121 | 1.4365e-05 | 9.0835e-06 | 0.066728 | 0.066728 | 0.066728 | 0.98751 | -0.24001 | 0.98786 | -0.23321 | 18.3318
14 | 0.011789 | 0.0029553 | -0.011786 | -0.0029537 | 2.8723e-06 | 1.5278e-06 | 0.017764 | 0.017764 | 0.017764 | 0.98751 | -0.24001 | 0.98725 | -0.24513 | 4.8802
15 | 0.032484 | 0.0081523 | -0.032482 | -0.0081508 | 2.3361e-06 | 1.4619e-06 | 0.048964 | 0.048964 | 0.048964 | 0.98728 | -0.24452 | 0.9872 | -0.24603 | 13.4516
16 | -0.087091 | -0.021858 | 0.087177 | 0.021912 | 8.5696e-05 | 5.4675e-05 | 0.1312 | 0.1312 | 0.1312 | 0.98786 | -0.23321 | 0.98892 | -0.2126 | 36.0431
17 | 0.024435 | 0.0061326 | -0.024415 | -0.0061204 | 1.9963e-05 | 1.2274e-05 | 0.036809 | 0.036809 | 0.036809 | 0.98786 | -0.23321 | 0.98698 | -0.25036 | 10.1125
18 | 0.018363 | 0.0046041 | -0.018358 | -0.0046013 | 4.6979e-06 | 2.7971e-06 | 0.02766 | 0.02766 | 0.02766 | 0.98786 | -0.23321 | 0.98758 | -0.23858 | 7.599
19 | 0.0054324 | 0.0013614 | -0.005432 | -0.0013614 | 3.8331e-07 | 5.0378e-08 | 0.0081879 | 0.0081879 | 0.0081879 | 0.98725 | -0.24513 | 0.98717 | -0.24661 | 2.2494
20 | 0.041936 | 0.010538 | -0.041893 | -0.01051 | 4.348e-05 | 2.7454e-05 | 0.06311 | 0.063111 | 0.063111 | 0.98892 | -0.2126 | 0.9878 | -0.23435 | 17.3381
21 | -0.12911 | -0.03245 | 0.12926 | 0.032542 | 0.0001447 | 9.2475e-05 | 0.19431 | 0.19431 | 0.19431 | 0.98892 | -0.2126 | 0.99013 | -0.18916 | 53.3811
22 | 0.011166 | 0.0027992 | -0.011164 | -0.0027979 | 2.5043e-06 | 1.3017e-06 | 0.016835 | 0.016835 | 0.016835 | 0.98698 | -0.25036 | 0.98674 | -0.25507 | 4.6251
23 | 0.013248 | 0.0033212 | -0.013247 | -0.0033202 | 1.7819e-06 | 9.8822e-07 | 0.019974 | 0.019974 | 0.019974 | 0.98698 | -0.25036 | 0.98683 | -0.25318 | 5.4874
24 | 0.010822 | 0.0027126 | -0.01082 | -0.0027117 | 1.8282e-06 | 9.3548e-07 | 0.016306 | 0.016306 | 0.016306 | 0.98758 | -0.23858 | 0.9874 | -0.24213 | 4.4796
25 | 0.22959 | 0.057982 | -0.22939 | -0.057851 | 0.00020624 | 0.00013103 | 0.34393 | 0.34393 | 0.34393 | 0.99379 | -0.11858 | 0.99281 | -0.13735 | 23.6215
26 | -0.22959 | -0.057982 | 0.22976 | 0.058086 | 0.0001646 | 0.00010458 | 0.34393 | 0.34393 | 0.34393 | 0.99379 | -0.11858 | 0.99457 | -0.10363 | 23.6215
27 | 0.21265 | 0.053657 | -0.21246 | -0.053531 | 0.00019842 | 0.00012592 | 0.31885 | 0.31885 | 0.31885 | 0.99281 | -0.13735 | 0.9918 | -0.15685 | 21.8992
28 | -0.23946 | -0.060519 | 0.23959 | 0.060597 | 0.00012256 | 7.7912e-05 | 0.35845 | 0.35845 | 0.35845 | 0.99457 | -0.10363 | 0.99512 | -0.092965 | 24.619
29 | 0.04304 | 0.010809 | -0.043011 | -0.010791 | 2.886e-05 | 1.8226e-05 | 0.064142 | 0.064142 | 0.064142 | 0.99859 | -0.026993 | 0.99786 | -0.041056 | 17.6216
30 | -0.04304 | -0.010809 | 0.043061 | 0.010823 | 2.1319e-05 | 1.3463e-05 | 0.064142 | 0.064142 | 0.064142 | 0.99859 | -0.026993 | 0.99913 | -0.016617 | 17.6215
31 | 0.032259 | 0.0080963 | -0.032244 | -0.008087 | 1.4792e-05 | 9.2443e-06 | 0.048108 | 0.048108 | 0.048108 | 0.99786 | -0.041056 | 0.99736 | -0.050675 | 13.2166
32 | -0.052773 | -0.013257 | 0.052815 | 0.013283 | 4.1887e-05 | 2.6571e-05 | 0.078606 | 0.078606 | 0.078606 | 0.99913 | -0.016617 | 1 | 0 | 21.5951
33 | 0.0094663 | 0.0023726 | -0.0094657 | -0.0023723 | 6.1936e-07 | 2.8911e-07 | 0.014149 | 0.014149 | 0.014149 | 0.99559 | -0.084269 | 0.99552 | -0.085642 | 3.887
34 | -0.0094663 | -0.0023726 | 0.0094693 | 0.002374 | 2.9362e-06 | 1.3704e-06 | 0.014149 | 0.014148 | 0.014149 | 0.99559 | -0.084269 | 0.99592 | -0.07776 | 3.887
35 | -0.014654 | -0.0036734 | 0.014657 | 0.003675 | 2.8941e-06 | 1.6427e-06 | 0.021895 | 0.021895 | 0.021895 | 0.99592 | -0.07776 | 0.99614 | -0.073616 | 6.015
36 | 0.019771 | 0.0049603 | -0.019764 | -0.004956 | 7.1922e-06 | 4.3162e-06 | 0.029518 | 0.029518 | 0.029518 | 0.99671 | -0.062659 | 0.99631 | -0.070292 | 8.1095
37 | 0.51794 | 0.13156 | -0.51719 | -0.13108 | 0.00075436 | 0.00048209 | 0.77387 | 0.77387 | 0.77387 | 0.99671 | -0.062659 | 0.99512 | -0.092965 | 53.1505
38 | -0.53771 | -0.13652 | 0.53934 | 0.13756 | 0.0016265 | 0.0010396 | 0.80339 | 0.80339 | 0.80339 | 0.99671 | -0.062659 | 1 | 0 | 55.1778
39 | 0.019764 | 0.004956 | -0.019761 | -0.0049541 | 3.1306e-06 | 1.8788e-06 | 0.029518 | 0.029519 | 0.029519 | 0.99631 | -0.070292 | 0.99614 | -0.073616 | 8.1095
40 | 0.052245 | 0.013134 | -0.052228 | -0.013123 | 1.7104e-05 | 1.0849e-05 | 0.078137 | 0.078137 | 0.078137 | 0.99512 | -0.092965 | 0.99477 | -0.099824 | 21.4663
41 | 0.22535 | 0.057349 | -0.22491 | -0.057068 | 0.00044256 | 0.00028109 | 0.33728 | 0.33728 | 0.33728 | 0.99512 | -0.092965 | 0.99299 | -0.13379 | 23.165
42 | 0.0047665 | 0.0011943 | -0.0047656 | -0.0011943 | 9.3205e-07 | -1.9685e-08 | 0.0071825 | 0.0071827 | 0.0071827 | 0.98748 | -0.24068 | 0.98727 | -0.24479 | 1.9733
43 | -0.0047665 | -0.0011943 | 0.004767 | 0.0011943 | 4.6321e-07 | -9.8948e-09 | 0.0071825 | 0.0071824 | 0.0071825 | 0.98748 | -0.24068 | 0.98758 | -0.23864 | 1.9732
44 | 0.0047656 | 0.0011943 | -0.0047654 | -0.0011943 | 2.2055e-07 | -4.6141e-09 | 0.0071827 | 0.0071827 | 0.0071827 | 0.98727 | -0.24479 | 0.98722 | -0.24576 | 1.9733
45 | -0.012266 | -0.0030736 | 0.01227 | 0.0030761 | 4.599e-06 | 2.4837e-06 | 0.018481 | 0.018481 | 0.018481 | 0.98758 | -0.23864 | 0.98799 | -0.23077 | 5.0772
46 | 0.027403 | 0.0068779 | -0.027394 | -0.0068726 | 8.6329e-06 | 5.3526e-06 | 0.041308 | 0.041308 | 0.041308 | 0.9872 | -0.24603 | 0.98686 | -0.25264 | 11.3485
47 | -0.012812 | -0.0032116 | 0.012812 | 0.003212 | 5.9721e-07 | 3.2757e-07 | 0.019308 | 0.019308 | 0.019308 | 0.98739 | -0.24226 | 0.98744 | -0.24129 | 5.3043
48 | 0.012812 | 0.0032116 | -0.012809 | -0.0032103 | 2.3704e-06 | 1.3002e-06 | 0.019308 | 0.019308 | 0.019308 | 0.98739 | -0.24226 | 0.98719 | -0.24615 | 5.3044
49 | -0.035743 | -0.0089643 | 0.035754 | 0.0089717 | 1.1823e-05 | 7.4274e-06 | 0.053864 | 0.053864 | 0.053864 | 0.98744 | -0.24129 | 0.9878 | -0.23435 | 14.7978
50 | 0.02293 | 0.0057523 | -0.022917 | -0.0057442 | 1.3289e-05 | 8.1258e-06 | 0.034556 | 0.034556 | 0.034556 | 0.98744 | -0.24129 | 0.98682 | -0.25345 | 9.4935
51 | 0.052228 | 0.013123 | -0.052193 | -0.0131 | 3.5795e-05 | 2.2706e-05 | 0.078137 | 0.078137 | 0.078137 | 0.99477 | -0.099824 | 0.99402 | -0.11419 | 21.4663
52 | 0.21719 | 0.055134 | -0.21706 | -0.055052 | 0.00013013 | 8.2607e-05 | 0.32572 | 0.32572 | 0.32572 | 0.99299 | -0.13379 | 0.99234 | -0.14625 | 22.3709
53 | -0.038082 | -0.009562 | 0.038085 | 0.0095634 | 2.2886e-06 | 1.4408e-06 | 0.057266 | 0.057266 | 0.057266 | 0.98965 | -0.19843 | 0.98972 | -0.19717 | 15.7324
54 | 0.038082 | 0.009562 | -0.038065 | -0.009551 | 1.7429e-05 | 1.0973e-05 | 0.057266 | 0.057266 | 0.057266 | 0.98965 | -0.19843 | 0.98916 | -0.20803 | 15.7325
55 | 0.0091466 | 0.0022928 | -0.0091445 | -0.0022918 | 2.1203e-06 | 9.7288e-07 | 0.013752 | 0.013752 | 0.013752 | 0.98972 | -0.19717 | 0.98947 | -0.20204 | 3.778
56 | -0.047231 | -0.011856 | 0.047249 | 0.011868 | 1.8066e-05 | 1.1439e-05 | 0.071018 | 0.071018 | 0.071018 | 0.98972 | -0.19717 | 0.99013 | -0.18916 | 19.5104
57 | 0.027376 | 0.0068722 | -0.027354 | -0.0068583 | 2.242e-05 | 1.3897e-05 | 0.041187 | 0.041187 | 0.041187 | 0.98916 | -0.20803 | 0.98827 | -0.22522 | 11.3151
58 | 0.003995 | 0.0010011 | -0.0039948 | -0.0010012 | 2.5305e-07 | -7.9367e-08 | 0.0060003 | 0.0060004 | 0.0060004 | 0.99071 | -0.17773 | 0.99064 | -0.17906 | 1.6485
59 | -0.003995 | -0.0010011 | 0.0039952 | 0.001001 | 1.7083e-07 | -5.3603e-08 | 0.0060003 | 0.0060003 | 0.0060003 | 0.99071 | -0.17773 | 0.99076 | -0.17683 | 1.6484
60 | -0.013388 | -0.0033551 | 0.013393 | 0.0033579 | 4.9828e-06 | 2.7656e-06 | 0.020108 | 0.020107 | 0.020108 | 0.99076 | -0.17683 | 0.99116 | -0.16902 | 5.5241
61 | 0.16748 | 0.042578 | -0.16729 | -0.042459 | 0.00018915 | 0.00011941 | 0.25146 | 0.25146 | 0.25146 | 0.99193 | -0.15413 | 0.9907 | -0.17761 | 17.2704
62 | -0.19026 | -0.048293 | 0.19033 | 0.048339 | 7.212e-05 | 4.567e-05 | 0.28563 | 0.28563 | 0.28563 | 0.99193 | -0.15413 | 0.99234 | -0.14625 | 19.6177
63 | 0.022782 | 0.0057151 | -0.022777 | -0.0057123 | 4.5364e-06 | 2.7697e-06 | 0.034177 | 0.034178 | 0.034178 | 0.99193 | -0.15413 | 0.99171 | -0.15831 | 9.3894
64 | 0.16729 | 0.042459 | -0.16724 | -0.042426 | 5.1679e-05 | 3.2626e-05 | 0.25146 | 0.25146 | 0.25146 | 0.9907 | -0.17761 | 0.99037 | -0.18403 | 17.2704
65 | 0.02673 | 0.0067129 | -0.026705 | -0.0066973 | 2.5124e-05 | 1.5541e-05 | 0.040087 | 0.040087 | 0.040087 | 0.99234 | -0.14625 | 0.99132 | -0.16597 | 11.013
66 | 0.017953 | 0.0045033 | -0.01795 | -0.0045011 | 3.7433e-06 | 2.2183e-06 | 0.02694 | 0.02694 | 0.02694 | 0.99171 | -0.15831 | 0.99149 | -0.16268 | 7.401
67 | -0.17651 | -0.04441 | 0.1766 | 0.044472 | 9.6934e-05 | 6.1849e-05 | 0.26533 | 0.26533 | 0.26533 | 0.99013 | -0.18916 | 0.99072 | -0.17767 | 36.4458
68 | -0.19423 | -0.048889 | 0.19442 | 0.049012 | 0.00019347 | 0.00012257 | 0.2918 | 0.2918 | 0.2918 | 0.99072 | -0.17767 | 0.9918 | -0.15685 | 20.0411
69 | 0.0063281 | 0.001586 | -0.0063274 | -0.0015858 | 7.1987e-07 | 1.885e-07 | 0.0095166 | 0.0095167 | 0.0095167 | 0.98947 | -0.20204 | 0.98934 | -0.20443 | 2.6145
70 | -0.015162 | -0.0038012 | 0.015185 | 0.0038145 | 2.3014e-05 | 1.3314e-05 | 0.023209 | 0.023208 | 0.023209 | 0.97214 | -0.53915 | 0.97375 | -0.50734 | 6.376
71 | 0.015162 | 0.0038012 | -0.01516 | -0.0037996 | 2.765e-06 | 1.5999e-06 | 0.023209 | 0.023209 | 0.023209 | 0.97214 | -0.53915 | 0.97195 | -0.54298 | 6.376
72 | -0.015185 | -0.0038145 | 0.015201 | 0.0038234 | 1.5512e-05 | 8.9713e-06 | 0.023208 | 0.023208 | 0.023208 | 0.97375 | -0.50734 | 0.97484 | -0.48596 | 6.3759
73 | 0.0077358 | 0.001939 | -0.007735 | -0.0019387 | 7.7535e-07 | 3.1355e-07 | 0.011843 | 0.011843 | 0.011843 | 0.97195 | -0.54298 | 0.97184 | -0.54508 | 3.2537
74 | 0.02946 | 0.0074012 | -0.029453 | -0.0073969 | 6.8407e-06 | 4.2565e-06 | 0.044106 | 0.044107 | 0.044107 | 0.99402 | -0.11419 | 0.99377 | -0.11906 | 12.1172
75 | 0.022733 | 0.0056993 | -0.02273 | -0.0056976 | 2.8535e-06 | 1.7411e-06 | 0.034031 | 0.034031 | 0.034031 | 0.99402 | -0.11419 | 0.99389 | -0.11683 | 9.3492
76 | -0.03451 | -0.0086628 | 0.034547 | 0.0086857 | 3.6489e-05 | 2.2915e-05 | 0.052682 | 0.052682 | 0.052682 | 0.97484 | -0.48596 | 0.97597 | -0.46381 | 14.473
77 | 0.007735 | 0.0019387 | -0.0077344 | -0.0019384 | 5.858e-07 | 2.3692e-07 | 0.011843 | 0.011843 | 0.011843 | 0.97184 | -0.54508 | 0.97176 | -0.54667 | 3.2537
78 | 0.0058635 | 0.0014695 | -0.0058627 | -0.0014693 | 7.843e-07 | 1.6031e-07 | 0.0088422 | 0.0088423 | 0.0088423 | 0.98674 | -0.25507 | 0.98659 | -0.25788 | 2.4292
79 | 0.0077919 | 0.0019531 | -0.0077898 | -0.0019523 | 2.0415e-06 | 8.0286e-07 | 0.011749 | 0.011749 | 0.011749 | 0.98683 | -0.25318 | 0.98655 | -0.25868 | 3.2279
80 | 0.029453 | 0.0073969 | -0.029424 | -0.007379 | 2.8848e-05 | 1.7951e-05 | 0.044107 | 0.044107 | 0.044107 | 0.99377 | -0.11906 | 0.99271 | -0.13961 | 12.1172
81 | 0.014666 | 0.0036764 | -0.014663 | -0.003675 | 2.4509e-06 | 1.3929e-06 | 0.021957 | 0.021957 | 0.021957 | 0.99389 | -0.11683 | 0.9937 | -0.12033 | 6.0322
82 | 0.022709 | 0.0056959 | -0.022702 | -0.0056921 | 6.2035e-06 | 3.7857e-06 | 0.034041 | 0.034041 | 0.034041 | 0.99271 | -0.13961 | 0.99241 | -0.14534 | 9.3518
83 | 0.097028 | 0.024555 | -0.096975 | -0.024522 | 5.3111e-05 | 3.2654e-05 | 0.14676 | 0.14676 | 0.14676 | 0.98438 | -0.29969 | 0.98379 | -0.3111 | 10.0794
84 | 0.0050934 | 0.0012764 | -0.0050928 | -0.0012764 | 6.8955e-07 | 4.7047e-08 | 0.0076994 | 0.0076995 | 0.0076995 | 0.98438 | -0.29969 | 0.98423 | -0.30253 | 2.1152
85 | -0.11325 | -0.028653 | 0.11331 | 0.028696 | 6.8108e-05 | 4.2325e-05 | 0.17112 | 0.17112 | 0.17112 | 0.98532 | -0.2814 | 0.98597 | -0.26887 | 11.7527
86 | 0.0085039 | 0.0021314 | -0.0085017 | -0.0021305 | 2.1837e-06 | 9.5621e-07 | 0.012902 | 0.012902 | 0.012902 | 0.98078 | -0.36988 | 0.98051 | -0.37527 | 3.5445
87 | -0.017586 | -0.004409 | 0.017607 | 0.0044211 | 2.044e-05 | 1.2114e-05 | 0.026682 | 0.026681 | 0.026682 | 0.98078 | -0.36988 | 0.98203 | -0.34552 | 7.3302
88 | 0.0090823 | 0.0022775 | -0.0090761 | -0.0022746 | 6.2335e-06 | 2.8856e-06 | 0.01378 | 0.01378 | 0.01378 | 0.98078 | -0.36988 | 0.98005 | -0.38429 | 3.7858
89 | 0.0025169 | 0.00063055 | -0.0025168 | -0.00063077 | 1.2972e-07 | -2.1601e-07 | 0.0038196 | 0.0038197 | 0.0038197 | 0.98051 | -0.37527 | 0.98045 | -0.37635 | 1.0494
90 | -0.025377 | -0.0063685 | 0.025411 | 0.0063893 | 3.3624e-05 | 2.0751e-05 | 0.038455 | 0.038455 | 0.038455 | 0.98203 | -0.34552 | 0.98345 | -0.31777 | 10.5647
91 | 0.0028854 | 0.00072311 | -0.0028854 | -0.00072314 | 3.116e-08 | -3.4612e-08 | 0.0043809 | 0.0043809 | 0.0043809 | 0.98005 | -0.38429 | 0.98004 | -0.38451 | 1.2036
92 | 0.0061907 | 0.0015515 | -0.0061902 | -0.0015514 | 4.902e-07 | 1.273e-07 | 0.0093994 | 0.0093995 | 0.0093995 | 0.98005 | -0.38429 | 0.97996 | -0.38595 | 2.5823
93 | -0.025411 | -0.0063893 | 0.025419 | 0.0063943 | 8.0952e-06 | 4.9957e-06 | 0.038455 | 0.038455 | 0.038455 | 0.98345 | -0.31777 | 0.98379 | -0.3111 | 10.5646
94 | 0.071557 | 0.018128 | -0.071505 | -0.018096 | 5.1496e-05 | 3.2363e-05 | 0.1083 | 0.1083 | 0.1083 | 0.98379 | -0.3111 | 0.98302 | -0.32609 | 14.8766
95 | 0.068636 | 0.017377 | -0.06854 | -0.017316 | 9.5704e-05 | 6.0952e-05 | 0.10396 | 0.10396 | 0.10396 | 0.98302 | -0.32609 | 0.98152 | -0.35518 | 28.5599
96 | -0.018656 | -0.0046767 | 0.018665 | 0.0046822 | 9.3067e-06 | 5.5489e-06 | 0.028019 | 0.028018 | 0.028019 | 0.99078 | -0.17644 | 0.99132 | -0.16597 | 7.6974
97 | -0.12421 | -0.031459 | 0.1243 | 0.031517 | 9.3147e-05 | 5.8168e-05 | 0.18741 | 0.18741 | 0.18741 | 0.98681 | -0.25264 | 0.98762 | -0.23704 | 12.8715
98 | 0.11913 | 0.030188 | -0.11906 | -0.030142 | 7.3369e-05 | 4.5719e-05 | 0.17976 | 0.17976 | 0.17976 | 0.98681 | -0.25264 | 0.98615 | -0.26547 | 12.3461
99 | 0.0042121 | 0.0010556 | -0.0042119 | -0.0010556 | 2.1225e-07 | -4.3824e-08 | 0.0063476 | 0.0063477 | 0.0063477 | 0.9874 | -0.24213 | 0.98735 | -0.24319 | 1.7439
100 | 0.032244 | 0.008087 | -0.032231 | -0.0080786 | 1.3466e-05 | 8.416e-06 | 0.048108 | 0.048109 | 0.048109 | 0.99736 | -0.050675 | 0.99691 | -0.059441 | 13.2166
101 | -0.020072 | -0.0050313 | 0.020077 | 0.0050345 | 5.316e-06 | 3.2035e-06 | 0.03023 | 0.03023 | 0.03023 | 0.98799 | -0.23077 | 0.98827 | -0.22522 | 8.305
102 | 0.02323 | 0.0058289 | -0.023223 | -0.0058246 | 6.9574e-06 | 4.2596e-06 | 0.035029 | 0.035029 | 0.035029 | 0.98686 | -0.25264 | 0.98654 | -0.25892 | 9.6234
103 | 0.019286 | 0.0048341 | -0.019285 | -0.0048338 | 4.6039e-07 | 2.7611e-07 | 0.029081 | 0.029081 | 0.029081 | 0.98682 | -0.25345 | 0.98679 | -0.25395 | 7.9893
104 | -0.013393 | -0.0033579 | 0.013395 | 0.0033589 | 1.8659e-06 | 1.0356e-06 | 0.020107 | 0.020107 | 0.020107 | 0.99116 | -0.16902 | 0.99131 | -0.1661 | 5.524
105 | 0.15878 | 0.040305 | -0.1586 | -0.040191 | 0.00018135 | 0.00011432 | 0.23875 | 0.23875 | 0.23875 | 0.99037 | -0.18403 | 0.98913 | -0.2078 | 16.3974
106 | 0.013397 | 0.0033602 | -0.013395 | -0.0033589 | 2.182e-06 | 1.2109e-06 | 0.020107 | 0.020107 | 0.020107 | 0.99149 | -0.16268 | 0.99131 | -0.1661 | 5.524
107 | 0.023223 | 0.0058246 | -0.023213 | -0.0058187 | 9.7051e-06 | 5.9421e-06 | 0.035029 | 0.035029 | 0.035029 | 0.98654 | -0.25892 | 0.98609 | -0.26769 | 9.6235
108 | 0.011044 | 0.0027687 | -0.01104 | -0.002767 | 3.2648e-06 | 1.6897e-06 | 0.016665 | 0.016665 | 0.016665 | 0.98609 | -0.26769 | 0.98577 | -0.2739 | 4.5784
109 | -0.0061578 | -0.0015433 | 0.0061586 | 0.0015435 | 7.4205e-07 | 1.6997e-07 | 0.0091951 | 0.009195 | 0.0091951 | 0.9965 | -0.067242 | 0.99664 | -0.064713 | 2.5261
110 | -0.012359 | -0.0030974 | 0.012362 | 0.0030991 | 3.1047e-06 | 1.67e-06 | 0.018452 | 0.018452 | 0.018452 | 0.99664 | -0.064713 | 0.99691 | -0.059441 | 5.0693
111 | -0.043998 | -0.011054 | 0.044039 | 0.01108 | 4.0916e-05 | 2.5883e-05 | 0.067091 | 0.067091 | 0.067091 | 0.97597 | -0.46381 | 0.97696 | -0.44435 | 18.4317
112 | -0.010999 | -0.0027565 | 0.011002 | 0.0027582 | 3.3193e-06 | 1.7047e-06 | 0.016502 | 0.016501 | 0.016502 | 0.9918 | -0.15711 | 0.99213 | -0.15077 | 4.5334
113 | -0.017374 | -0.0043551 | 0.017378 | 0.0043577 | 4.4982e-06 | 2.6507e-06 | 0.026057 | 0.026057 | 0.026057 | 0.99213 | -0.15077 | 0.99241 | -0.14534 | 7.1586
114 | 0.0090396 | 0.0022656 | -0.0090386 | -0.0022652 | 9.6507e-07 | 4.3572e-07 | 0.013536 | 0.013536 | 0.013536 | 0.9937 | -0.12033 | 0.99359 | -0.12258 | 3.7188
115 | 0.013956 | 0.0034986 | -0.013952 | -0.0034967 | 3.2455e-06 | 1.8267e-06 | 0.021027 | 0.021027 | 0.021027 | 0.98762 | -0.23704 | 0.98737 | -0.24192 | 5.7766
116 | -0.13826 | -0.035016 | 0.13827 | 0.035028 | 1.9405e-05 | 1.2176e-05 | 0.20844 | 0.20844 | 0.20844 | 0.98762 | -0.23704 | 0.98777 | -0.23412 | 14.3156
117 | 0.11659 | 0.029524 | -0.11657 | -0.029512 | 1.9048e-05 | 1.1856e-05 | 0.17604 | 0.17604 | 0.17604 | 0.98615 | -0.26547 | 0.98597 | -0.26887 | 12.0904
118 | 0.0057394 | 0.0014384 | -0.0057388 | -0.0014383 | 6.3559e-07 | 1.1707e-07 | 0.0086496 | 0.0086497 | 0.0086497 | 0.98737 | -0.24192 | 0.98725 | -0.24424 | 2.3763
119 | -0.14236 | -0.036053 | 0.14244 | 0.036103 | 8.0047e-05 | 5.028e-05 | 0.2146 | 0.2146 | 0.2146 | 0.98777 | -0.23412 | 0.98838 | -0.22241 | 14.7388
120 | -0.14586 | -0.036959 | 0.14589 | 0.036981 | 3.3926e-05 | 2.1328e-05 | 0.21974 | 0.21974 | 0.21974 | 0.98838 | -0.22241 | 0.98863 | -0.21757 | 15.0919
121 | 0.065056 | 0.016442 | -0.065025 | -0.016423 | 3.0747e-05 | 1.9572e-05 | 0.098676 | 0.098676 | 0.098676 | 0.98152 | -0.35518 | 0.98101 | -0.36504 | 27.1089
122 | 0.061402 | 0.015515 | -0.061326 | -0.015466 | 7.6165e-05 | 4.8451e-05 | 0.093181 | 0.093181 | 0.093181 | 0.98101 | -0.36504 | 0.97969 | -0.39095 | 25.5992
123 | 0.056769 | 0.014324 | -0.056693 | -0.014276 | 7.6348e-05 | 4.8519e-05 | 0.086259 | 0.08626 | 0.08626 | 0.97969 | -0.39095 | 0.97825 | -0.41908 | 23.6977
124 | 0.054039 | 0.013611 | -0.05402 | -0.013599 | 1.9006e-05 | 1.207e-05 | 0.082223 | 0.082223 | 0.082223 | 0.97825 | -0.41908 | 0.97787 | -0.42644 | 22.5887
125 | -0.14931 | -0.037836 | 0.14938 | 0.03788 | 7.0157e-05 | 4.4141e-05 | 0.22488 | 0.22488 | 0.22488 | 0.98863 | -0.21757 | 0.98913 | -0.2078 | 15.4448
126 | -0.051322 | -0.012906 | 0.051366 | 0.012934 | 4.3948e-05 | 2.7887e-05 | 0.078185 | 0.078184 | 0.078185 | 0.97696 | -0.44435 | 0.97787 | -0.42644 | 21.4793
127 | 0.015625 | 0.0039166 | -0.015624 | -0.003916 | 1.0004e-06 | 5.7889e-07 | 0.023562 | 0.023562 | 0.023562 | 0.98679 | -0.25395 | 0.98672 | -0.25529 | 6.4731
128 | 0.011993 | 0.003006 | -0.011993 | -0.0030059 | 1.6154e-07 | 8.6568e-08 | 0.018087 | 0.018087 | 0.018087 | 0.98672 | -0.25529 | 0.98671 | -0.25558 | 4.9688
129 | 0.0083333 | 0.0020886 | -0.0083327 | -0.0020884 | 6.7174e-07 | 2.8506e-07 | 0.012567 | 0.012567 | 0.012567 | 0.98671 | -0.25558 | 0.98662 | -0.25727 | 3.4525
130 | -0.0035323 | -0.00088528 | 0.0035324 | 0.00088521 | 1.1565e-07 | -6.8699e-08 | 0.0052902 | 0.0052902 | 0.0052902 | 0.99355 | -0.12326 | 0.99359 | -0.12258 | 1.4534

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.59968 | 0.15232

## res_load
| p_mw | q_mvar
0 | 0.00078648 | 0.00019711
1 | 0.0041044 | 0.0010287
2 | 0.00096172 | 0.00024103
3 | 0.010948 | 0.0027437
4 | 0.0029283 | 0.0007339
5 | 0.0021458 | 0.00053779
6 | 0.0063533 | 0.0015923
7 | 0.007536 | 0.0018887
8 | 0.016732 | 0.0041934
9 | 0.0097072 | 0.0024329
10 | 0.010752 | 0.0026948
11 | 0.0097117 | 0.002434
12 | 0.0094657 | 0.0023723
13 | 0.0051846 | 0.0012994
14 | 0.0058789 | 0.0014734
15 | 0.0074987 | 0.0018794
16 | 0.0050789 | 0.0012729
17 | 0.012809 | 0.0032103
18 | 0.0077157 | 0.0019337
19 | 0.010689 | 0.0026788
20 | 0.0051037 | 0.0012791
21 | 0.0039948 | 0.0010012
22 | 0.009393 | 0.0023541
23 | 0.0048238 | 0.001209
24 | 0.017626 | 0.0044176
25 | 0.0028163 | 0.00070584
26 | 0.0074238 | 0.0018606
27 | 0.0061382 | 0.0015384
28 | 0.019309 | 0.0048393
29 | 0.0077344 | 0.0019384
30 | 0.0047654 | 0.0011943
31 | 0.0053004 | 0.0013284
32 | 0.0054547 | 0.0013671
33 | 0.0080644 | 0.0020211
34 | 0.0067154 | 0.001683
35 | 0.0051787 | 0.0012979
36 | 0.0059848 | 0.0014999
37 | 0.0077703 | 0.0019474
38 | 0.0050928 | 0.0012764
39 | 0.0028696 | 0.00071918
40 | 0.0077036 | 0.0019307
41 | 0.0058627 | 0.0014693
42 | 0.0077898 | 0.0019523
43 | 0.005432 | 0.0013614
44 | 0.0066079 | 0.0016561
45 | 0.0042119 | 0.0010556
46 | 0.018032 | 0.0045192
47 | 0.0078013 | 0.0019552
48 | 0.0041644 | 0.0010437
49 | 0.0036311 | 0.00091005
50 | 0.0072771 | 0.0018238
51 | 0.008461 | 0.0021205
52 | 0.0080403 | 0.0020151
53 | 0.0045525 | 0.001141
54 | 0.01217 | 0.00305
55 | 0.01104 | 0.002767
56 | 0.0063274 | 0.0015858
57 | 0.0025168 | 0.00063077
58 | 0.0061578 | 0.0015433
59 | 0.0062003 | 0.0015539
60 | 0.0094511 | 0.0023687
61 | 0.010999 | 0.0027565
62 | 0.0063715 | 0.0015968
63 | 0.0056236 | 0.0014094
64 | 0.0053243 | 0.0013344
65 | 0.002467 | 0.0006183
66 | 0.0082129 | 0.0020584
67 | 0.0040896 | 0.0010249
68 | 0.0032579 | 0.0008165
69 | 0.0057388 | 0.0014383
70 | 0.0034157 | 0.00085606
71 | 0.0061902 | 0.0015514
72 | 0.0028854 | 0.00072314
73 | 0.0034839 | 0.00087314
74 | 0.003623 | 0.000908
75 | 0.0045571 | 0.0011421
76 | 0.0026539 | 0.00066512
77 | 0.0034136 | 0.00085553
78 | 0.0092197 | 0.0023107
79 | 0.0072833 | 0.0018254
80 | 0.0026539 | 0.00066512
81 | 0.0036599 | 0.00091726
82 | 0.0036309 | 0.00090999
83 | 0.0036599 | 0.00091726
84 | 0.0083327 | 0.0020884
85 | 0.019869 | 0.0049795
86 | 0.0035323 | 0.00088528
87 | 0.0055062 | 0.00138

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1