## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-199_1_4_node_16 | 0.4 | n |  | TRUE
1 | bus_LV_261-199_1_4_node_19 | 0.4 | n |  | TRUE
2 | bus_LV_261-199_1_4_node_178 | 0.4 | n |  | TRUE
3 | bus_LV_261-199_1_4_node_30 | 0.4 | n |  | TRUE
4 | bus_LV_261-199_1_4_node_21 | 0.4 | n |  | TRUE
5 | bus_LV_261-199_1_4_node_52 | 0.4 | n |  | TRUE
6 | bus_LV_261-199_1_4_node_50 | 0.4 | n |  | TRUE
7 | bus_LV_261-199_1_4_node_22 | 0.4 | n |  | TRUE
8 | bus_LV_261-199_1_4_node_27 | 0.4 | n |  | TRUE
9 | bus_LV_261-199_1_4_node_36 | 0.4 | n |  | TRUE
10 | bus_LV_261-199_1_4_node_25 | 0.4 | n |  | TRUE
11 | bus_LV_261-199_1_4_node_28 | 0.4 | n |  | TRUE
12 | bus_LV_261-199_1_4_node_162 | 0.4 | n |  | TRUE
13 | bus_LV_261-199_1_4_node_166 | 0.4 | n |  | TRUE
14 | bus_LV_261-199_1_4_node_26 | 0.4 | n |  | TRUE
15 | bus_LV_261-199_1_4_node_108 | 0.4 | n |  | TRUE
16 | bus_LV_261-199_1_4_node_105 | 0.4 | n |  | TRUE
17 | bus_LV_261-199_1_4_node_185 | 0.4 | n |  | TRUE
18 | bus_LV_261-199_1_4_node_53 | 0.4 | n |  | TRUE
19 | bus_LV_261-199_1_4_node_48 | 0.4 | n |  | TRUE
20 | bus_LV_261-199_1_4_node_29 | 0.4 | n |  | TRUE
21 | bus_LV_261-199_1_4_node_38 | 0.4 | n |  | TRUE
22 | bus_LV_261-199_1_4_node_40 | 0.4 | n |  | TRUE
23 | bus_LV_261-199_1_4_node_39 | 0.4 | n |  | TRUE
24 | bus_LV_261-199_1_4_node_31 | 0.4 | n |  | TRUE
25 | bus_LV_261-199_1_4_node_82 | 0.4 | n |  | TRUE
26 | bus_LV_261-199_1_4_node_33 | 0.4 | n |  | TRUE
27 | bus_LV_261-199_1_4_node_81 | 0.4 | n |  | TRUE
28 | bus_LV_261-199_1_4_node_32 | 0.4 | n |  | TRUE
29 | bus_LV_261-199_1_4_node_79 | 0.4 | n |  | TRUE
30 | bus_LV_261-199_1_4_node_34 | 0.4 | n |  | TRUE
31 | bus_LV_261-199_1_4_node_94 | 0.4 | n |  | TRUE
32 | bus_LV_261-199_1_4_node_77 | 0.4 | n |  | TRUE
33 | bus_LV_261-199_1_4_node_78 | 0.4 | n |  | TRUE
34 | bus_LV_261-199_1_4_node_74 | 0.4 | n |  | TRUE
35 | bus_LV_261-199_1_4_node_88 | 0.4 | n |  | TRUE
36 | bus_LV_261-199_1_4_node_37 | 0.4 | n |  | TRUE
37 | bus_LV_261-199_1_4_node_176 | 0.4 | n |  | TRUE
38 | bus_LV_261-199_1_4_node_154 | 0.4 | n |  | TRUE
39 | bus_LV_261-199_1_4_node_184 | 0.4 | n |  | TRUE
40 | bus_LV_261-199_1_4_node_49 | 0.4 | n |  | TRUE
41 | bus_LV_261-199_1_4_node_84 | 0.4 | n |  | TRUE
42 | bus_LV_261-199_1_4_node_83 | 0.4 | n |  | TRUE
43 | bus_LV_261-199_1_4_node_150 | 0.4 | n |  | TRUE
44 | bus_LV_261-199_1_4_node_147 | 0.4 | n |  | TRUE
45 | bus_LV_261-199_1_4_node_160 | 0.4 | n |  | TRUE
46 | bus_LV_261-199_1_4_node_168 | 0.4 | n |  | TRUE
47 | bus_LV_261-199_1_4_node_164 | 0.4 | n |  | TRUE
48 | bus_LV_261-199_1_4_node_120 | 0.4 | n |  | TRUE
49 | bus_LV_261-199_1_4_node_106 | 0.4 | n |  | TRUE
50 | bus_LV_261-199_1_4_node_46 | 0.4 | n |  | TRUE
51 | bus_LV_261-199_1_4_node_80 | 0.4 | n |  | TRUE
52 | bus_LV_261-199_1_4_node_119 | 0.4 | n |  | TRUE
53 | bus_LV_261-199_1_4_node_93 | 0.4 | n |  | TRUE
54 | bus_LV_261-199_1_4_node_153 | 0.4 | n |  | TRUE
55 | bus_LV_261-199_1_4_node_182 | 0.4 | n |  | TRUE
56 | bus_LV_261-199_1_4_node_41 | 0.4 | n |  | TRUE
57 | bus_LV_261-199_1_4_node_42 | 0.4 | n |  | TRUE
58 | bus_LV_261-199_1_4_node_43 | 0.4 | n |  | TRUE
59 | bus_LV_261-199_1_4_node_44 | 0.4 | n |  | TRUE
60 | bus_LV_261-199_1_4_node_131 | 0.4 | n |  | TRUE
61 | bus_LV_261-199_1_4_node_47 | 0.4 | n |  | TRUE
62 | bus_LV_261-199_1_4_node_129 | 0.4 | n |  | TRUE
63 | bus_LV_261-199_1_4_node_45 | 0.4 | n |  | TRUE
64 | bus_LV_261-199_1_4_node_51 | 0.4 | n |  | TRUE
65 | bus_LV_261-199_1_4_node_75 | 0.4 | n |  | TRUE
66 | bus_LV_261-199_1_4_node_76 | 0.4 | n |  | TRUE
67 | bus_LV_261-199_1_4_node_90 | 0.4 | n |  | TRUE
68 | bus_LV_261-199_1_4_node_91 | 0.4 | n |  | TRUE
69 | bus_LV_261-199_1_4_node_85 | 0.4 | n |  | TRUE
70 | bus_LV_261-199_1_4_node_87 | 0.4 | n |  | TRUE
71 | bus_LV_261-199_1_4_node_89 | 0.4 | n |  | TRUE
72 | bus_LV_261-199_1_4_node_177 | 0.4 | n |  | TRUE
73 | bus_LV_261-199_1_4_node_92 | 0.4 | n |  | TRUE
74 | bus_LV_261-199_1_4_node_101 | 0.4 | n |  | TRUE
75 | bus_LV_261-199_1_4_node_102 | 0.4 | n |  | TRUE
76 | bus_LV_261-199_1_4_node_95 | 0.4 | n |  | TRUE
77 | bus_LV_261-199_1_4_node_96 | 0.4 | n |  | TRUE
78 | bus_LV_261-199_1_4_node_97 | 0.4 | n |  | TRUE
79 | bus_LV_261-199_1_4_node_98 | 0.4 | n |  | TRUE
80 | bus_LV_261-199_1_4_node_99 | 0.4 | n |  | TRUE
81 | bus_LV_261-199_1_4_node_100 | 0.4 | n |  | TRUE
82 | bus_LV_261-199_1_4_node_103 | 0.4 | n |  | TRUE
83 | bus_LV_261-199_1_4_node_104 | 0.4 | n |  | TRUE
84 | bus_LV_261-199_1_4_node_138 | 0.4 | n |  | TRUE
85 | bus_LV_261-199_1_4_node_137 | 0.4 | n |  | TRUE
86 | bus_LV_261-199_1_4_node_135 | 0.4 | n |  | TRUE
87 | bus_LV_261-199_1_4_node_117 | 0.4 | n |  | TRUE
88 | bus_LV_261-199_1_4_node_107 | 0.4 | n |  | TRUE
89 | bus_LV_261-199_1_4_node_112 | 0.4 | n |  | TRUE
90 | bus_LV_261-199_1_4_node_110 | 0.4 | n |  | TRUE
91 | bus_LV_261-199_1_4_node_109 | 0.4 | n |  | TRUE
92 | bus_LV_261-199_1_4_node_111 | 0.4 | n |  | TRUE
93 | bus_LV_261-199_1_4_node_113 | 0.4 | n |  | TRUE
94 | bus_LV_261-199_1_4_node_132 | 0.4 | n |  | TRUE
95 | bus_LV_261-199_1_4_node_130 | 0.4 | n |  | TRUE
96 | bus_LV_261-199_1_4_node_114 | 0.4 | n |  | TRUE
97 | bus_LV_261-199_1_4_node_115 | 0.4 | n |  | TRUE
98 | bus_LV_261-199_1_4_node_116 | 0.4 | n |  | TRUE
99 | bus_LV_261-199_1_4_node_118 | 0.4 | n |  | TRUE
100 | bus_LV_261-199_1_4_node_136 | 0.4 | n |  | TRUE
101 | bus_LV_261-199_1_4_node_128 | 0.4 | n |  | TRUE
102 | bus_LV_261-199_1_4_node_145 | 0.4 | n |  | TRUE
103 | bus_LV_261-199_1_4_node_146 | 0.4 | n |  | TRUE
104 | bus_LV_261-199_1_4_node_148 | 0.4 | n |  | TRUE
105 | bus_LV_261-199_1_4_node_149 | 0.4 | n |  | TRUE
106 | bus_LV_261-199_1_4_node_151 | 0.4 | n |  | TRUE
107 | bus_LV_261-199_1_4_node_152 | 0.4 | n |  | TRUE
108 | bus_LV_261-199_1_4_node_158 | 0.4 | n |  | TRUE
109 | bus_LV_261-199_1_4_node_155 | 0.4 | n |  | TRUE
110 | bus_LV_261-199_1_4_node_171 | 0.4 | n |  | TRUE
111 | bus_LV_261-199_1_4_node_156 | 0.4 | n |  | TRUE
112 | bus_LV_261-199_1_4_node_167 | 0.4 | n |  | TRUE
113 | bus_LV_261-199_1_4_node_169 | 0.4 | n |  | TRUE
114 | bus_LV_261-199_1_4_node_165 | 0.4 | n |  | TRUE
115 | bus_LV_261-199_1_4_node_157 | 0.4 | n |  | TRUE
116 | bus_LV_261-199_1_4_node_163 | 0.4 | n |  | TRUE
117 | bus_LV_261-199_1_4_node_170 | 0.4 | n |  | TRUE
118 | bus_LV_261-199_1_4_node_159 | 0.4 | n |  | TRUE
119 | bus_LV_261-199_1_4_node_161 | 0.4 | n |  | TRUE
120 | bus_LV_261-199_1_4_node_181 | 0.4 | n |  | TRUE
121 | bus_LV_261-199_1_4_node_180 | 0.4 | n |  | TRUE
122 | bus_LV_261-199_1_4_node_172 | 0.4 | n |  | TRUE
123 | bus_LV_261-199_1_4_node_173 | 0.4 | n |  | TRUE
124 | bus_LV_261-199_1_4_node_175 | 0.4 | n |  | TRUE
125 | bus_LV_261-199_1_4_node_179 | 0.4 | n |  | TRUE
126 | bus_LV_261-199_1_4_node_183 | 0.4 | n |  | TRUE
127 | bus_MV_543_0_node_12 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-199_1_4_load_178 | 2 | 0.011355 | 0.0028459 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-199_1_4_load_52 | 5 | 0.0032171 | 0.00080629 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-199_1_4_load_50 | 6 | 0.0020309 | 0.00050898 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-199_1_4_load_36 | 9 | 0.0036239 | 0.00090824 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-199_1_4_load_162 | 12 | 0.0017396 | 0.00043599 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-199_1_4_load_108 | 15 | 0.0040493 | 0.0010149 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-199_1_4_load_105 | 16 | 0.0048486 | 0.0012152 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-199_1_4_load_185 | 17 | 0.0014872 | 0.00037273 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-199_1_4_load_53 | 18 | 0.0013492 | 0.00033814 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-199_1_4_load_48 | 19 | 0.0010855 | 0.00027204 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-199_1_4_load_38 | 21 | 0.0050255 | 0.0012595 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-199_1_4_load_40 | 22 | 0.0059472 | 0.0014905 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-199_1_4_load_39 | 23 | 0.0054714 | 0.0013713 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-199_1_4_load_82 | 25 | 0.0058512 | 0.0014665 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-199_1_4_load_81 | 27 | 0.0035776 | 0.00089664 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-199_1_4_load_79 | 29 | 0.0068978 | 0.0017287 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-199_1_4_load_94 | 31 | 0.0033313 | 0.00083489 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-199_1_4_load_77 | 32 | 0.0047043 | 0.001179 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-199_1_4_load_78 | 33 | 0.0019934 | 0.0004996 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-199_1_4_load_74 | 34 | 0.0052736 | 0.0013217 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-199_1_4_load_176 | 37 | 0.0016969 | 0.00042527 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-199_1_4_load_184 | 39 | 0.00053724 | 0.00013465 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-199_1_4_load_84 | 41 | 0.0073545 | 0.0018432 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-199_1_4_load_83 | 42 | 0.0079641 | 0.001996 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-199_1_4_load_150 | 43 | 0.0027083 | 0.00067877 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-199_1_4_load_160 | 45 | 0.0022721 | 0.00056944 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-199_1_4_load_168 | 46 | 0.0018197 | 0.00045605 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-199_1_4_load_164 | 47 | 0.0023293 | 0.00058377 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-199_1_4_load_120 | 48 | 0.0036712 | 0.0009201 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-199_1_4_load_106 | 49 | 0.006415 | 0.0016078 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-199_1_4_load_46 | 50 | 0.0045528 | 0.001141 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-199_1_4_load_80 | 51 | 0.0019459 | 0.00048768 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-199_1_4_load_119 | 52 | 0.0016302 | 0.00040858 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-199_1_4_load_93 | 53 | 0.004352 | 0.0010907 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-199_1_4_load_153 | 54 | 0.0035047 | 0.00087835 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-199_1_4_load_41 | 56 | 0.0016197 | 0.00040595 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-199_1_4_load_42 | 57 | 0.0057256 | 0.001435 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-199_1_4_load_43 | 58 | 0.0023604 | 0.00059158 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-199_1_4_load_131 | 60 | 0.0022955 | 0.00057532 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-199_1_4_load_45 | 63 | 0.0022991 | 0.00057621 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-199_1_4_load_51 | 64 | 0.0048053 | 0.0012043 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-199_1_4_load_75 | 65 | 0.0063975 | 0.0016034 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-199_1_4_load_76 | 66 | 0.0020309 | 0.00050898 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-199_1_4_load_90 | 67 | 0.00038899 | 9.7489e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-199_1_4_load_91 | 68 | 0.00037897 | 9.4979e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-199_1_4_load_85 | 69 | 0.027586 | 0.0069137 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-199_1_4_load_89 | 71 | 0.0053489 | 0.0013406 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-199_1_4_load_177 | 72 | 0.0013568 | 0.00034005 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-199_1_4_load_92 | 73 | 0.00037575 | 9.4172e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-199_1_4_load_101 | 74 | 0.0003652 | 9.1528e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-199_1_4_load_102 | 75 | 0.005991 | 0.0015015 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-199_1_4_load_96 | 77 | 0.0099549 | 0.0024949 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-199_1_4_load_97 | 78 | 0.0043905 | 0.0011004 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-199_1_4_load_98 | 79 | 0.0031568 | 0.00079116 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-199_1_4_load_99 | 80 | 0.0096613 | 0.0024214 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-199_1_4_load_100 | 81 | 0.0023151 | 0.00058021 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-199_1_4_load_103 | 82 | 0.0038351 | 0.00096116 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-199_1_4_load_104 | 83 | 0.0043989 | 0.0011025 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-199_1_4_load_137 | 85 | 0.0058061 | 0.0014552 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-199_1_4_load_135 | 86 | 0.0042769 | 0.0010719 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-199_1_4_load_107 | 88 | 0.0037677 | 0.00094427 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-199_1_4_load_112 | 89 | 0.0017541 | 0.00043962 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-199_1_4_load_110 | 90 | 0.0064665 | 0.0016207 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-199_1_4_load_109 | 91 | 0.0037894 | 0.00094971 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-199_1_4_load_111 | 92 | 0.0014512 | 0.00036372 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-199_1_4_load_113 | 93 | 0.001365 | 0.00034211 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-199_1_4_load_132 | 94 | 0.0061117 | 0.0015317 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-199_1_4_load_130 | 95 | 0.0058135 | 0.001457 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-199_1_4_load_114 | 96 | 0.0027193 | 0.00068152 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-199_1_4_load_115 | 97 | 0.0072129 | 0.0018077 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-199_1_4_load_116 | 98 | 0.0074785 | 0.0018743 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-199_1_4_load_118 | 99 | 0.0028481 | 0.0007138 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-199_1_4_load_136 | 100 | 0.011904 | 0.0029833 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-199_1_4_load_128 | 101 | 0.01045 | 0.0026189 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-199_1_4_load_145 | 102 | 0.0026083 | 0.00065369 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-199_1_4_load_146 | 103 | 0.00093639 | 0.00023468 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-199_1_4_load_148 | 104 | 0.00095047 | 0.00023821 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-199_1_4_load_149 | 105 | 0.0012161 | 0.00030478 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-199_1_4_load_152 | 107 | 0.001047 | 0.0002624 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-199_1_4_load_158 | 108 | 0.0014238 | 0.00035685 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-199_1_4_load_155 | 109 | 0.0014704 | 0.00036852 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-199_1_4_load_171 | 110 | 0.0017159 | 0.00043005 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_261-199_1_4_load_156 | 111 | 0.0011304 | 0.00028331 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_261-199_1_4_load_169 | 113 | 0.0037505 | 0.00093996 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_261-199_1_4_load_165 | 114 | 0.0010489 | 0.00026289 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_261-199_1_4_load_157 | 115 | 0.0014626 | 0.00036657 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_261-199_1_4_load_163 | 116 | 0.0021278 | 0.00053328 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_261-199_1_4_load_170 | 117 | 0.0014632 | 0.00036671 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_261-199_1_4_load_159 | 118 | 0.0014893 | 0.00037324 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_261-199_1_4_load_161 | 119 | 0.001722 | 0.00043157 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_261-199_1_4_load_181 | 120 | 0.00086322 | 0.00021634 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_261-199_1_4_load_180 | 121 | 0.00055281 | 0.00013855 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_261-199_1_4_load_172 | 122 | 0.0018349 | 0.00045987 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_261-199_1_4_load_173 | 123 | 0.0005752 | 0.00014416 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_261-199_1_4_load_175 | 124 | 0.000698 | 0.00017493 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_261-199_1_4_load_179 | 125 | 0.0017254 | 0.00043243 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_261-199_1_4_load_183 | 126 | 0.00056476 | 0.00014154 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 82 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-199_1_4_line_0 |  | 0 | 1 | 0.15012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-199_1_4_line_1 |  | 0 | 2 | 0.039405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-199_1_4_line_2 |  | 1 | 3 | 0.058792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-199_1_4_line_3 |  | 2 | 35 | 0.03415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-199_1_4_line_4 |  | 3 | 22 | 0.01133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-199_1_4_line_5 |  | 3 | 23 | 0.03208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-199_1_4_line_6 |  | 4 | 5 | 0.003776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-199_1_4_line_7 |  | 4 | 6 | 0.01061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-199_1_4_line_8 |  | 6 | 40 | 0.0097292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-199_1_4_line_9 |  | 7 | 8 | 0.003257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-199_1_4_line_10 |  | 7 | 9 | 0.0075628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-199_1_4_line_11 |  | 8 | 17 | 0.009788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-199_1_4_line_12 |  | 9 | 20 | 0.0026194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-199_1_4_line_13 |  | 10 | 11 | 0.23824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-199_1_4_line_14 |  | 10 | 12 | 0.011867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-199_1_4_line_15 |  | 10 | 13 | 0.044125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-199_1_4_line_16 |  | 11 | 18 | 0.018758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-199_1_4_line_17 |  | 11 | 19 | 0.016579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-199_1_4_line_18 |  | 12 | 45 | 0.0017515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-199_1_4_line_19 |  | 13 | 46 | 0.011029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-199_1_4_line_20 |  | 13 | 47 | 0.033756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-199_1_4_line_21 |  | 14 | 15 | 0.011362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-199_1_4_line_22 |  | 14 | 16 | 0.013433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-199_1_4_line_23 |  | 15 | 48 | 0.022075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-199_1_4_line_24 |  | 16 | 49 | 0.027149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-199_1_4_line_25 |  | 19 | 50 | 0.015473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-199_1_4_line_26 |  | 20 | 21 | 0.018426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-199_1_4_line_27 |  | 21 | 23 | 0.021439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-199_1_4_line_28 |  | 22 | 28 | 0.042436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-199_1_4_line_29 |  | 24 | 25 | 0.0037821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-199_1_4_line_30 |  | 24 | 26 | 0.0072061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_261-199_1_4_line_31 |  | 24 | 27 | 0.019089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
32 | LV_261-199_1_4_line_32 |  | 25 | 42 | 0.016939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-199_1_4_line_33 |  | 26 | 31 | 0.011607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_261-199_1_4_line_34 |  | 27 | 51 | 0.010498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_261-199_1_4_line_35 |  | 28 | 29 | 0.020649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-199_1_4_line_36 |  | 28 | 30 | 0.0097046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-199_1_4_line_37 |  | 29 | 51 | 0.017033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-199_1_4_line_38 |  | 30 | 32 | 0.025652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-199_1_4_line_39 |  | 30 | 33 | 0.020532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-199_1_4_line_40 |  | 30 | 34 | 0.015577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-199_1_4_line_41 |  | 31 | 53 | 0.0028403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
42 | LV_261-199_1_4_line_42 |  | 32 | 52 | 0.02381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-199_1_4_line_43 |  | 35 | 72 | 0.033047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-199_1_4_line_44 |  | 36 | 37 | 0.028545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-199_1_4_line_45 |  | 36 | 38 | 0.026284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-199_1_4_line_46 |  | 36 | 39 | 0.022369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-199_1_4_line_47 |  | 38 | 54 | 0.0071509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-199_1_4_line_48 |  | 39 | 55 | 0.012854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-199_1_4_line_49 |  | 40 | 64 | 0.002978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-199_1_4_line_50 |  | 40 | 61 | 0.021347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-199_1_4_line_51 |  | 41 | 42 | 0.029977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-199_1_4_line_52 |  | 43 | 44 | 0.042363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-199_1_4_line_53 |  | 44 | 105 | 0.028726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-199_1_4_line_54 |  | 44 | 102 | 0.015103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-199_1_4_line_55 |  | 45 | 118 | 0.017719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-199_1_4_line_56 |  | 46 | 117 | 0.0032763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-199_1_4_line_57 |  | 47 | 114 | 0.016409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-199_1_4_line_58 |  | 49 | 88 | 0.0037382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-199_1_4_line_59 |  | 50 | 63 | 0.0020144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-199_1_4_line_60 |  | 53 | 76 | 0.015849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
61 | LV_261-199_1_4_line_61 |  | 55 | 121 | 0.011159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-199_1_4_line_62 |  | 55 | 126 | 0.02901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-199_1_4_line_63 |  | 56 | 57 | 0.0049731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-199_1_4_line_64 |  | 56 | 58 | 0.010705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-199_1_4_line_65 |  | 57 | 59 | 0.017868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-199_1_4_line_66 |  | 59 | 60 | 0.014669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-199_1_4_line_67 |  | 59 | 61 | 0.006231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-199_1_4_line_68 |  | 60 | 62 | 0.040014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
69 | LV_261-199_1_4_line_69 |  | 61 | 63 | 0.01394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-199_1_4_line_70 |  | 62 | 95 | 0.013597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-199_1_4_line_71 |  | 62 | 101 | 5.6137e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
72 | LV_261-199_1_4_line_72 |  | 65 | 66 | 0.02411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-199_1_4_line_73 |  | 66 | 67 | 0.019294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-199_1_4_line_74 |  | 67 | 68 | 0.019858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-199_1_4_line_75 |  | 68 | 73 | 0.0047717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-199_1_4_line_76 |  | 69 | 70 | 0.10713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-199_1_4_line_77 |  | 70 | 71 | 0.023138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-199_1_4_line_78 |  | 71 | 72 | 0.042453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-199_1_4_line_79 |  | 73 | 74 | 0.015465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-199_1_4_line_80 |  | 74 | 75 | 0.025457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_261-199_1_4_line_81 |  | 75 | 84 | 0.018176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-199_1_4_line_82 |  | 76 | 77 | 0.002514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_261-199_1_4_line_83 |  | 76 | 78 | 0.0054173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
84 | LV_261-199_1_4_line_84 |  | 78 | 79 | 0.019133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
85 | LV_261-199_1_4_line_85 |  | 79 | 80 | 0.0013689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
86 | LV_261-199_1_4_line_86 |  | 80 | 81 | 0.014485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
87 | LV_261-199_1_4_line_87 |  | 81 | 82 | 0.0051376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
88 | LV_261-199_1_4_line_88 |  | 82 | 83 | 0.022385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
89 | LV_261-199_1_4_line_89 |  | 83 | 86 | 0.0012768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
90 | LV_261-199_1_4_line_90 |  | 84 | 85 | 0.0086511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_261-199_1_4_line_91 |  | 85 | 100 | 0.020828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_261-199_1_4_line_92 |  | 86 | 87 | 0.012301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
93 | LV_261-199_1_4_line_93 |  | 87 | 100 | 0.0094859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_261-199_1_4_line_94 |  | 87 | 97 | 0.023533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
95 | LV_261-199_1_4_line_95 |  | 88 | 89 | 0.016829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_261-199_1_4_line_96 |  | 89 | 90 | 0.011614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_261-199_1_4_line_97 |  | 90 | 91 | 0.00086369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_261-199_1_4_line_98 |  | 91 | 92 | 0.010876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_261-199_1_4_line_99 |  | 92 | 93 | 0.0049651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_261-199_1_4_line_100 |  | 93 | 94 | 0.013169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_261-199_1_4_line_101 |  | 94 | 95 | 0.0054736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_261-199_1_4_line_102 |  | 96 | 97 | 0.007067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
103 | LV_261-199_1_4_line_103 |  | 96 | 98 | 0.02107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
104 | LV_261-199_1_4_line_104 |  | 98 | 99 | 0.01177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
105 | LV_261-199_1_4_line_105 |  | 99 | 101 | 0.0083396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
106 | LV_261-199_1_4_line_106 |  | 102 | 103 | 0.00027438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_261-199_1_4_line_107 |  | 103 | 104 | 0.023664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_261-199_1_4_line_108 |  | 104 | 106 | 0.0085972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_261-199_1_4_line_109 |  | 105 | 107 | 0.022315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-199_1_4_line_110 |  | 106 | 108 | 0.0090041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_261-199_1_4_line_111 |  | 106 | 109 | 0.013144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_261-199_1_4_line_112 |  | 108 | 110 | 0.007815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_261-199_1_4_line_113 |  | 109 | 111 | 0.015691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_261-199_1_4_line_114 |  | 110 | 117 | 0.012884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_261-199_1_4_line_115 |  | 111 | 115 | 0.0027605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_261-199_1_4_line_116 |  | 112 | 113 | 0.026348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_261-199_1_4_line_117 |  | 112 | 114 | 0.069859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_261-199_1_4_line_118 |  | 113 | 120 | 0.0064874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_261-199_1_4_line_119 |  | 115 | 116 | 0.0051681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_261-199_1_4_line_120 |  | 118 | 119 | 0.012092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_261-199_1_4_line_121 |  | 120 | 121 | 0.023596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_261-199_1_4_line_122 |  | 122 | 123 | 1.2697e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_261-199_1_4_line_123 |  | 123 | 124 | 0.018585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_261-199_1_4_line_124 |  | 124 | 125 | 0.00076306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_261-199_1_4_line_125 |  | 125 | 126 | 0.017868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-199_1_4_trafo_103 | 0.63 MVA 20/0.4 kV | 127 | 82 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17
0 | 2683656.442 | 1252568.1278 | 2683659.9786 | 1252573.6819 | 2683667.675 | 1252587.1451 | 2683677.9067 | 1252603.8466 | 2683683.1759 | 1252612.8278 | 2683686.3312 | 1252614.9184 | 2683695.0331 | 1252626.1163 | 2683701.7343 | 1252636.2964 | 2683704.201 | 1252640.1119 | 2683709.6251 | 1252645.6038 | 2683732.8675 | 1252630.8211 | 2683756.5664 | 1252615.7891
1 | 2683756.5664 | 1252615.7891 | 2683764.5962 | 1252609.3978 | 2683771.9375 | 1252597.804 | 2683779.3959 | 1252594.9962 | 2683786.3679 | 1252592.3691
2 | 2683656.442 | 1252568.1278 | 2683652.2672 | 1252561.8085 | 2683661.162 | 1252560.4331 | 2683669.9837 | 1252559.9573 | 2683681.3657 | 1252559.3509 | 2683696.4111 | 1252558.5294 | 2683696.1507 | 1252555.0565 | 2683699.5799 | 1252554.8603
3 | 2683817.1059 | 1252577.5831 | 2683796.7516 | 1252588.2366 | 2683788.4402 | 1252591.5882 | 2683786.3679 | 1252592.3691
4 | 2683699.5799 | 1252554.8603 | 2683710.6667 | 1252554.3165 | 2683710.8966 | 1252554.3036
5 | 2683699.5799 | 1252554.8603 | 2683699.3744 | 1252551.2436 | 2683698.9468 | 1252545.7223 | 2683698.1026 | 1252537.6376 | 2683696.5922 | 1252533.4353 | 2683692.8282 | 1252527.4221 | 2683691.1062 | 1252524.6877
6 | 2683738.3472 | 1252334.5981 | 2683739.7391 | 1252338.1093
7 | 2683738.3472 | 1252334.5981 | 2683748.2516 | 1252330.7938
8 | 2683757.3339 | 1252327.3054 | 2683748.2516 | 1252330.7938
9 | 2683662.7121 | 1252479.572 | 2683664.4466 | 1252482.3319
10 | 2683664.4466 | 1252482.3319 | 2683668.4764 | 1252488.7317
11 | 2683671.0787 | 1252474.4529 | 2683666.7542 | 1252477.1272 | 2683662.7121 | 1252479.572
12 | 2683669.8721 | 1252490.9483 | 2683668.4764 | 1252488.7317
13 | 2683838.7451 | 1252274.6949 | 2683827.5345 | 1252256.7561 | 2683821.462 | 1252246.3958 | 2683817.3733 | 1252237.1866 | 2683814.7157 | 1252227.6529 | 2683812.0908 | 1252212.0708 | 2683807.8915 | 1252181.8776 | 2683786.4515 | 1252195.0287 | 2683765.5994 | 1252207.1764 | 2683759.5277 | 1252210.0928 | 2683754.8371 | 1252212.4838 | 2683749.9196 | 1252215.4388 | 2683744.6297 | 1252216.9763 | 2683743.666 | 1252222.678 | 2683737.5106 | 1252237.9136 | 2683746.5287 | 1252246.0027 | 2683752.7531 | 1252256.8321 | 2683760.6527 | 1252274.6238
14 | 2683838.7451 | 1252274.6949 | 2683848.7792 | 1252268.3592
15 | 2683838.7451 | 1252274.6949 | 2683861.7593 | 1252312.3822
16 | 2683778.1544 | 1252267.7438 | 2683760.6527 | 1252274.6238
17 | 2683760.6527 | 1252274.6238 | 2683766.7071 | 1252290.0581
18 | 2683850.2602 | 1252267.4241 | 2683848.7792 | 1252268.3592
19 | 2683861.7593 | 1252312.3822 | 2683871.1455 | 1252306.5907
20 | 2683861.7593 | 1252312.3822 | 2683879.0545 | 1252341.3711
21 | 2683701.0316 | 1252432.411 | 2683704.1172 | 1252437.8365 | 2683706.6509 | 1252442.286
22 | 2683701.0316 | 1252432.411 | 2683704.0612 | 1252430.5858 | 2683709.5714 | 1252427.3278 | 2683712.442 | 1252425.3353
23 | 2683706.6509 | 1252442.286 | 2683716.0475 | 1252458.7874 | 2683717.573 | 1252461.4698
24 | 2683712.442 | 1252425.3353 | 2683716.4008 | 1252422.5874 | 2683727.7926 | 1252412.7632 | 2683733.7338 | 1252408.544
25 | 2683766.7071 | 1252290.0581 | 2683768.9864 | 1252295.8687 | 2683772.0542 | 1252304.5754
26 | 2683669.8721 | 1252490.9483 | 2683672.7729 | 1252495.5594 | 2683679.6855 | 1252506.5433
27 | 2683679.6855 | 1252506.5433 | 2683687.8826 | 1252519.5686 | 2683691.1062 | 1252524.6877
28 | 2683752.7446 | 1252549.3073 | 2683749.1746 | 1252550.9248 | 2683744.1519 | 1252552.2659 | 2683720.7954 | 1252553.7481 | 2683710.8966 | 1252554.3036
29 | 2683726.3332 | 1252491.4239 | 2683724.4703 | 1252488.1324
30 | 2683726.3332 | 1252491.4239 | 2683729.7058 | 1252489.8926 | 2683732.7344 | 1252488.1341
31 | 2683726.3332 | 1252491.4239 | 2683729.0598 | 1252496.0771 | 2683735.96 | 1252507.9071
32 | 2683724.4703 | 1252488.1324 | 2683716.1271 | 1252473.3906
33 | 2683732.7344 | 1252488.1341 | 2683742.7809 | 1252482.3205
34 | 2683741.2494 | 1252516.9755 | 2683735.96 | 1252507.9071
35 | 2683752.7446 | 1252549.3073 | 2683755.1442 | 1252547.729 | 2683756.1411 | 1252545.0188 | 2683755.5816 | 1252541.8863 | 2683749.8296 | 1252531.69
36 | 2683752.7446 | 1252549.3073 | 2683755.0295 | 1252553.1759 | 2683756.8168 | 1252558.0715
37 | 2683741.2494 | 1252516.9755 | 2683749.7579 | 1252531.5629 | 2683749.8296 | 1252531.69
38 | 2683756.8168 | 1252558.0715 | 2683759.8408 | 1252556.6354 | 2683762.1679 | 1252554.3221 | 2683763.2952 | 1252551.9918 | 2683764.5309 | 1252547.8618 | 2683764.1469 | 1252544.5983 | 2683762.851 | 1252540.7104 | 2683760.585 | 1252536.5476
39 | 2683756.8168 | 1252558.0715 | 2683752.0015 | 1252559.1598 | 2683743.2063 | 1252559.8916 | 2683736.4478 | 1252560.2717
40 | 2683756.8168 | 1252558.0715 | 2683762.1664 | 1252572.7015
41 | 2683745.2392 | 1252480.8979 | 2683742.7809 | 1252482.3205
42 | 2683760.585 | 1252536.5476 | 2683760.1367 | 1252535.7238 | 2683754.9757 | 1252527.1 | 2683748.6138 | 1252515.9674
43 | 2683817.1059 | 1252577.5831 | 2683825.105 | 1252600.0243 | 2683829.4906 | 1252603.7002 | 2683832.0943 | 1252606.0399
44 | 2684009.5229 | 1252417.6655 | 2684024.1862 | 1252442.1568
45 | 2684009.5229 | 1252417.6655 | 2683995.7881 | 1252395.2317
46 | 2684009.5229 | 1252417.6655 | 2683990.2476 | 1252429.0153
47 | 2683995.7881 | 1252395.2317 | 2683993.1285 | 1252388.5937
48 | 2683979.1709 | 1252435.5376 | 2683990.2476 | 1252429.0153
49 | 2683757.3339 | 1252327.3054 | 2683758.3661 | 1252330.0998
50 | 2683777.3146 | 1252319.6376 | 2683757.3339 | 1252327.3054
51 | 2683701.3564 | 1252447.3048 | 2683706.9016 | 1252457.0903 | 2683709.7438 | 1252462.112 | 2683716.1271 | 1252473.3906
52 | 2683939.757 | 1252264.2615 | 2683925.7447 | 1252243.792 | 2683915.8239 | 1252229.3064
53 | 2683939.757 | 1252264.2615 | 2683955.8403 | 1252288.0626
54 | 2683939.757 | 1252264.2615 | 2683926.9031 | 1252272.1908
55 | 2683865.2427 | 1252257.964 | 2683850.2602 | 1252267.4241
56 | 2683873.9338 | 1252304.8702 | 2683871.1455 | 1252306.5907
57 | 2683879.0545 | 1252341.3711 | 2683887.4617 | 1252355.4626
58 | 2683736.7821 | 1252406.3804 | 2683736.7735 | 1252406.3853 | 2683733.7338 | 1252408.544
59 | 2683772.7237 | 1252306.4754 | 2683772.0542 | 1252304.5754
60 | 2683758.9566 | 1252472.96 | 2683745.2392 | 1252480.8979
61 | 2683979.1709 | 1252435.5376 | 2683968.9123 | 1252439.9288
62 | 2683979.1709 | 1252435.5376 | 2683994.1032 | 1252460.4095
63 | 2683804.4927 | 1252309.2718 | 2683799.8458 | 1252311.0431
64 | 2683814.496 | 1252305.4586 | 2683804.4927 | 1252309.2718
65 | 2683783.1501 | 1252317.4073 | 2683799.8458 | 1252311.0431
66 | 2683783.1501 | 1252317.4073 | 2683788.7342 | 1252330.9714
67 | 2683783.1501 | 1252317.4073 | 2683777.3146 | 1252319.6376
68 | 2683803.9671 | 1252367.973 | 2683788.7342 | 1252330.9714
69 | 2683777.3146 | 1252319.6376 | 2683773.9713 | 1252310.0164 | 2683772.7237 | 1252306.4754
70 | 2683803.9671 | 1252367.973 | 2683792.1624 | 1252374.7214
71 | 2683803.989 | 1252368.0247 | 2683803.9671 | 1252367.973
72 | 2683804.5577 | 1252557.1947 | 2683799.5577 | 1252561.6785 | 2683786.0861 | 1252571.8178 | 2683785.645 | 1252572.118
73 | 2683804.5577 | 1252557.1947 | 2683812.2774 | 1252550.272 | 2683818.3986 | 1252543.7772
74 | 2683818.3986 | 1252543.7772 | 2683824.9047 | 1252536.8739 | 2683831.0451 | 1252528.5145
75 | 2683833.87 | 1252524.6688 | 2683831.0451 | 1252528.5145
76 | 2683892.1134 | 1252627.8379 | 2683907.1569 | 1252631.9318 | 2683915.1502 | 1252629.7322 | 2683925.9999 | 1252626.7392 | 2683930.1204 | 1252621.9606 | 2683918.0085 | 1252577.1554 | 2683909.1769 | 1252574.0724 | 2683906.4991 | 1252564.5269
77 | 2683892.1134 | 1252627.8379 | 2683883.2465 | 1252625.1215 | 2683876.5533 | 1252626.1164 | 2683869.741 | 1252624.1239
78 | 2683832.0943 | 1252606.0399 | 2683834.2302 | 1252607.9593 | 2683842.1419 | 1252614.7208 | 2683859.2142 | 1252621.0449 | 2683869.741 | 1252624.1239
79 | 2683833.87 | 1252524.6688 | 2683836.4402 | 1252521.1697 | 2683841.5497 | 1252511.2892
80 | 2683849.987 | 1252487.4488 | 2683849.814 | 1252490.2357 | 2683844.4947 | 1252505.5942 | 2683841.5497 | 1252511.2892
81 | 2683847.6525 | 1252469.6674 | 2683850.4594 | 1252479.837 | 2683849.987 | 1252487.4488
82 | 2683758.9566 | 1252472.96 | 2683757.7501 | 1252470.7524
83 | 2683758.9566 | 1252472.96 | 2683763.6439 | 1252470.244
84 | 2683780.2418 | 1252460.7276 | 2683771.9385 | 1252465.4378 | 2683763.6439 | 1252470.244
85 | 2683781.4326 | 1252460.0521 | 2683780.2418 | 1252460.7276
86 | 2683781.4326 | 1252460.0521 | 2683785.2301 | 1252457.8979 | 2683793.0845 | 1252451.5174
87 | 2683793.0845 | 1252451.5174 | 2683796.8811 | 1252448.4333 | 2683797.1111 | 1252448.3453
88 | 2683817.8583 | 1252439.9457 | 2683803.1567 | 1252446.0313 | 2683797.1111 | 1252448.3453
89 | 2683819.038 | 1252439.4573 | 2683817.8583 | 1252439.9457
90 | 2683847.6525 | 1252469.6674 | 2683844.1262 | 1252461.7676
91 | 2683834.8518 | 1252443.1308 | 2683840.8494 | 1252454.4264 | 2683844.1262 | 1252461.7676
92 | 2683830.4033 | 1252434.7527 | 2683819.038 | 1252439.4573
93 | 2683830.4033 | 1252434.7527 | 2683834.8518 | 1252443.1308
94 | 2683830.4033 | 1252434.7527 | 2683822.7391 | 1252415.8301 | 2683821.5617 | 1252412.9437
95 | 2683751.3922 | 1252398.0283 | 2683736.7821 | 1252406.3804
96 | 2683751.3922 | 1252398.0283 | 2683761.4753 | 1252392.2641
97 | 2683762.2251 | 1252391.8355 | 2683761.4753 | 1252392.2641
98 | 2683771.6673 | 1252386.4377 | 2683762.2251 | 1252391.8355
99 | 2683775.9778 | 1252383.9735 | 2683771.6673 | 1252386.4377
100 | 2683775.9778 | 1252383.9735 | 2683787.4105 | 1252377.4379
101 | 2683787.4105 | 1252377.4379 | 2683792.1624 | 1252374.7214
102 | 2683818.8926 | 1252406.4002 | 2683821.5617 | 1252412.9437
103 | 2683811.43 | 1252386.7004 | 2683816.0284 | 1252399.3783 | 2683818.8926 | 1252406.4002
104 | 2683807.243 | 1252375.7033 | 2683808.1958 | 1252377.9514 | 2683809.5055 | 1252381.3948 | 2683811.43 | 1252386.7004
105 | 2683807.243 | 1252375.7033 | 2683803.989 | 1252368.0247
106 | 2683926.9031 | 1252272.1908 | 2683926.6696 | 1252272.3348
107 | 2683906.5293 | 1252284.759 | 2683926.6696 | 1252272.3348
108 | 2683899.2124 | 1252289.2727 | 2683906.5293 | 1252284.759
109 | 2683966.8219 | 1252307.4052 | 2683964.9031 | 1252303.2581 | 2683962.2814 | 1252297.5945 | 2683955.8403 | 1252288.0626
110 | 2683899.2124 | 1252289.2727 | 2683891.5496 | 1252294.0009
111 | 2683899.2124 | 1252289.2727 | 2683906.5323 | 1252300.1899
112 | 2683884.8988 | 1252298.1046 | 2683891.5496 | 1252294.0009
113 | 2683906.5323 | 1252300.1899 | 2683915.2706 | 1252313.2225
114 | 2683884.8988 | 1252298.1046 | 2683873.9338 | 1252304.8702
115 | 2683916.8079 | 1252315.5153 | 2683915.2706 | 1252313.2225
116 | 2683936.9324 | 1252397.4994 | 2683950.0016 | 1252420.3773
117 | 2683936.9324 | 1252397.4994 | 2683928.9698 | 1252397.5088 | 2683920.5432 | 1252395.6548 | 2683913.2561 | 1252392.2045 | 2683908.174 | 1252387.6069 | 2683903.7814 | 1252382.8189 | 2683890.4819 | 1252360.5249 | 2683887.4617 | 1252355.4626
118 | 2683950.0016 | 1252420.3773 | 2683953.2196 | 1252426.0104
119 | 2683919.686 | 1252319.8078 | 2683916.8079 | 1252315.5153
120 | 2683875.4673 | 1252251.5082 | 2683865.2427 | 1252257.964
121 | 2683968.9123 | 1252439.9288 | 2683960.9921 | 1252439.6164 | 2683953.2196 | 1252426.0104
122 | 2684013.2594 | 1252492.3168 | 2684013.266 | 1252492.3277
123 | 2684013.2594 | 1252492.3168 | 2684003.6934 | 1252476.3832
124 | 2684003.3006 | 1252475.729 | 2684003.6934 | 1252476.3832
125 | 2683994.1032 | 1252460.4095 | 2684003.3006 | 1252475.729

## bus_geodata
| x | y | coords
0 | 2683756.5664 | 1252615.7891
1 | 2683656.442 | 1252568.1278
2 | 2683786.3679 | 1252592.3691
3 | 2683699.5799 | 1252554.8603
4 | 2683738.3472 | 1252334.5981
5 | 2683739.7391 | 1252338.1093
6 | 2683748.2516 | 1252330.7938
7 | 2683664.4466 | 1252482.3319
8 | 2683662.7121 | 1252479.572
9 | 2683668.4764 | 1252488.7317
10 | 2683838.7451 | 1252274.6949
11 | 2683760.6527 | 1252274.6238
12 | 2683848.7792 | 1252268.3592
13 | 2683861.7593 | 1252312.3822
14 | 2683701.0316 | 1252432.411
15 | 2683706.6509 | 1252442.286
16 | 2683712.442 | 1252425.3353
17 | 2683671.0787 | 1252474.4529
18 | 2683778.1544 | 1252267.7438
19 | 2683766.7071 | 1252290.0581
20 | 2683669.8721 | 1252490.9483
21 | 2683679.6855 | 1252506.5433
22 | 2683710.8966 | 1252554.3036
23 | 2683691.1062 | 1252524.6877
24 | 2683726.3332 | 1252491.4239
25 | 2683724.4703 | 1252488.1324
26 | 2683732.7344 | 1252488.1341
27 | 2683735.96 | 1252507.9071
28 | 2683752.7446 | 1252549.3073
29 | 2683749.8296 | 1252531.69
30 | 2683756.8168 | 1252558.0715
31 | 2683742.7809 | 1252482.3205
32 | 2683760.585 | 1252536.5476
33 | 2683736.4478 | 1252560.2717
34 | 2683762.1664 | 1252572.7015
35 | 2683817.1059 | 1252577.5831
36 | 2684009.5229 | 1252417.6655
37 | 2684024.1862 | 1252442.1568
38 | 2683995.7881 | 1252395.2317
39 | 2683990.2476 | 1252429.0153
40 | 2683757.3339 | 1252327.3054
41 | 2683701.3564 | 1252447.3048
42 | 2683716.1271 | 1252473.3906
43 | 2683915.8239 | 1252229.3064
44 | 2683939.757 | 1252264.2615
45 | 2683850.2602 | 1252267.4241
46 | 2683871.1455 | 1252306.5907
47 | 2683879.0545 | 1252341.3711
48 | 2683717.573 | 1252461.4698
49 | 2683733.7338 | 1252408.544
50 | 2683772.0542 | 1252304.5754
51 | 2683741.2494 | 1252516.9755
52 | 2683748.6138 | 1252515.9674
53 | 2683745.2392 | 1252480.8979
54 | 2683993.1285 | 1252388.5937
55 | 2683979.1709 | 1252435.5376
56 | 2683804.4927 | 1252309.2718
57 | 2683799.8458 | 1252311.0431
58 | 2683814.496 | 1252305.4586
59 | 2683783.1501 | 1252317.4073
60 | 2683788.7342 | 1252330.9714
61 | 2683777.3146 | 1252319.6376
62 | 2683803.9671 | 1252367.973
63 | 2683772.7237 | 1252306.4754
64 | 2683758.3661 | 1252330.0998
65 | 2683785.645 | 1252572.118
66 | 2683804.5577 | 1252557.1947
67 | 2683818.3986 | 1252543.7772
68 | 2683831.0451 | 1252528.5145
69 | 2683906.4991 | 1252564.5269
70 | 2683892.1134 | 1252627.8379
71 | 2683869.741 | 1252624.1239
72 | 2683832.0943 | 1252606.0399
73 | 2683833.87 | 1252524.6688
74 | 2683841.5497 | 1252511.2892
75 | 2683849.987 | 1252487.4488
76 | 2683758.9566 | 1252472.96
77 | 2683757.7501 | 1252470.7524
78 | 2683763.6439 | 1252470.244
79 | 2683780.2418 | 1252460.7276
80 | 2683781.4326 | 1252460.0521
81 | 2683793.0845 | 1252451.5174
82 | 2683797.1111 | 1252448.3453
83 | 2683817.8583 | 1252439.9457
84 | 2683847.6525 | 1252469.6674
85 | 2683844.1262 | 1252461.7676
86 | 2683819.038 | 1252439.4573
87 | 2683830.4033 | 1252434.7527
88 | 2683736.7821 | 1252406.3804
89 | 2683751.3922 | 1252398.0283
90 | 2683761.4753 | 1252392.2641
91 | 2683762.2251 | 1252391.8355
92 | 2683771.6673 | 1252386.4377
93 | 2683775.9778 | 1252383.9735
94 | 2683787.4105 | 1252377.4379
95 | 2683792.1624 | 1252374.7214
96 | 2683818.8926 | 1252406.4002
97 | 2683821.5617 | 1252412.9437
98 | 2683811.43 | 1252386.7004
99 | 2683807.243 | 1252375.7033
100 | 2683834.8518 | 1252443.1308
101 | 2683803.989 | 1252368.0247
102 | 2683926.9031 | 1252272.1908
103 | 2683926.6696 | 1252272.3348
104 | 2683906.5293 | 1252284.759
105 | 2683955.8403 | 1252288.0626
106 | 2683899.2124 | 1252289.2727
107 | 2683966.8219 | 1252307.4052
108 | 2683891.5496 | 1252294.0009
109 | 2683906.5323 | 1252300.1899
110 | 2683884.8988 | 1252298.1046
111 | 2683915.2706 | 1252313.2225
112 | 2683936.9324 | 1252397.4994
113 | 2683950.0016 | 1252420.3773
114 | 2683887.4617 | 1252355.4626
115 | 2683916.8079 | 1252315.5153
116 | 2683919.686 | 1252319.8078
117 | 2683873.9338 | 1252304.8702
118 | 2683865.2427 | 1252257.964
119 | 2683875.4673 | 1252251.5082
120 | 2683953.2196 | 1252426.0104
121 | 2683968.9123 | 1252439.9288
122 | 2684013.266 | 1252492.3277
123 | 2684013.2594 | 1252492.3168
124 | 2684003.6934 | 1252476.3832
125 | 2684003.3006 | 1252475.729
126 | 2683994.1032 | 1252460.4095
127 | 2683830.4033 | 1252434.7527

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9786 | -0.41051 | 0 | 0
1 | 0.985 | -0.28657 | 0 | 0
2 | 0.97693 | -0.44331 | 0.011355 | 0.0028459
3 | 0.9875 | -0.23847 | 0 | 0
4 | 0.98845 | -0.22078 | 0 | 0
5 | 0.98844 | -0.22099 | 0.0032171 | 0.00080629
6 | 0.98848 | -0.22017 | 0.0020309 | 0.00050898
7 | 0.98674 | -0.25344 | 0 | 0
8 | 0.98673 | -0.25353 | 0 | 0
9 | 0.98675 | -0.25324 | 0.0036239 | 0.00090824
10 | 0.97546 | -0.47264 | 0 | 0
11 | 0.98634 | -0.26112 | 0 | 0
12 | 0.97538 | -0.47421 | 0.0017396 | 0.00043599
13 | 0.97374 | -0.50647 | 0 | 0
14 | 0.98876 | -0.21537 | 0 | 0
15 | 0.98868 | -0.21693 | 0.0040493 | 0.0010149
16 | 0.98886 | -0.21352 | 0.0048486 | 0.0012152
17 | 0.98672 | -0.25379 | 0.0014872 | 0.00037273
18 | 0.98632 | -0.26157 | 0.0013492 | 0.00033814
19 | 0.98712 | -0.24617 | 0.0010855 | 0.00027204
20 | 0.98676 | -0.253 | 0 | 0
21 | 0.98685 | -0.25131 | 0.0050255 | 0.0012595
22 | 0.98815 | -0.22607 | 0.0059472 | 0.0014905
23 | 0.98704 | -0.24742 | 0.0054714 | 0.0013713
24 | 0.99499 | -0.095301 | 0 | 0
25 | 0.99492 | -0.096711 | 0.0058512 | 0.0014665
26 | 0.99537 | -0.088045 | 0 | 0
27 | 0.99417 | -0.11098 | 0.0035776 | 0.00089664
28 | 0.9908 | -0.17528 | 0 | 0
29 | 0.99235 | -0.1457 | 0.0068978 | 0.0017287
30 | 0.99068 | -0.17763 | 0 | 0
31 | 0.99598 | -0.07637 | 0.0033313 | 0.00083489
32 | 0.99053 | -0.18052 | 0.0047043 | 0.001179
33 | 0.99064 | -0.17836 | 0.0019934 | 0.0004996
34 | 0.9906 | -0.17909 | 0.0052736 | 0.0013217
35 | 0.97583 | -0.46472 | 0 | 0
36 | 0.97076 | -0.5653 | 0 | 0
37 | 0.97072 | -0.5662 | 0.0016969 | 0.00042527
38 | 0.97067 | -0.56701 | 0 | 0
39 | 0.97087 | -0.56315 | 0.00053724 | 0.00013465
40 | 0.98853 | -0.21926 | 0 | 0
41 | 0.99448 | -0.10517 | 0.0073545 | 0.0018432
42 | 0.99468 | -0.10128 | 0.0079641 | 0.001996
43 | 0.97253 | -0.53043 | 0.0027083 | 0.00067877
44 | 0.97263 | -0.52831 | 0 | 0
45 | 0.97537 | -0.47438 | 0.0022721 | 0.00056944
46 | 0.97351 | -0.51095 | 0.0018197 | 0.00045605
47 | 0.97312 | -0.51869 | 0.0023293 | 0.00058377
48 | 0.98861 | -0.21838 | 0.0036712 | 0.0009201
49 | 0.98917 | -0.20744 | 0.006415 | 0.0016078
50 | 0.98786 | -0.23194 | 0.0045528 | 0.001141
51 | 0.99373 | -0.11929 | 0.0019459 | 0.00048768
52 | 0.99049 | -0.18121 | 0.0016302 | 0.00040858
53 | 0.99614 | -0.073432 | 0.004352 | 0.0010907
54 | 0.97065 | -0.56747 | 0.0035047 | 0.00087835
55 | 0.97094 | -0.56179 | 0 | 0
56 | 0.98894 | -0.21128 | 0.0016197 | 0.00040595
57 | 0.98896 | -0.21093 | 0.0057256 | 0.001435
58 | 0.98892 | -0.21173 | 0.0023604 | 0.00059158
59 | 0.98912 | -0.20784 | 0 | 0
60 | 0.99018 | -0.18746 | 0.0022955 | 0.00057532
61 | 0.98873 | -0.21543 | 0 | 0
62 | 0.99167 | -0.15892 | 0 | 0
63 | 0.98797 | -0.22993 | 0.0022991 | 0.00057621
64 | 0.98852 | -0.21951 | 0.0048053 | 0.0012043
65 | 0.99475 | -0.10038 | 0.0063975 | 0.0016034
66 | 0.99489 | -0.097659 | 0.0020309 | 0.00050898
67 | 0.99504 | -0.094795 | 0.00038899 | 9.7489e-05
68 | 0.9952 | -0.091713 | 0.00037897 | 9.4979e-05
69 | 0.97011 | -0.5775 | 0.027586 | 0.0069137
70 | 0.97287 | -0.52292 | 0 | 0
71 | 0.97347 | -0.51117 | 0.0053489 | 0.0013406
72 | 0.97477 | -0.48549 | 0.0013568 | 0.00034005
73 | 0.99524 | -0.090941 | 0.00037575 | 9.4172e-05
74 | 0.99537 | -0.088335 | 0.0003652 | 9.1528e-05
75 | 0.99561 | -0.083885 | 0.005991 | 0.0015015
76 | 0.99703 | -0.056451 | 0 | 0
77 | 0.99701 | -0.05689 | 0.0099549 | 0.0024949
78 | 0.99736 | -0.050181 | 0.0043905 | 0.0011004
79 | 0.99856 | -0.027336 | 0.0031568 | 0.00079116
80 | 0.99865 | -0.025666 | 0.0096613 | 0.0024214
81 | 0.99964 | -0.0067896 | 0.0023151 | 0.00058021
82 | 1 | 0 | -0.3603 | -0.091502
83 | 0.99791 | -0.039665 | 0.0043989 | 0.0011025
84 | 0.99587 | -0.078794 | 0 | 0
85 | 0.99599 | -0.076372 | 0.0058061 | 0.0014552
86 | 0.9978 | -0.041883 | 0.0042769 | 0.0010719
87 | 0.9967 | -0.062819 | 0 | 0
88 | 0.98924 | -0.20617 | 0.0037677 | 0.00094427
89 | 0.98959 | -0.19935 | 0.0017541 | 0.00043962
90 | 0.98985 | -0.19429 | 0.0064665 | 0.0016207
91 | 0.98987 | -0.19381 | 0.0037894 | 0.00094971
92 | 0.99022 | -0.18709 | 0.0014512 | 0.00036372
93 | 0.99038 | -0.18389 | 0.001365 | 0.00034211
94 | 0.99084 | -0.1751 | 0.0061117 | 0.0015317
95 | 0.99106 | -0.17086 | 0.0058135 | 0.001457
96 | 0.99446 | -0.10557 | 0.0027193 | 0.00068152
97 | 0.99496 | -0.096029 | 0.0072129 | 0.0018077
98 | 0.99299 | -0.13359 | 0.0074785 | 0.0018743
99 | 0.99222 | -0.14849 | 0.0028481 | 0.0007138
100 | 0.99641 | -0.06842 | 0.011904 | 0.0029833
101 | 0.99168 | -0.15886 | 0.01045 | 0.0026189
102 | 0.9727 | -0.52693 | 0.0026083 | 0.00065369
103 | 0.9727 | -0.52689 | 0.00093639 | 0.00023468
104 | 0.97289 | -0.52318 | 0.00095047 | 0.00023821
105 | 0.97257 | -0.52951 | 0.0012161 | 0.00030478
106 | 0.97297 | -0.52168 | 0 | 0
107 | 0.97255 | -0.52994 | 0.001047 | 0.0002624
108 | 0.9731 | -0.51908 | 0.0014238 | 0.00035685
109 | 0.97289 | -0.52318 | 0.0014704 | 0.00036852
110 | 0.97322 | -0.51662 | 0.0017159 | 0.00043005
111 | 0.97282 | -0.52454 | 0.0011304 | 0.00028331
112 | 0.97179 | -0.54495 | 0 | 0
113 | 0.97139 | -0.55288 | 0.0037505 | 0.00093996
114 | 0.97285 | -0.52394 | 0.0010489 | 0.00026289
115 | 0.97281 | -0.52472 | 0.0014626 | 0.00036657
116 | 0.9728 | -0.52493 | 0.0021278 | 0.00053328
117 | 0.97345 | -0.51217 | 0.0014632 | 0.00036671
118 | 0.97532 | -0.47543 | 0.0014893 | 0.00037324
119 | 0.9753 | -0.47581 | 0.001722 | 0.00043157
120 | 0.97131 | -0.55439 | 0.00086322 | 0.00021634
121 | 0.97105 | -0.55949 | 0.00055281 | 0.00013855
122 | 0.97067 | -0.56715 | 0.0018349 | 0.00045987
123 | 0.97067 | -0.56715 | 0.0005752 | 0.00014416
124 | 0.97071 | -0.56632 | 0.000698 | 0.00017493
125 | 0.97071 | -0.56628 | 0.0017254 | 0.00043243
126 | 0.97079 | -0.56468 | 0.00056476 | 0.00014154
127 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.045917 | -0.011609 | 0.046191 | 0.011783 | 0.0002747 | 0.00017391 | 0.069855 | 0.069855 | 0.069855 | 0.9786 | -0.41051 | 0.985 | -0.28657 | 19.191
1 | 0.045917 | 0.011609 | -0.045845 | -0.011564 | 7.2109e-05 | 4.5655e-05 | 0.069855 | 0.069856 | 0.069856 | 0.9786 | -0.41051 | 0.97693 | -0.44331 | 19.1911
2 | -0.046191 | -0.011783 | 0.046299 | 0.011851 | 0.00010758 | 6.8102e-05 | 0.069855 | 0.069854 | 0.069855 | 0.985 | -0.28657 | 0.9875 | -0.23847 | 19.1909
3 | 0.034489 | 0.0087179 | -0.034454 | -0.0086956 | 3.5378e-05 | 2.2215e-05 | 0.05256 | 0.05256 | 0.05256 | 0.97693 | -0.44331 | 0.97583 | -0.46472 | 14.4395
4 | -0.061916 | -0.015768 | 0.061953 | 0.015791 | 3.7056e-05 | 2.3571e-05 | 0.093388 | 0.093388 | 0.093388 | 0.9875 | -0.23847 | 0.98815 | -0.22607 | 25.6559
5 | 0.015617 | 0.0039163 | -0.01561 | -0.0039125 | 6.6625e-06 | 3.8538e-06 | 0.023533 | 0.023534 | 0.023534 | 0.9875 | -0.23847 | 0.98704 | -0.24742 | 6.4653
6 | 0.0032172 | 0.00080626 | -0.0032171 | -0.00080629 | 3.3213e-08 | -2.7144e-08 | 0.0048431 | 0.0048431 | 0.0048431 | 0.98845 | -0.22078 | 0.98844 | -0.22099 | 1.3305
7 | -0.0032172 | -0.00080626 | 0.0032173 | 0.00080618 | 9.3322e-08 | -7.6276e-08 | 0.0048431 | 0.0048431 | 0.0048431 | 0.98845 | -0.22078 | 0.98848 | -0.22017 | 1.3305
8 | -0.0052481 | -0.0013152 | 0.0052483 | 0.0013152 | 2.2771e-07 | 2.1012e-08 | 0.0079002 | 0.0079002 | 0.0079002 | 0.98848 | -0.22017 | 0.98853 | -0.21926 | 2.1704
9 | 0.0014872 | 0.00037257 | -0.0014872 | -0.00037261 | 6.1432e-09 | -3.7672e-08 | 0.0022427 | 0.0022427 | 0.0022427 | 0.98674 | -0.25344 | 0.98673 | -0.25353 | 0.61613
10 | -0.0014872 | -0.00037257 | 0.0014872 | 0.00037249 | 1.4264e-08 | -8.7476e-08 | 0.0022427 | 0.0022427 | 0.0022427 | 0.98674 | -0.25344 | 0.98675 | -0.25324 | 0.61612
11 | 0.0014872 | 0.00037261 | -0.0014872 | -0.00037273 | 1.8462e-08 | -1.1321e-07 | 0.0022427 | 0.0022428 | 0.0022428 | 0.98673 | -0.25353 | 0.98672 | -0.25379 | 0.61614
12 | -0.0051112 | -0.0012807 | 0.0051112 | 0.0012807 | 5.8353e-08 | 3.8858e-09 | 0.0077075 | 0.0077075 | 0.0077075 | 0.98675 | -0.25324 | 0.98676 | -0.253 | 2.1175
13 | -0.049117 | -0.012353 | 0.049619 | 0.012671 | 0.00050174 | 0.00031811 | 0.074941 | 0.07494 | 0.074941 | 0.97546 | -0.47264 | 0.98634 | -0.26112 | 20.5883
14 | 0.0072237 | 0.0018102 | -0.0072232 | -0.00181 | 5.4037e-07 | 1.9771e-07 | 0.011019 | 0.011019 | 0.011019 | 0.97546 | -0.47264 | 0.97538 | -0.47421 | 3.0273
15 | 0.041893 | 0.010543 | -0.041826 | -0.0105 | 6.7611e-05 | 4.2721e-05 | 0.063922 | 0.063922 | 0.063922 | 0.97546 | -0.47264 | 0.97374 | -0.50647 | 17.561
16 | 0.0013492 | 0.00033791 | -0.0013492 | -0.00033814 | 2.9142e-08 | -2.2076e-07 | 0.0020354 | 0.0020354 | 0.0020354 | 0.98634 | -0.26112 | 0.98632 | -0.26157 | 0.55919
17 | -0.050968 | -0.013009 | 0.051005 | 0.013032 | 3.6839e-05 | 2.3365e-05 | 0.076976 | 0.076976 | 0.076976 | 0.98634 | -0.26112 | 0.98712 | -0.24617 | 21.1471
18 | 0.0054836 | 0.001374 | -0.0054835 | -0.001374 | 4.5965e-08 | 7.5572e-09 | 0.0083655 | 0.0083655 | 0.0083655 | 0.97538 | -0.47421 | 0.97537 | -0.47438 | 2.2982
19 | 0.022098 | 0.0055424 | -0.022093 | -0.0055395 | 4.7168e-06 | 2.8816e-06 | 0.03377 | 0.033771 | 0.033771 | 0.97374 | -0.50647 | 0.97351 | -0.51095 | 9.2776
20 | 0.019728 | 0.0049577 | -0.019716 | -0.0049508 | 1.1508e-05 | 6.9456e-06 | 0.030152 | 0.030152 | 0.030152 | 0.97374 | -0.50647 | 0.97312 | -0.51869 | 8.2835
21 | 0.0077214 | 0.0019351 | -0.0077208 | -0.0019348 | 5.7531e-07 | 2.2248e-07 | 0.01162 | 0.01162 | 0.01162 | 0.98876 | -0.21537 | 0.98868 | -0.21693 | 3.1923
22 | -0.0077214 | -0.0019351 | 0.0077221 | 0.0019353 | 6.8015e-07 | 2.6299e-07 | 0.01162 | 0.01162 | 0.01162 | 0.98876 | -0.21537 | 0.98886 | -0.21352 | 3.1923
23 | 0.0036715 | 0.00091997 | -0.0036712 | -0.0009201 | 2.5276e-07 | -1.213e-07 | 0.0055257 | 0.0055258 | 0.0055258 | 0.98868 | -0.21693 | 0.98861 | -0.21838 | 1.5181
24 | -0.012571 | -0.0031505 | 0.012574 | 0.0031525 | 3.6428e-06 | 1.983e-06 | 0.018916 | 0.018916 | 0.018916 | 0.98886 | -0.21352 | 0.98917 | -0.20744 | 5.1967
25 | -0.05209 | -0.013304 | 0.052126 | 0.013327 | 3.5858e-05 | 2.2751e-05 | 0.078612 | 0.078612 | 0.078612 | 0.98712 | -0.24617 | 0.98786 | -0.23194 | 21.5966
26 | -0.0051112 | -0.0012807 | 0.0051116 | 0.0012808 | 4.1047e-07 | 2.7307e-08 | 0.0077075 | 0.0077075 | 0.0077075 | 0.98676 | -0.253 | 0.98685 | -0.25131 | 2.1175
27 | -0.010137 | -0.0025403 | 0.010139 | 0.0025412 | 1.8784e-06 | 9.2819e-07 | 0.015285 | 0.015285 | 0.015285 | 0.98685 | -0.25131 | 0.98704 | -0.24742 | 4.1992
28 | -0.0679 | -0.017282 | 0.068067 | 0.017388 | 0.00016668 | 0.00010613 | 0.10234 | 0.10234 | 0.10234 | 0.98815 | -0.22607 | 0.9908 | -0.17528 | 28.1162
29 | 0.021176 | 0.0053089 | -0.021175 | -0.0053081 | 1.4225e-06 | 8.6128e-07 | 0.031669 | 0.031669 | 0.031669 | 0.99499 | -0.095301 | 0.99492 | -0.096711 | 8.7004
30 | -0.11561 | -0.029434 | 0.11565 | 0.02946 | 4.0464e-05 | 2.571e-05 | 0.17305 | 0.17305 | 0.17305 | 0.99499 | -0.095301 | 0.99537 | -0.088045 | 23.7712
31 | 0.094431 | 0.024125 | -0.094359 | -0.02408 | 7.1546e-05 | 4.5294e-05 | 0.14139 | 0.14139 | 0.14139 | 0.99499 | -0.095301 | 0.99417 | -0.11098 | 19.4211
32 | 0.015323 | 0.0038416 | -0.01532 | -0.0038397 | 3.3365e-06 | 1.9154e-06 | 0.022918 | 0.022918 | 0.022918 | 0.99492 | -0.096711 | 0.99468 | -0.10128 | 6.2963
33 | -0.11565 | -0.02946 | 0.11571 | 0.029502 | 6.5178e-05 | 4.1412e-05 | 0.17305 | 0.17305 | 0.17305 | 0.99537 | -0.088045 | 0.99598 | -0.07637 | 23.7712
34 | 0.090782 | 0.023184 | -0.090745 | -0.023161 | 3.6425e-05 | 2.304e-05 | 0.13603 | 0.13603 | 0.13603 | 0.99417 | -0.11098 | 0.99373 | -0.11929 | 18.6856
35 | -0.081672 | -0.020797 | 0.081788 | 0.020872 | 0.00011672 | 7.4434e-05 | 0.12277 | 0.12277 | 0.12277 | 0.9908 | -0.17528 | 0.99235 | -0.1457 | 33.7292
36 | 0.013605 | 0.0034095 | -0.013603 | -0.0034087 | 1.5192e-06 | 8.4732e-07 | 0.020432 | 0.020432 | 0.020432 | 0.9908 | -0.17528 | 0.99068 | -0.17763 | 5.6131
37 | -0.088686 | -0.022601 | 0.088799 | 0.022673 | 0.00011319 | 7.222e-05 | 0.13312 | 0.13312 | 0.13312 | 0.99235 | -0.1457 | 0.99373 | -0.11929 | 36.5707
38 | 0.0063355 | 0.0015876 | -0.0063346 | -0.0015873 | 8.711e-07 | 2.2725e-07 | 0.0095159 | 0.009516 | 0.009516 | 0.99068 | -0.17763 | 0.99053 | -0.18052 | 2.6143
39 | 0.0019935 | 0.00049938 | -0.0019934 | -0.0004996 | 6.9027e-08 | -2.2017e-07 | 0.0029942 | 0.0029943 | 0.0029943 | 0.99068 | -0.17763 | 0.99064 | -0.17836 | 0.8226
40 | 0.005274 | 0.0013217 | -0.0052736 | -0.0013217 | 3.6657e-07 | 3.4048e-08 | 0.0079216 | 0.0079217 | 0.0079217 | 0.99068 | -0.17763 | 0.9906 | -0.17909 | 2.1763
41 | -0.11904 | -0.030336 | 0.11906 | 0.030347 | 1.6879e-05 | 1.0729e-05 | 0.17803 | 0.17803 | 0.17803 | 0.99598 | -0.07637 | 0.99614 | -0.073432 | 24.4549
42 | 0.0016303 | 0.0004083 | -0.0016302 | -0.00040858 | 5.3554e-08 | -2.722e-07 | 0.002449 | 0.0024491 | 0.0024491 | 0.99053 | -0.18052 | 0.99049 | -0.18121 | 0.67283
43 | 0.034454 | 0.0086956 | -0.03442 | -0.0086741 | 3.4235e-05 | 2.1498e-05 | 0.05256 | 0.05256 | 0.05256 | 0.97583 | -0.46472 | 0.97477 | -0.48549 | 14.4396
44 | 0.0016969 | 0.00042496 | -0.0016969 | -0.00042527 | 7.2421e-08 | -3.0655e-07 | 0.002601 | 0.0026011 | 0.0026011 | 0.97076 | -0.5653 | 0.97072 | -0.5662 | 0.71459
45 | 0.003505 | 0.00087817 | -0.0035048 | -0.00087832 | 2.8451e-07 | -1.4284e-07 | 0.0053725 | 0.0053727 | 0.0053727 | 0.97076 | -0.5653 | 0.97067 | -0.56701 | 1.476
46 | -0.005202 | -0.0013031 | 0.0052025 | 0.0013032 | 5.3329e-07 | 6.4727e-08 | 0.0079735 | 0.0079734 | 0.0079735 | 0.97076 | -0.5653 | 0.97087 | -0.56315 | 2.1905
47 | 0.0035048 | 0.00087832 | -0.0035047 | -0.00087835 | 7.7406e-08 | -3.8851e-08 | 0.0053727 | 0.0053727 | 0.0053727 | 0.97067 | -0.56701 | 0.97065 | -0.56747 | 1.476
48 | -0.0057397 | -0.0014378 | 0.0057401 | 0.0014379 | 3.7302e-07 | 7.9764e-08 | 0.0087968 | 0.0087968 | 0.0087968 | 0.97087 | -0.56315 | 0.97094 | -0.56179 | 2.4167
49 | 0.0048054 | 0.0012043 | -0.0048053 | -0.0012043 | 5.8431e-08 | -7.8165e-10 | 0.0072334 | 0.0072334 | 0.0072334 | 0.98853 | -0.21926 | 0.98852 | -0.21951 | 1.9872
50 | -0.010054 | -0.0025195 | 0.010056 | 0.0025204 | 1.8334e-06 | 8.9963e-07 | 0.015134 | 0.015134 | 0.015134 | 0.98853 | -0.21926 | 0.98873 | -0.21543 | 4.1576
51 | -0.0073545 | -0.0018432 | 0.0073558 | 0.0018437 | 1.3613e-06 | 4.8219e-07 | 0.011004 | 0.011004 | 0.011004 | 0.99448 | -0.10517 | 0.99468 | -0.10128 | 3.0232
52 | -0.0027083 | -0.00067877 | 0.0027086 | 0.00067842 | 2.7278e-07 | -3.5113e-07 | 0.0041439 | 0.0041437 | 0.0041439 | 0.97253 | -0.53043 | 0.97263 | -0.52831 | 1.1384
53 | 0.0022632 | 0.00056665 | -0.0022631 | -0.00056692 | 1.2914e-07 | -2.7385e-07 | 0.0034623 | 0.0034624 | 0.0034624 | 0.97263 | -0.52831 | 0.97257 | -0.52951 | 0.95121
54 | -0.0049718 | -0.0012451 | 0.0049722 | 0.0012451 | 3.2764e-07 | 2.2234e-08 | 0.007606 | 0.0076059 | 0.007606 | 0.97263 | -0.52831 | 0.9727 | -0.52693 | 2.0896
55 | 0.0032114 | 0.00080456 | -0.0032113 | -0.00080468 | 1.5949e-07 | -1.1907e-07 | 0.0048992 | 0.0048993 | 0.0048993 | 0.97537 | -0.47438 | 0.97532 | -0.47543 | 1.346
56 | 0.020274 | 0.0050834 | -0.020272 | -0.0050827 | 1.1799e-06 | 7.1439e-07 | 0.030989 | 0.030989 | 0.030989 | 0.97351 | -0.51095 | 0.97345 | -0.51217 | 8.5135
57 | 0.017387 | 0.004367 | -0.017383 | -0.0043644 | 4.3506e-06 | 2.5806e-06 | 0.02659 | 0.02659 | 0.02659 | 0.97312 | -0.51869 | 0.97285 | -0.52394 | 7.305
58 | -0.018989 | -0.0047602 | 0.01899 | 0.0047609 | 1.1439e-06 | 6.8412e-07 | 0.028566 | 0.028566 | 0.028566 | 0.98917 | -0.20744 | 0.98924 | -0.20617 | 7.8478
59 | -0.056679 | -0.014468 | 0.056684 | 0.014472 | 5.5182e-06 | 3.5059e-06 | 0.08547 | 0.08547 | 0.08547 | 0.98786 | -0.23194 | 0.98797 | -0.22993 | 23.4806
60 | -0.12341 | -0.031438 | 0.12351 | 0.031502 | 0.00010119 | 6.4348e-05 | 0.18453 | 0.18453 | 0.18453 | 0.99614 | -0.073432 | 0.99703 | -0.056451 | 25.3478
61 | -0.01114 | -0.0027908 | 0.011141 | 0.0027915 | 1.2196e-06 | 6.4249e-07 | 0.017072 | 0.017072 | 0.017072 | 0.97094 | -0.56179 | 0.97105 | -0.55949 | 4.69
62 | 0.0053995 | 0.0013529 | -0.0053987 | -0.0013528 | 7.4492e-07 | 1.1801e-07 | 0.0082749 | 0.008275 | 0.008275 | 0.97094 | -0.56179 | 0.97079 | -0.56468 | 2.2734
63 | -0.0039802 | -0.00099742 | 0.0039803 | 0.0009974 | 6.6886e-08 | -2.1002e-08 | 0.0059888 | 0.0059888 | 0.0059888 | 0.98894 | -0.21128 | 0.98896 | -0.21093 | 1.6453
64 | 0.0023605 | 0.00059148 | -0.0023604 | -0.00059158 | 5.0641e-08 | -1.0494e-07 | 0.0035517 | 0.0035517 | 0.0035517 | 0.98894 | -0.21128 | 0.98892 | -0.21173 | 0.97575
65 | -0.0097059 | -0.0024324 | 0.0097074 | 0.0024331 | 1.429e-06 | 6.8524e-07 | 0.014604 | 0.014604 | 0.014604 | 0.98896 | -0.21093 | 0.98912 | -0.20784 | 4.012
66 | -0.078813 | -0.020044 | 0.078891 | 0.020093 | 7.7463e-05 | 4.9388e-05 | 0.11867 | 0.11867 | 0.11867 | 0.98912 | -0.20784 | 0.99018 | -0.18746 | 32.6014
67 | 0.069106 | 0.017611 | -0.06908 | -0.017595 | 2.5305e-05 | 1.6115e-05 | 0.10407 | 0.10407 | 0.10407 | 0.98912 | -0.20784 | 0.98873 | -0.21543 | 28.5894
68 | -0.081186 | -0.020669 | 0.081298 | 0.020739 | 0.00011189 | 7.0577e-05 | 0.12212 | 0.12212 | 0.12212 | 0.99018 | -0.18746 | 0.99167 | -0.15892 | 16.7745
69 | 0.059025 | 0.015074 | -0.058984 | -0.015048 | 4.1344e-05 | 2.6281e-05 | 0.088932 | 0.088932 | 0.088932 | 0.98873 | -0.21543 | 0.98797 | -0.22993 | 24.4319
70 | 0.049593 | 0.012462 | -0.049565 | -0.012444 | 2.8245e-05 | 1.7902e-05 | 0.074427 | 0.074427 | 0.074427 | 0.99167 | -0.15892 | 0.99106 | -0.17086 | 20.4469
71 | -0.13089 | -0.033201 | 0.13089 | 0.033202 | 4.0661e-07 | 2.5878e-07 | 0.19654 | 0.19654 | 0.19654 | 0.99167 | -0.15892 | 0.99168 | -0.15886 | 26.9979
72 | -0.0063975 | -0.0016034 | 0.0063983 | 0.0016036 | 8.2801e-07 | 2.1688e-07 | 0.0095698 | 0.0095697 | 0.0095698 | 0.99475 | -0.10038 | 0.99489 | -0.097659 | 2.6291
73 | -0.0084292 | -0.0021126 | 0.0084303 | 0.002113 | 1.15e-06 | 4.8539e-07 | 0.012607 | 0.012607 | 0.012607 | 0.99489 | -0.097659 | 0.99504 | -0.094795 | 3.4635
74 | -0.0088193 | -0.0022105 | 0.0088206 | 0.0022111 | 1.2953e-06 | 5.7102e-07 | 0.013189 | 0.013189 | 0.013189 | 0.99504 | -0.094795 | 0.9952 | -0.091713 | 3.6233
75 | -0.0091996 | -0.0023061 | 0.0091999 | 0.0023062 | 3.3856e-07 | 1.5468e-07 | 0.013755 | 0.013755 | 0.013755 | 0.9952 | -0.091713 | 0.99524 | -0.090941 | 3.7789
76 | -0.027586 | -0.0069137 | 0.027658 | 0.0069584 | 7.1926e-05 | 4.4706e-05 | 0.042313 | 0.042313 | 0.042313 | 0.97011 | -0.5775 | 0.97287 | -0.52292 | 11.6246
77 | -0.027658 | -0.0069584 | 0.027674 | 0.0069681 | 1.5535e-05 | 9.6548e-06 | 0.042313 | 0.042313 | 0.042313 | 0.97287 | -0.52292 | 0.97347 | -0.51117 | 11.6244
78 | -0.033022 | -0.0083087 | 0.033063 | 0.0083341 | 4.0582e-05 | 2.5444e-05 | 0.050489 | 0.050489 | 0.050489 | 0.97347 | -0.51117 | 0.97477 | -0.48549 | 13.8706
79 | -0.0095757 | -0.0024004 | 0.0095768 | 0.002401 | 1.1887e-06 | 5.5981e-07 | 0.014317 | 0.014317 | 0.014317 | 0.99524 | -0.090941 | 0.99537 | -0.088335 | 3.9333
80 | -0.0099421 | -0.0024925 | 0.0099442 | 0.0024935 | 2.1089e-06 | 1.0187e-06 | 0.014863 | 0.014863 | 0.014863 | 0.99537 | -0.088335 | 0.99561 | -0.083885 | 4.0832
81 | -0.015935 | -0.003995 | 0.015939 | 0.0039972 | 3.8664e-06 | 2.2381e-06 | 0.023817 | 0.023817 | 0.023817 | 0.99561 | -0.083885 | 0.99587 | -0.078794 | 6.5431
82 | 0.0099551 | 0.002495 | -0.0099549 | -0.0024949 | 2.0811e-07 | 1.004e-07 | 0.014858 | 0.014858 | 0.014858 | 0.99703 | -0.056451 | 0.99701 | -0.05689 | 4.0817
83 | -0.13347 | -0.033997 | 0.13351 | 0.034023 | 4.0382e-05 | 2.5703e-05 | 0.19939 | 0.19939 | 0.19939 | 0.99703 | -0.056451 | 0.99736 | -0.050181 | 27.3887
84 | -0.1379 | -0.035123 | 0.13805 | 0.03522 | 0.00015215 | 9.6873e-05 | 0.20594 | 0.20594 | 0.20594 | 0.99736 | -0.050181 | 0.99856 | -0.027336 | 28.2884
85 | -0.14121 | -0.036011 | 0.14122 | 0.036019 | 1.1389e-05 | 7.2531e-06 | 0.21064 | 0.21064 | 0.21064 | 0.99856 | -0.027336 | 0.99865 | -0.025666 | 28.9346
86 | -0.15088 | -0.03844 | 0.15102 | 0.038528 | 0.00013755 | 8.765e-05 | 0.22504 | 0.22504 | 0.22504 | 0.99865 | -0.025666 | 0.99964 | -0.0067896 | 30.912
87 | -0.15333 | -0.039108 | 0.15338 | 0.03914 | 5.029e-05 | 3.2051e-05 | 0.22849 | 0.22849 | 0.22849 | 0.99964 | -0.0067896 | 1 | 0 | 31.3853
88 | 0.20526 | 0.052362 | -0.20487 | -0.052112 | 0.00039239 | 0.00025054 | 0.30576 | 0.30576 | 0.30576 | 1 | 0 | 0.99791 | -0.039665 | 42.0003
89 | 0.20047 | 0.051009 | -0.20045 | -0.050996 | 2.1432e-05 | 1.3683e-05 | 0.2992 | 0.2992 | 0.2992 | 0.99791 | -0.039665 | 0.9978 | -0.041883 | 41.0993
90 | -0.015939 | -0.0039972 | 0.015941 | 0.0039983 | 1.8402e-06 | 1.0652e-06 | 0.023817 | 0.023817 | 0.023817 | 0.99587 | -0.078794 | 0.99599 | -0.076372 | 6.5431
91 | -0.021747 | -0.0054535 | 0.021755 | 0.0054585 | 8.2455e-06 | 5.0059e-06 | 0.032491 | 0.032491 | 0.032491 | 0.99599 | -0.076372 | 0.99641 | -0.06842 | 8.9261
92 | 0.19618 | 0.049924 | -0.19598 | -0.049797 | 0.00019776 | 0.00012625 | 0.29282 | 0.29283 | 0.29283 | 0.9978 | -0.041883 | 0.9967 | -0.062819 | 40.2232
93 | 0.033668 | 0.0084474 | -0.033659 | -0.0084418 | 8.9885e-06 | 5.6291e-06 | 0.050268 | 0.050268 | 0.050268 | 0.9967 | -0.062819 | 0.99641 | -0.06842 | 13.8098
94 | 0.16231 | 0.04135 | -0.16205 | -0.041185 | 0.0002596 | 0.00016553 | 0.24256 | 0.24256 | 0.24256 | 0.9967 | -0.062819 | 0.99496 | -0.096029 | 33.3184
95 | -0.022758 | -0.0057052 | 0.022766 | 0.0057097 | 7.3958e-06 | 4.5172e-06 | 0.034233 | 0.034233 | 0.034233 | 0.98924 | -0.20617 | 0.98959 | -0.19935 | 9.4048
96 | -0.02452 | -0.0061493 | 0.024526 | 0.0061529 | 5.921e-06 | 3.6402e-06 | 0.036871 | 0.036871 | 0.036871 | 0.98959 | -0.19935 | 0.98985 | -0.19429 | 10.1294
97 | -0.030992 | -0.0077736 | 0.030993 | 0.007774 | 7.0309e-07 | 4.3887e-07 | 0.046592 | 0.046592 | 0.046592 | 0.98985 | -0.19429 | 0.98987 | -0.19381 | 12.7999
98 | -0.034782 | -0.0087238 | 0.034793 | 0.0087308 | 1.1151e-05 | 6.9968e-06 | 0.052288 | 0.052288 | 0.052288 | 0.98987 | -0.19381 | 0.99022 | -0.18709 | 14.3649
99 | -0.036245 | -0.0090945 | 0.03625 | 0.0090979 | 5.5241e-06 | 3.4715e-06 | 0.054469 | 0.054469 | 0.054469 | 0.99022 | -0.18709 | 0.99038 | -0.18389 | 14.964
100 | -0.037615 | -0.0094401 | 0.037631 | 0.00945 | 1.5775e-05 | 9.9268e-06 | 0.05652 | 0.05652 | 0.05652 | 0.99038 | -0.18389 | 0.99084 | -0.1751 | 15.5274
101 | -0.043743 | -0.010982 | 0.043751 | 0.010987 | 8.8595e-06 | 5.5996e-06 | 0.065698 | 0.065698 | 0.065698 | 0.99084 | -0.1751 | 0.99106 | -0.17086 | 18.0489
102 | -0.15477 | -0.039331 | 0.15484 | 0.039377 | 7.1179e-05 | 4.5371e-05 | 0.23177 | 0.23177 | 0.23177 | 0.99446 | -0.10557 | 0.99496 | -0.096029 | 31.8366
103 | 0.15205 | 0.03865 | -0.15184 | -0.038519 | 0.00020483 | 0.00013054 | 0.2277 | 0.2277 | 0.2277 | 0.99446 | -0.10557 | 0.99299 | -0.13359 | 31.2777
104 | 0.14436 | 0.036645 | -0.14426 | -0.036579 | 0.00010343 | 6.5893e-05 | 0.2165 | 0.2165 | 0.2165 | 0.99299 | -0.13359 | 0.99222 | -0.14849 | 29.7384
105 | 0.14141 | 0.035865 | -0.14134 | -0.035821 | 7.0427e-05 | 4.4858e-05 | 0.21222 | 0.21222 | 0.21222 | 0.99222 | -0.14849 | 0.99168 | -0.15886 | 29.1517
106 | -0.0075804 | -0.0018988 | 0.0075804 | 0.0018988 | 1.3835e-08 | 5.4486e-09 | 0.011596 | 0.011596 | 0.011596 | 0.9727 | -0.52693 | 0.9727 | -0.52689 | 3.1857
107 | -0.0085168 | -0.0021335 | 0.0085183 | 0.0021341 | 1.5063e-06 | 6.7022e-07 | 0.013028 | 0.013028 | 0.013028 | 0.9727 | -0.52689 | 0.97289 | -0.52318 | 3.5792
108 | -0.0094688 | -0.0023723 | 0.0094695 | 0.0023727 | 6.7616e-07 | 3.2597e-07 | 0.014482 | 0.014482 | 0.014482 | 0.97289 | -0.52318 | 0.97297 | -0.52168 | 3.9786
109 | 0.001047 | 0.00026214 | -0.001047 | -0.0002624 | 2.1472e-08 | -2.6317e-07 | 0.0016018 | 0.0016019 | 0.0016019 | 0.97257 | -0.52951 | 0.97255 | -0.52994 | 0.44009
110 | -0.015662 | -0.0039244 | 0.015663 | 0.0039255 | 1.9371e-06 | 1.1279e-06 | 0.023952 | 0.023952 | 0.023952 | 0.97297 | -0.52168 | 0.9731 | -0.51908 | 6.5802
111 | 0.0061921 | 0.0015517 | -0.0061916 | -0.0015516 | 4.4202e-07 | 1.1966e-07 | 0.0094698 | 0.0094699 | 0.0094699 | 0.97297 | -0.52168 | 0.97289 | -0.52318 | 2.6016
112 | -0.017087 | -0.0042824 | 0.017089 | 0.0042836 | 2.0008e-06 | 1.1834e-06 | 0.026129 | 0.026129 | 0.026129 | 0.9731 | -0.51908 | 0.97322 | -0.51662 | 7.1783
113 | 0.0047212 | 0.0011831 | -0.0047209 | -0.0011831 | 3.0681e-07 | 1.5277e-09 | 0.0072209 | 0.007221 | 0.007221 | 0.97289 | -0.52318 | 0.97282 | -0.52454 | 1.9838
114 | -0.018805 | -0.0047136 | 0.018809 | 0.004716 | 3.9944e-06 | 2.3962e-06 | 0.028753 | 0.028753 | 0.028753 | 0.97322 | -0.51662 | 0.97345 | -0.51217 | 7.8991
115 | 0.0035905 | 0.00089978 | -0.0035905 | -0.0008998 | 3.1223e-08 | -1.4291e-08 | 0.0054919 | 0.0054919 | 0.0054919 | 0.97282 | -0.52454 | 0.97281 | -0.52472 | 1.5088
116 | 0.016317 | 0.004092 | -0.016311 | -0.0040883 | 6.1684e-06 | 3.6215e-06 | 0.024986 | 0.024986 | 0.024986 | 0.97179 | -0.54495 | 0.97139 | -0.55288 | 6.8643
117 | -0.016317 | -0.004092 | 0.016334 | 0.0041016 | 1.6355e-05 | 9.6005e-06 | 0.024986 | 0.024986 | 0.024986 | 0.97179 | -0.54495 | 0.97285 | -0.52394 | 6.8643
118 | 0.012561 | 0.0031484 | -0.01256 | -0.0031479 | 9.0066e-07 | 4.9612e-07 | 0.019241 | 0.019241 | 0.019241 | 0.97139 | -0.55288 | 0.97131 | -0.55439 | 5.286
119 | 0.0021278 | 0.00053323 | -0.0021278 | -0.00053328 | 2.053e-08 | -5.1025e-08 | 0.0032547 | 0.0032547 | 0.0032547 | 0.97281 | -0.52472 | 0.9728 | -0.52493 | 0.89416
120 | 0.001722 | 0.00043144 | -0.001722 | -0.00043157 | 3.1298e-08 | -1.3087e-07 | 0.0026272 | 0.0026272 | 0.0026272 | 0.97532 | -0.47543 | 0.9753 | -0.47581 | 0.72177
121 | 0.011696 | 0.0029315 | -0.011694 | -0.00293 | 2.8411e-06 | 1.5263e-06 | 0.017919 | 0.017919 | 0.017919 | 0.97131 | -0.55439 | 0.97105 | -0.55949 | 4.9227
122 | -0.0018349 | -0.00045987 | 0.0018349 | 0.00045987 | 3.6137e-11 | -1.3126e-10 | 0.0028129 | 0.0028129 | 0.0028129 | 0.97067 | -0.56715 | 0.97067 | -0.56715 | 0.77277
123 | -0.0024101 | -0.00060403 | 0.0024102 | 0.00060386 | 9.5132e-08 | -1.6885e-07 | 0.0036947 | 0.0036946 | 0.0036947 | 0.97067 | -0.56715 | 0.97071 | -0.56632 | 1.015
124 | -0.0031082 | -0.0007788 | 0.0031082 | 0.00077879 | 6.4959e-09 | -5.2756e-09 | 0.0047646 | 0.0047645 | 0.0047646 | 0.97071 | -0.56632 | 0.97071 | -0.56628 | 1.3089
125 | -0.0048336 | -0.0012112 | 0.004834 | 0.0012112 | 3.6786e-07 | 1.4522e-08 | 0.0074094 | 0.0074094 | 0.0074094 | 0.97071 | -0.56628 | 0.97079 | -0.56468 | 2.0356

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.36413 | 0.092463

## res_load
| p_mw | q_mvar
0 | 0.011355 | 0.0028459
1 | 0.0032171 | 0.00080629
2 | 0.0020309 | 0.00050898
3 | 0.0036239 | 0.00090824
4 | 0.0017396 | 0.00043599
5 | 0.0040493 | 0.0010149
6 | 0.0048486 | 0.0012152
7 | 0.0014872 | 0.00037273
8 | 0.0013492 | 0.00033814
9 | 0.0010855 | 0.00027204
10 | 0.0050255 | 0.0012595
11 | 0.0059472 | 0.0014905
12 | 0.0054714 | 0.0013713
13 | 0.0058512 | 0.0014665
14 | 0.0035776 | 0.00089664
15 | 0.0068978 | 0.0017287
16 | 0.0033313 | 0.00083489
17 | 0.0047043 | 0.001179
18 | 0.0019934 | 0.0004996
19 | 0.0052736 | 0.0013217
20 | 0.0016969 | 0.00042527
21 | 0.00053724 | 0.00013465
22 | 0.0073545 | 0.0018432
23 | 0.0079641 | 0.001996
24 | 0.0027083 | 0.00067877
25 | 0.0022721 | 0.00056944
26 | 0.0018197 | 0.00045605
27 | 0.0023293 | 0.00058377
28 | 0.0036712 | 0.0009201
29 | 0.006415 | 0.0016078
30 | 0.0045528 | 0.001141
31 | 0.0019459 | 0.00048768
32 | 0.0016302 | 0.00040858
33 | 0.004352 | 0.0010907
34 | 0.0035047 | 0.00087835
35 | 0.0016197 | 0.00040595
36 | 0.0057256 | 0.001435
37 | 0.0023604 | 0.00059158
38 | 0.0022955 | 0.00057532
39 | 0.0022991 | 0.00057621
40 | 0.0048053 | 0.0012043
41 | 0.0063975 | 0.0016034
42 | 0.0020309 | 0.00050898
43 | 0.00038899 | 9.7489e-05
44 | 0.00037897 | 9.4979e-05
45 | 0.027586 | 0.0069137
46 | 0.0053489 | 0.0013406
47 | 0.0013568 | 0.00034005
48 | 0.00037575 | 9.4172e-05
49 | 0.0003652 | 9.1528e-05
50 | 0.005991 | 0.0015015
51 | 0.0099549 | 0.0024949
52 | 0.0043905 | 0.0011004
53 | 0.0031568 | 0.00079116
54 | 0.0096613 | 0.0024214
55 | 0.0023151 | 0.00058021
56 | 0.0038351 | 0.00096116
57 | 0.0043989 | 0.0011025
58 | 0.0058061 | 0.0014552
59 | 0.0042769 | 0.0010719
60 | 0.0037677 | 0.00094427
61 | 0.0017541 | 0.00043962
62 | 0.0064665 | 0.0016207
63 | 0.0037894 | 0.00094971
64 | 0.0014512 | 0.00036372
65 | 0.001365 | 0.00034211
66 | 0.0061117 | 0.0015317
67 | 0.0058135 | 0.001457
68 | 0.0027193 | 0.00068152
69 | 0.0072129 | 0.0018077
70 | 0.0074785 | 0.0018743
71 | 0.0028481 | 0.0007138
72 | 0.011904 | 0.0029833
73 | 0.01045 | 0.0026189
74 | 0.0026083 | 0.00065369
75 | 0.00093639 | 0.00023468
76 | 0.00095047 | 0.00023821
77 | 0.0012161 | 0.00030478
78 | 0.001047 | 0.0002624
79 | 0.0014238 | 0.00035685
80 | 0.0014704 | 0.00036852
81 | 0.0017159 | 0.00043005
82 | 0.0011304 | 0.00028331
83 | 0.0037505 | 0.00093996
84 | 0.0010489 | 0.00026289
85 | 0.0014626 | 0.00036657
86 | 0.0021278 | 0.00053328
87 | 0.0014632 | 0.00036671
88 | 0.0014893 | 0.00037324
89 | 0.001722 | 0.00043157
90 | 0.00086322 | 0.00021634
91 | 0.00055281 | 0.00013855
92 | 0.0018349 | 0.00045987
93 | 0.0005752 | 0.00014416
94 | 0.000698 | 0.00017493
95 | 0.0017254 | 0.00043243
96 | 0.00056476 | 0.00014154

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1