## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-205_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-205_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-205_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-205_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-205_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-205_0_3_node_29 | 0.4 | n |  | TRUE
6 | bus_LV_261-205_0_3_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_261-205_0_3_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_261-205_0_3_node_19 | 0.4 | n |  | TRUE
9 | bus_LV_261-205_0_3_node_18 | 0.4 | n |  | TRUE
10 | bus_LV_261-205_0_3_node_22 | 0.4 | n |  | TRUE
11 | bus_LV_261-205_0_3_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_261-205_0_3_node_16 | 0.4 | n |  | TRUE
13 | bus_LV_261-205_0_3_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_261-205_0_3_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_261-205_0_3_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_261-205_0_3_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_261-205_0_3_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_261-205_0_3_node_17 | 0.4 | n |  | TRUE
19 | bus_LV_261-205_0_3_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_261-205_0_3_node_31 | 0.4 | n |  | TRUE
21 | bus_LV_261-205_0_3_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_261-205_0_3_node_21 | 0.4 | n |  | TRUE
23 | bus_LV_261-205_0_3_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_261-205_0_3_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_261-205_0_3_node_25 | 0.4 | n |  | TRUE
26 | bus_LV_261-205_0_3_node_28 | 0.4 | n |  | TRUE
27 | bus_LV_261-205_0_3_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_261-205_0_3_node_27 | 0.4 | n |  | TRUE
29 | bus_LV_261-205_0_3_node_32 | 0.4 | n |  | TRUE
30 | bus_LV_261-205_0_3_node_33 | 0.4 | n |  | TRUE
31 | bus_LV_261-205_0_3_node_30 | 0.4 | n |  | TRUE
32 | bus_MV_547_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-205_0_3_load_0 | 0 | 0.025191 | 0.0063134 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-205_0_3_load_1 | 1 | 0.033573 | 0.0084143 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-205_0_3_load_29 | 5 | 0.032894 | 0.008244 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-205_0_3_load_19 | 8 | 0.018791 | 0.0047095 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-205_0_3_load_18 | 9 | 0.087658 | 0.021969 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-205_0_3_load_22 | 10 | 0.0083112 | 0.002083 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-205_0_3_load_16 | 12 | 0.013243 | 0.0033191 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-205_0_3_load_12 | 15 | 0.018622 | 0.0046671 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-205_0_3_load_14 | 17 | 0.0053431 | 0.0013391 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-205_0_3_load_17 | 18 | 0.016271 | 0.0040778 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-205_0_3_load_15 | 19 | 0.022468 | 0.005631 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-205_0_3_load_31 | 20 | 0.033203 | 0.0083214 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-205_0_3_load_13 | 21 | 0.021398 | 0.0053628 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-205_0_3_load_21 | 22 | 0.0023094 | 0.00057879 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-205_0_3_load_20 | 23 | 0.001319 | 0.00033058 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-205_0_3_load_23 | 24 | 0.01475 | 0.0036967 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-205_0_3_load_24 | 27 | 0.0067351 | 0.001688 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-205_0_3_load_33 | 30 | 0.0096799 | 0.002426 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-205_0_3_load_30 | 31 | 0.032997 | 0.0082699 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 21 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-205_0_3_line_0 |  | 0 | 1 | 0.015272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_261-205_0_3_line_1 |  | 0 | 2 | 0.018271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_261-205_0_3_line_2 |  | 1 | 3 | 0.0068687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_261-205_0_3_line_3 |  | 2 | 4 | 0.006556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_261-205_0_3_line_4 |  | 3 | 5 | 0.0092714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-205_0_3_line_5 |  | 3 | 6 | 0.00827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-205_0_3_line_6 |  | 4 | 7 | 0.046141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_261-205_0_3_line_7 |  | 5 | 20 | 0.017305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-205_0_3_line_8 |  | 6 | 10 | 0.006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-205_0_3_line_9 |  | 7 | 8 | 0.022141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_261-205_0_3_line_10 |  | 7 | 9 | 0.022626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-205_0_3_line_11 |  | 8 | 18 | 0.024158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_261-205_0_3_line_12 |  | 9 | 11 | 0.023442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-205_0_3_line_13 |  | 10 | 24 | 0.028805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-205_0_3_line_14 |  | 10 | 23 | 0.016035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-205_0_3_line_15 |  | 11 | 12 | 0.016748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-205_0_3_line_16 |  | 13 | 14 | 0.032774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_261-205_0_3_line_17 |  | 13 | 15 | 0.018633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_261-205_0_3_line_18 |  | 14 | 18 | 0.034553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_261-205_0_3_line_19 |  | 14 | 19 | 0.011257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-205_0_3_line_20 |  | 14 | 16 | 0.10761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-205_0_3_line_21 |  | 15 | 21 | 0.017841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_261-205_0_3_line_22 |  | 16 | 17 | 0.10847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-205_0_3_line_23 |  | 20 | 31 | 0.017697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-205_0_3_line_24 |  | 22 | 23 | 0.0053094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-205_0_3_line_25 |  | 24 | 28 | 0.03093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-205_0_3_line_26 |  | 25 | 26 | 0.19943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-205_0_3_line_27 |  | 25 | 27 | 0.052628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-205_0_3_line_28 |  | 26 | 28 | 0.13941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-205_0_3_line_29 |  | 28 | 29 | 0.062397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-205_0_3_line_30 |  | 29 | 30 | 0.019484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-205_0_3_trafo_13 | 0.63 MVA 20/0.4 kV | 32 | 21 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2682200.6616 | 1246300.7244 | 2682205.0516 | 1246307.719 | 2682208.6014 | 1246313.7679
1 | 2682190.1011 | 1246285.8625 | 2682195.1394 | 1246291.9257 | 2682200.6616 | 1246300.7244
2 | 2682212.0779 | 1246319.6918 | 2682208.6014 | 1246313.7679
3 | 2682190.1011 | 1246285.8625 | 2682183.5268 | 1246285.9715
4 | 2682212.0779 | 1246319.6918 | 2682216.7689 | 1246327.6889
5 | 2682219.0749 | 1246315.2522 | 2682213.6176 | 1246318.7124 | 2682212.0779 | 1246319.6918
6 | 2682169.0743 | 1246319.7404 | 2682174.8652 | 1246320.0097 | 2682175.1646 | 1246314.7656 | 2682177.1329 | 1246286.1386 | 2682182.4156 | 1246286.0117 | 2682183.5268 | 1246285.9715
7 | 2682225.5246 | 1246342.6151 | 2682216.7689 | 1246327.6889
8 | 2682219.0749 | 1246315.2522 | 2682221.8647 | 1246313.4785 | 2682223.2214 | 1246312.6189 | 2682224.1512 | 1246312.0313
9 | 2682169.0743 | 1246319.7404 | 2682167.6417 | 1246341.8354
10 | 2682169.0743 | 1246319.7404 | 2682146.4885 | 1246318.3933
11 | 2682166.0787 | 1246365.9426 | 2682167.6417 | 1246341.8354
12 | 2682123.0868 | 1246319.7703 | 2682146.4885 | 1246318.3933
13 | 2682224.1512 | 1246312.0313 | 2682238.7618 | 1246336.8558
14 | 2682224.1512 | 1246312.0313 | 2682215.9241 | 1246298.2678
15 | 2682123.0868 | 1246319.7703 | 2682124.151 | 1246336.4849
16 | 2682160.0865 | 1246397.495 | 2682159.7585 | 1246402.0827 | 2682170.1299 | 1246402.7268 | 2682170.8635 | 1246389.594 | 2682175.4826 | 1246389.9138
17 | 2682175.4826 | 1246389.9138 | 2682176.7766 | 1246371.3256
18 | 2682160.0865 | 1246397.495 | 2682161.2038 | 1246397.5549 | 2682162.203 | 1246397.4131 | 2682163.0934 | 1246396.9473 | 2682163.7682 | 1246396.2228 | 2682164.1735 | 1246395.3278 | 2682166.0787 | 1246365.9426
19 | 2682160.0865 | 1246397.495 | 2682148.8486 | 1246396.8411
20 | 2682154.7456 | 1246485.2185 | 2682158.0759 | 1246485.3202 | 2682163.9685 | 1246485.8689 | 2682167.0261 | 1246444.0585 | 2682169.2413 | 1246413.9672 | 2682170.1299 | 1246402.7268 | 2682159.7585 | 1246402.0827 | 2682160.0865 | 1246397.495
21 | 2682176.7766 | 1246371.3256 | 2682178.0155 | 1246353.5277
22 | 2682154.7456 | 1246485.2185 | 2682159.3613 | 1246413.8413 | 2682158.8777 | 1246411.6664 | 2682157.6463 | 1246409.4811 | 2682155.5408 | 1246407.6839 | 2682151.8083 | 1246406.6203 | 2682126.3043 | 1246405.0228
23 | 2682234.4785 | 1246357.8793 | 2682225.5246 | 1246342.6151
24 | 2682213.2 | 1246293.7106 | 2682215.9241 | 1246298.2678
25 | 2682254.4501 | 1246363.5113 | 2682238.7618 | 1246336.8558
26 | 2682315.3926 | 1246474.7046 | 2682318.8915 | 1246469.7384 | 2682319.7392 | 1246468.5382 | 2682320.5868 | 1246467.338 | 2682326.0586 | 1246459.5749 | 2682322.487 | 1246457.2681 | 2682313.1055 | 1246450.6219 | 2682302.2542 | 1246440.4751 | 2682296.2004 | 1246433.5749 | 2682301.7797 | 1246430.5723 | 2682310.1829 | 1246426.0634 | 2682313.3233 | 1246421.8817 | 2682348.0356 | 1246370.3814 | 2682377.484 | 1246329.1157 | 2682381.9164 | 1246324.9409 | 2682382.9797 | 1246324.5331
27 | 2682382.9797 | 1246324.5331 | 2682382.7387 | 1246271.9055
28 | 2682254.4501 | 1246363.5113 | 2682249.7068 | 1246366.1474 | 2682248.5642 | 1246366.8209 | 2682279.5304 | 1246420.2561 | 2682283.3479 | 1246426.6249 | 2682290.239 | 1246437.4284 | 2682296.4496 | 1246446.0986 | 2682301.9802 | 1246452.5912 | 2682306.088 | 1246457.0848 | 2682310.8769 | 1246461.499 | 2682319.7392 | 1246468.5382 | 2682318.8915 | 1246469.7384 | 2682315.3926 | 1246474.7046
29 | 2682288.1742 | 1246330.3881 | 2682285.0274 | 1246334.4808 | 2682282.1114 | 1246337.1868 | 2682273.6183 | 1246341.6389 | 2682271.2351 | 1246342.9735 | 2682269.6775 | 1246345.7873 | 2682269.9765 | 1246349.8277 | 2682271.7516 | 1246355.2896 | 2682272.362 | 1246359.2121 | 2682271.7686 | 1246361.6834 | 2682269.1357 | 1246364.6824 | 2682264.129 | 1246365.6137 | 2682260.8528 | 1246364.334 | 2682258.8209 | 1246361.0367 | 2682254.4501 | 1246363.5113
30 | 2682288.1742 | 1246330.3881 | 2682282.2776 | 1246328.4827 | 2682278.912 | 1246326.568 | 2682277.0543 | 1246324.8743 | 2682273.4954 | 1246318.9206

## bus_geodata
| x | y | coords
0 | 2682200.6616 | 1246300.7244
1 | 2682208.6014 | 1246313.7679
2 | 2682190.1011 | 1246285.8625
3 | 2682212.0779 | 1246319.6918
4 | 2682183.5268 | 1246285.9715
5 | 2682216.7689 | 1246327.6889
6 | 2682219.0749 | 1246315.2522
7 | 2682169.0743 | 1246319.7404
8 | 2682167.6417 | 1246341.8354
9 | 2682146.4885 | 1246318.3933
10 | 2682224.1512 | 1246312.0313
11 | 2682123.0868 | 1246319.7703
12 | 2682124.151 | 1246336.4849
13 | 2682175.4826 | 1246389.9138
14 | 2682160.0865 | 1246397.495
15 | 2682176.7766 | 1246371.3256
16 | 2682154.7456 | 1246485.2185
17 | 2682126.3043 | 1246405.0228
18 | 2682166.0787 | 1246365.9426
19 | 2682148.8486 | 1246396.8411
20 | 2682225.5246 | 1246342.6151
21 | 2682178.0155 | 1246353.5277
22 | 2682213.2 | 1246293.7106
23 | 2682215.9241 | 1246298.2678
24 | 2682238.7618 | 1246336.8558
25 | 2682382.9797 | 1246324.5331
26 | 2682315.3926 | 1246474.7046
27 | 2682382.7387 | 1246271.9055
28 | 2682254.4501 | 1246363.5113
29 | 2682288.1742 | 1246330.3881
30 | 2682273.4954 | 1246318.9206
31 | 2682234.4785 | 1246357.8793
32 | 2682175.4826 | 1246389.9138

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97964 | -0.391 | 0.025191 | 0.0063134
1 | 0.97881 | -0.40727 | 0.033573 | 0.0084143
2 | 0.98077 | -0.3688 | 0 | 0
3 | 0.97835 | -0.41616 | 0 | 0
4 | 0.98118 | -0.36084 | 0 | 0
5 | 0.9775 | -0.4329 | 0.032894 | 0.008244
6 | 0.97802 | -0.42266 | 0 | 0
7 | 0.98405 | -0.30504 | 0 | 0
8 | 0.98612 | -0.26502 | 0.018791 | 0.0047095
9 | 0.98194 | -0.34622 | 0.087658 | 0.021969
10 | 0.97778 | -0.42737 | 0.0083112 | 0.002083
11 | 0.98166 | -0.35184 | 0 | 0
12 | 0.98145 | -0.35585 | 0.013243 | 0.0033191
13 | 0.99579 | -0.079566 | 0 | 0
14 | 0.9921 | -0.14987 | 0 | 0
15 | 0.99789 | -0.039826 | 0.018622 | 0.0046671
16 | 0.99158 | -0.16007 | 0 | 0
17 | 0.99105 | -0.17035 | 0.0053431 | 0.0013391
18 | 0.98851 | -0.21885 | 0.016271 | 0.0040778
19 | 0.99187 | -0.15435 | 0.022468 | 0.005631
20 | 0.97644 | -0.45382 | 0.033203 | 0.0083214
21 | 1 | 0 | -0.39164 | -0.1003
22 | 0.97772 | -0.42866 | 0.0023094 | 0.00057879
23 | 0.97773 | -0.42843 | 0.001319 | 0.00033058
24 | 0.97695 | -0.44376 | 0.01475 | 0.0036967
25 | 0.97435 | -0.4949 | 0 | 0
26 | 0.9756 | -0.47025 | 0 | 0
27 | 0.97402 | -0.50141 | 0.0067351 | 0.001688
28 | 0.97648 | -0.45305 | 0 | 0
29 | 0.97592 | -0.46409 | 0 | 0
30 | 0.97574 | -0.46755 | 0.0096799 | 0.002426
31 | 0.9759 | -0.46451 | 0.032997 | 0.0082699
32 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.17621 | 0.044324 | -0.17607 | -0.044237 | 0.00013681 | 8.6983e-05 | 0.26771 | 0.26771 | 0.26771 | 0.97964 | -0.391 | 0.97881 | -0.40727 | 24.5155
1 | -0.2014 | -0.050637 | 0.20161 | 0.050773 | 0.00021382 | 0.00013615 | 0.30597 | 0.30597 | 0.30597 | 0.97964 | -0.391 | 0.98077 | -0.3688 | 28.0194
2 | 0.1425 | 0.035822 | -0.14244 | -0.035784 | 6.0461e-05 | 3.8522e-05 | 0.21667 | 0.21667 | 0.21667 | 0.97881 | -0.40727 | 0.97835 | -0.41616 | 29.7624
3 | -0.20161 | -0.050773 | 0.20169 | 0.050822 | 7.6721e-05 | 4.8853e-05 | 0.30597 | 0.30597 | 0.30597 | 0.98077 | -0.3688 | 0.98118 | -0.36084 | 28.0194
4 | 0.099256 | 0.024939 | -0.099177 | -0.024888 | 7.9259e-05 | 5.0609e-05 | 0.15099 | 0.15099 | 0.15099 | 0.97835 | -0.41616 | 0.9775 | -0.4329 | 41.4795
5 | 0.043182 | 0.010845 | -0.043168 | -0.010837 | 1.338e-05 | 8.4596e-06 | 0.065685 | 0.065685 | 0.065685 | 0.97835 | -0.41616 | 0.97802 | -0.42266 | 18.0453
6 | -0.20169 | -0.050822 | 0.20223 | 0.051166 | 0.00053995 | 0.00034382 | 0.30597 | 0.30597 | 0.30597 | 0.98118 | -0.36084 | 0.98405 | -0.30504 | 28.0194
7 | 0.066283 | 0.016644 | -0.066217 | -0.016602 | 6.6082e-05 | 4.2076e-05 | 0.10091 | 0.10091 | 0.10091 | 0.9775 | -0.4329 | 0.97644 | -0.45382 | 27.7231
8 | 0.043168 | 0.010837 | -0.043159 | -0.010831 | 9.7076e-06 | 6.1376e-06 | 0.065685 | 0.065685 | 0.065685 | 0.97802 | -0.42266 | 0.97778 | -0.42737 | 18.0453
9 | -0.30334 | -0.076584 | 0.30392 | 0.076956 | 0.0005828 | 0.00037215 | 0.45888 | 0.45888 | 0.45888 | 0.98405 | -0.30504 | 0.98612 | -0.26502 | 42.0224
10 | 0.10111 | 0.025418 | -0.10091 | -0.025292 | 0.00019839 | 0.00012669 | 0.15291 | 0.15291 | 0.15291 | 0.98405 | -0.30504 | 0.98194 | -0.34622 | 42.0092
11 | -0.32271 | -0.081666 | 0.32343 | 0.082124 | 0.00071689 | 0.00045788 | 0.48724 | 0.48724 | 0.48724 | 0.98612 | -0.26502 | 0.98851 | -0.21885 | 44.619
12 | 0.013249 | 0.0033225 | -0.013246 | -0.0033205 | 3.544e-06 | 1.9717e-06 | 0.020078 | 0.020079 | 0.020079 | 0.98194 | -0.34622 | 0.98166 | -0.35184 | 5.5161
13 | 0.031219 | 0.0078385 | -0.031194 | -0.0078232 | 2.4387e-05 | 1.5247e-05 | 0.047515 | 0.047515 | 0.047515 | 0.97778 | -0.42737 | 0.97695 | -0.44376 | 13.0535
14 | 0.0036286 | 0.00090923 | -0.0036284 | -0.00090931 | 1.8336e-07 | -8.3762e-08 | 0.0055221 | 0.0055221 | 0.0055221 | 0.97778 | -0.42737 | 0.97773 | -0.42843 | 1.5171
15 | 0.013246 | 0.0033205 | -0.013243 | -0.0033191 | 2.5321e-06 | 1.4088e-06 | 0.020079 | 0.020079 | 0.020079 | 0.98166 | -0.35184 | 0.98145 | -0.35585 | 5.5161
16 | 0.3699 | 0.094699 | -0.36865 | -0.093898 | 0.0012549 | 0.00080187 | 0.55346 | 0.55346 | 0.55346 | 0.99579 | -0.079566 | 0.9921 | -0.14987 | 50.683
17 | -0.3699 | -0.094699 | 0.37062 | 0.095155 | 0.00071346 | 0.00045588 | 0.55346 | 0.55346 | 0.55346 | 0.99579 | -0.079566 | 0.99789 | -0.039826 | 50.683
18 | 0.34083 | 0.086924 | -0.3397 | -0.086201 | 0.001131 | 0.00072252 | 0.51173 | 0.51173 | 0.51173 | 0.9921 | -0.14987 | 0.98851 | -0.21885 | 46.8618
19 | 0.022473 | 0.005634 | -0.022468 | -0.005631 | 4.7961e-06 | 2.9242e-06 | 0.033707 | 0.033707 | 0.033707 | 0.9921 | -0.14987 | 0.99187 | -0.15435 | 9.2601
20 | 0.0053483 | 0.0013397 | -0.0053457 | -0.0013394 | 2.5967e-06 | 2.7304e-07 | 0.0080214 | 0.0080219 | 0.0080219 | 0.9921 | -0.14987 | 0.99158 | -0.16007 | 2.2038
21 | -0.38924 | -0.099822 | 0.38999 | 0.1003 | 0.00075339 | 0.00048147 | 0.58123 | 0.58123 | 0.58123 | 0.99789 | -0.039826 | 1 | 0 | 53.2258
22 | 0.0053457 | 0.0013394 | -0.0053431 | -0.0013391 | 2.6176e-06 | 2.7691e-07 | 0.0080219 | 0.0080224 | 0.0080224 | 0.99158 | -0.16007 | 0.99105 | -0.17035 | 2.204
23 | 0.033014 | 0.0082805 | -0.032997 | -0.0082699 | 1.6799e-05 | 1.053e-05 | 0.050313 | 0.050314 | 0.050314 | 0.97644 | -0.45382 | 0.9759 | -0.46451 | 13.8224
24 | -0.0023094 | -0.00057879 | 0.0023094 | 0.00057874 | 2.4595e-08 | -5.0845e-08 | 0.0035147 | 0.0035147 | 0.0035147 | 0.97772 | -0.42866 | 0.97773 | -0.42843 | 0.96558
25 | 0.016445 | 0.0041266 | -0.016437 | -0.0041223 | 7.2775e-06 | 4.2705e-06 | 0.025049 | 0.025049 | 0.025049 | 0.97695 | -0.44376 | 0.97648 | -0.45305 | 6.8816
26 | -0.0067372 | -0.0016886 | 0.0067451 | 0.0016912 | 7.9163e-06 | 2.5793e-06 | 0.010289 | 0.010288 | 0.010289 | 0.97435 | -0.4949 | 0.9756 | -0.47025 | 2.8266
27 | 0.0067372 | 0.0016886 | -0.0067351 | -0.001688 | 2.0893e-06 | 6.8189e-07 | 0.010289 | 0.010289 | 0.010289 | 0.97435 | -0.4949 | 0.97402 | -0.50141 | 2.8267
28 | -0.0067451 | -0.0016912 | 0.0067506 | 0.001693 | 5.533e-06 | 1.7988e-06 | 0.010288 | 0.010287 | 0.010288 | 0.9756 | -0.47025 | 0.97648 | -0.45305 | 2.8264
29 | 0.0096866 | 0.0024293 | -0.0096815 | -0.0024268 | 5.0989e-06 | 2.4832e-06 | 0.014762 | 0.014762 | 0.014762 | 0.97648 | -0.45305 | 0.97592 | -0.46409 | 4.0555
30 | 0.0096815 | 0.0024268 | -0.0096799 | -0.002426 | 1.5922e-06 | 7.756e-07 | 0.014762 | 0.014762 | 0.014762 | 0.97592 | -0.46409 | 0.97574 | -0.46755 | 4.0555

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.41304 | 0.10567

## res_load
| p_mw | q_mvar
0 | 0.025191 | 0.0063134
1 | 0.033573 | 0.0084143
2 | 0.032894 | 0.008244
3 | 0.018791 | 0.0047095
4 | 0.087658 | 0.021969
5 | 0.0083112 | 0.002083
6 | 0.013243 | 0.0033191
7 | 0.018622 | 0.0046671
8 | 0.0053431 | 0.0013391
9 | 0.016271 | 0.0040778
10 | 0.022468 | 0.005631
11 | 0.033203 | 0.0083214
12 | 0.021398 | 0.0053628
13 | 0.0023094 | 0.00057879
14 | 0.001319 | 0.00033058
15 | 0.01475 | 0.0036967
16 | 0.0067351 | 0.001688
17 | 0.0096799 | 0.002426
18 | 0.032997 | 0.0082699

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1