## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-209_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-209_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-209_0_5_node_9 | 0.4 | n |  | TRUE
3 | bus_LV_261-209_0_5_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_261-209_0_5_node_16 | 0.4 | n |  | TRUE
5 | bus_LV_261-209_0_5_node_24 | 0.4 | n |  | TRUE
6 | bus_LV_261-209_0_5_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_261-209_0_5_node_21 | 0.4 | n |  | TRUE
8 | bus_LV_261-209_0_5_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_261-209_0_5_node_19 | 0.4 | n |  | TRUE
10 | bus_LV_261-209_0_5_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_261-209_0_5_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_261-209_0_5_node_17 | 0.4 | n |  | TRUE
13 | bus_LV_261-209_0_5_node_30 | 0.4 | n |  | TRUE
14 | bus_LV_261-209_0_5_node_29 | 0.4 | n |  | TRUE
15 | bus_LV_261-209_0_5_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_261-209_0_5_node_26 | 0.4 | n |  | TRUE
17 | bus_LV_261-209_0_5_node_25 | 0.4 | n |  | TRUE
18 | bus_LV_261-209_0_5_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_261-209_0_5_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_261-209_0_5_node_27 | 0.4 | n |  | TRUE
21 | bus_LV_261-209_0_5_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_261-209_0_5_node_28 | 0.4 | n |  | TRUE
23 | bus_LV_261-209_0_5_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_261-209_0_5_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_261-209_0_5_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_261-209_0_5_node_23 | 0.4 | n |  | TRUE
27 | bus_MV_531_0_node_42 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-209_0_5_load_0 | 0 | 0.098124 | 0.024592 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-209_0_5_load_24 | 5 | 0.032832 | 0.0082285 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-209_0_5_load_21 | 7 | 0.018426 | 0.0046181 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-209_0_5_load_19 | 9 | 0.019647 | 0.004924 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-209_0_5_load_30 | 13 | 0.095778 | 0.024004 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-209_0_5_load_29 | 14 | 0.093519 | 0.023438 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-209_0_5_load_26 | 16 | 0.035382 | 0.0088675 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-209_0_5_load_25 | 17 | 0.016784 | 0.0042065 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-209_0_5_load_27 | 20 | 0.019414 | 0.0048655 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-209_0_5_load_28 | 22 | 0.040967 | 0.010267 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-209_0_5_load_22 | 23 | 0.010728 | 0.0026886 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-209_0_5_load_20 | 24 | 0.039672 | 0.0099427 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-209_0_5_load_18 | 25 | 0.043187 | 0.010824 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-209_0_5_load_23 | 26 | 0.010385 | 0.0026028 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 2 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-209_0_5_line_0 |  | 0 | 1 | 0.045094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-209_0_5_line_1 |  | 1 | 2 | 0.11435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-209_0_5_line_2 |  | 2 | 14 | 0.05124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-209_0_5_line_3 |  | 2 | 6 | 0.11085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_261-209_0_5_line_4 |  | 3 | 4 | 0.025571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-209_0_5_line_5 |  | 3 | 5 | 0.011442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-209_0_5_line_6 |  | 4 | 24 | 0.012017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-209_0_5_line_7 |  | 4 | 11 | 0.003231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-209_0_5_line_8 |  | 6 | 7 | 0.02119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_261-209_0_5_line_9 |  | 6 | 8 | 0.16615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-209_0_5_line_10 |  | 6 | 9 | 0.0096012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-209_0_5_line_11 |  | 7 | 17 | 0.013176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-209_0_5_line_12 |  | 8 | 13 | 0.015206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-209_0_5_line_13 |  | 9 | 24 | 0.022047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-209_0_5_line_14 |  | 10 | 11 | 0.014669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-209_0_5_line_15 |  | 10 | 12 | 0.01359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-209_0_5_line_16 |  | 12 | 25 | 0.012003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-209_0_5_line_17 |  | 15 | 16 | 0.014588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-209_0_5_line_18 |  | 15 | 17 | 0.023692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-209_0_5_line_19 |  | 16 | 20 | 0.019834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-209_0_5_line_20 |  | 18 | 19 | 0.002097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-209_0_5_line_21 |  | 18 | 20 | 0.0076729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-209_0_5_line_22 |  | 19 | 23 | 0.019203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-209_0_5_line_23 |  | 19 | 21 | 0.014649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-209_0_5_line_24 |  | 21 | 22 | 0.024517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-209_0_5_line_25 |  | 23 | 26 | 0.0090012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-209_0_5_trafo_9 | 0.63 MVA 20/0.4 kV | 27 | 2 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17
0 | 2682749.7436 | 1247697.179 | 2682725.2245 | 1247659.333
1 | 2682749.7436 | 1247697.179 | 2682752.4624 | 1247695.5824 | 2682754.2598 | 1247694.5178 | 2682757.5347 | 1247692.5843 | 2682758.8295 | 1247691.8129 | 2682762.6751 | 1247689.5761 | 2682758.371 | 1247683 | 2682765.1165 | 1247679.1803 | 2682786.1508 | 1247666.8537 | 2682782.5803 | 1247659.1315 | 2682779.5654 | 1247654.3414 | 2682794.7647 | 1247645.0023 | 2682801.0424 | 1247650.8831 | 2682804.5793 | 1247648.5864 | 2682801.4868 | 1247644.4846 | 2682803.2353 | 1247643.1414 | 2682806.7768 | 1247647.5385 | 2682808.1096 | 1247646.7566
2 | 2682808.1096 | 1247646.7566 | 2682820.2222 | 1247666.418 | 2682827.2934 | 1247693.6626
3 | 2682808.1096 | 1247646.7566 | 2682806.7768 | 1247647.5385 | 2682803.2353 | 1247643.1414 | 2682801.4868 | 1247644.4846 | 2682804.5793 | 1247648.5864 | 2682818.9937 | 1247639.203 | 2682820.7972 | 1247638.2497 | 2682837.945 | 1247626.7696 | 2682840.8339 | 1247624.8975 | 2682846.1478 | 1247621.3803 | 2682826.2615 | 1247590.4575 | 2682829.952 | 1247587.9739 | 2682826.9407 | 1247583.473
4 | 2682853.2301 | 1247576.1904 | 2682851.455 | 1247573.4969 | 2682866.0724 | 1247563.6606 | 2682863.5449 | 1247559.6668
5 | 2682853.2301 | 1247576.1904 | 2682853.6887 | 1247576.8862 | 2682859.5176 | 1247585.75
6 | 2682863.5449 | 1247559.6668 | 2682853.4711 | 1247566.2185
7 | 2682861.8233 | 1247556.9296 | 2682863.5449 | 1247559.6668
8 | 2682826.9407 | 1247583.473 | 2682815.6205 | 1247565.5596
9 | 2682826.9407 | 1247583.473 | 2682829.952 | 1247587.9739 | 2682826.2615 | 1247590.4575 | 2682846.1478 | 1247621.3803 | 2682859.4862 | 1247642.5044 | 2682865.1487 | 1247651.3233 | 2682908.3373 | 1247718.3541 | 2682904.6354 | 1247720.5706
10 | 2682826.9407 | 1247583.473 | 2682834.9895 | 1247578.2383
11 | 2682815.6205 | 1247565.5596 | 2682808.5817 | 1247554.4211
12 | 2682891.5793 | 1247728.4272 | 2682898.9149 | 1247724.0043 | 2682904.6354 | 1247720.5706
13 | 2682834.9895 | 1247578.2383 | 2682853.4711 | 1247566.2185
14 | 2682861.8233 | 1247556.9296 | 2682863.4834 | 1247555.9632 | 2682867.0326 | 1247553.8668 | 2682874.5176 | 1247549.5794
15 | 2682885.932 | 1247553.8198 | 2682882.8973 | 1247554.767 | 2682878.4304 | 1247553.8928 | 2682877.826 | 1247553.3617 | 2682875.6694 | 1247551.4746 | 2682874.5176 | 1247549.5794
16 | 2682885.932 | 1247553.8198 | 2682888.5294 | 1247551.1875 | 2682890.2998 | 1247548.2768 | 2682892.2005 | 1247543.762
17 | 2682795.9249 | 1247534.3927 | 2682808.2914 | 1247526.6545
18 | 2682795.9249 | 1247534.3927 | 2682808.5817 | 1247554.4211
19 | 2682825.1053 | 1247516.1335 | 2682808.2914 | 1247526.6545
20 | 2682833.6902 | 1247512.3705 | 2682831.6098 | 1247512.0634
21 | 2682831.6098 | 1247512.0634 | 2682825.1053 | 1247516.1335
22 | 2682833.6902 | 1247512.3705 | 2682843.942 | 1247528.6081
23 | 2682833.6902 | 1247512.3705 | 2682835.0192 | 1247511.3216 | 2682835.3477 | 1247511.0593 | 2682836.4627 | 1247510.1854 | 2682838.5173 | 1247508.5573 | 2682840.5948 | 1247506.9185 | 2682842.191 | 1247505.6621 | 2682843.7033 | 1247504.4712 | 2682844.9991 | 1247503.0883
24 | 2682844.9991 | 1247503.0883 | 2682847.5046 | 1247507.0373 | 2682851.0077 | 1247512.557 | 2682854.7031 | 1247518.3796 | 2682858.1324 | 1247523.7759 | 2682858.1395 | 1247523.787
25 | 2682848.7474 | 1247536.2192 | 2682843.942 | 1247528.6081

## bus_geodata
| x | y | coords
0 | 2682725.2245 | 1247659.333
1 | 2682749.7436 | 1247697.179
2 | 2682808.1096 | 1247646.7566
3 | 2682853.2301 | 1247576.1904
4 | 2682863.5449 | 1247559.6668
5 | 2682859.5176 | 1247585.75
6 | 2682826.9407 | 1247583.473
7 | 2682815.6205 | 1247565.5596
8 | 2682904.6354 | 1247720.5706
9 | 2682834.9895 | 1247578.2383
10 | 2682874.5176 | 1247549.5794
11 | 2682861.8233 | 1247556.9296
12 | 2682885.932 | 1247553.8198
13 | 2682891.5793 | 1247728.4272
14 | 2682827.2934 | 1247693.6626
15 | 2682795.9249 | 1247534.3927
16 | 2682808.2914 | 1247526.6545
17 | 2682808.5817 | 1247554.4211
18 | 2682831.6098 | 1247512.0634
19 | 2682833.6902 | 1247512.3705
20 | 2682825.1053 | 1247516.1335
21 | 2682844.9991 | 1247503.0883
22 | 2682858.1395 | 1247523.787
23 | 2682843.942 | 1247528.6081
24 | 2682853.4711 | 1247566.2185
25 | 2682892.2005 | 1247543.762
26 | 2682848.7474 | 1247536.2192
27 | 2682804.5793 | 1247648.5864

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9856 | -0.27668 | 0.098124 | 0.024592
1 | 0.98967 | -0.19762 | 0 | 0
2 | 1 | 0 | -0.58601 | -0.15015
3 | 0.98168 | -0.3509 | 0 | 0
4 | 0.98245 | -0.33573 | 0 | 0
5 | 0.98133 | -0.3577 | 0.032832 | 0.0082285
6 | 0.98685 | -0.25009 | 0 | 0
7 | 0.98536 | -0.27898 | 0.018426 | 0.0046181
8 | 0.97198 | -0.53926 | 0 | 0
9 | 0.98565 | -0.27338 | 0.019647 | 0.004924
10 | 0.98174 | -0.3497 | 0 | 0
11 | 0.98233 | -0.33825 | 0 | 0
12 | 0.9812 | -0.36032 | 0 | 0
13 | 0.97062 | -0.56617 | 0.095778 | 0.024004
14 | 0.99564 | -0.083887 | 0.093519 | 0.023438
15 | 0.98116 | -0.36065 | 0 | 0
16 | 0.97958 | -0.39157 | 0.035382 | 0.0088675
17 | 0.98373 | -0.31065 | 0.016784 | 0.0042065
18 | 0.97764 | -0.42966 | 0 | 0
19 | 0.97751 | -0.43203 | 0 | 0
20 | 0.97808 | -0.42097 | 0.019414 | 0.0048655
21 | 0.97696 | -0.44299 | 0 | 0
22 | 0.97602 | -0.46134 | 0.040967 | 0.010267
23 | 0.97714 | -0.43943 | 0.010728 | 0.0026886
24 | 0.9833 | -0.31925 | 0.039672 | 0.0099427
25 | 0.98072 | -0.36971 | 0.043187 | 0.010824
26 | 0.97705 | -0.44114 | 0.010385 | 0.0026028
27 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.098124 | -0.024592 | 0.098495 | 0.024829 | 0.00037113 | 0.00023694 | 0.14814 | 0.14814 | 0.14814 | 0.9856 | -0.27668 | 0.98967 | -0.19762 | 40.699
1 | -0.098495 | -0.024829 | 0.099437 | 0.02543 | 0.00094111 | 0.00060082 | 0.14814 | 0.14814 | 0.14814 | 0.98967 | -0.19762 | 1 | 0 | 40.6989
2 | 0.093894 | 0.023678 | -0.093519 | -0.023438 | 0.00037536 | 0.00023956 | 0.13977 | 0.13977 | 0.13977 | 1 | 0 | 0.99564 | -0.083887 | 38.3976
3 | 0.39103 | 0.10104 | -0.38632 | -0.09803 | 0.0047087 | 0.0030093 | 0.58294 | 0.58294 | 0.58294 | 1 | 0 | 0.98685 | -0.25009 | 53.3829
4 | -0.032843 | -0.0082351 | 0.032866 | 0.00825 | 2.3766e-05 | 1.4887e-05 | 0.049784 | 0.049784 | 0.049784 | 0.98168 | -0.3509 | 0.98245 | -0.33573 | 13.6769
5 | 0.032843 | 0.0082351 | -0.032832 | -0.0082285 | 1.0634e-05 | 6.6614e-06 | 0.049784 | 0.049784 | 0.049784 | 0.98168 | -0.3509 | 0.98133 | -0.3577 | 13.6769
6 | -0.076123 | -0.019118 | 0.076183 | 0.019156 | 5.9918e-05 | 3.8195e-05 | 0.11531 | 0.11531 | 0.11531 | 0.98245 | -0.33573 | 0.9833 | -0.31925 | 31.6785
7 | 0.043257 | 0.010868 | -0.043252 | -0.010865 | 5.2023e-06 | 3.2886e-06 | 0.065526 | 0.065526 | 0.065526 | 0.98245 | -0.33573 | 0.98233 | -0.33825 | 18.0017
8 | 0.15317 | 0.038807 | -0.15296 | -0.038672 | 0.00021221 | 0.00013527 | 0.2311 | 0.2311 | 0.2311 | 0.98685 | -0.25009 | 0.98536 | -0.27898 | 31.745
9 | 0.097244 | 0.02494 | -0.095901 | -0.024083 | 0.0013433 | 0.00085762 | 0.14683 | 0.14683 | 0.14683 | 0.98685 | -0.25009 | 0.97198 | -0.53926 | 40.339
10 | 0.13591 | 0.034282 | -0.13576 | -0.034185 | 0.00015132 | 9.672e-05 | 0.205 | 0.205 | 0.205 | 0.98685 | -0.25009 | 0.98565 | -0.27338 | 56.3201
11 | 0.13453 | 0.034054 | -0.13433 | -0.033923 | 0.00020417 | 0.0001305 | 0.20328 | 0.20328 | 0.20328 | 0.98536 | -0.27898 | 0.98373 | -0.31065 | 55.8456
12 | 0.095901 | 0.024083 | -0.095778 | -0.024004 | 0.00012294 | 7.8494e-05 | 0.14683 | 0.14683 | 0.14683 | 0.97198 | -0.53926 | 0.97062 | -0.56617 | 40.339
13 | 0.11611 | 0.029261 | -0.11585 | -0.029099 | 0.00025419 | 0.0001624 | 0.17534 | 0.17534 | 0.17534 | 0.98565 | -0.27338 | 0.9833 | -0.31925 | 48.1716
14 | -0.043228 | -0.01085 | 0.043252 | 0.010865 | 2.3619e-05 | 1.4931e-05 | 0.065526 | 0.065526 | 0.065526 | 0.98174 | -0.3497 | 0.98233 | -0.33825 | 18.0017
15 | 0.043228 | 0.01085 | -0.043206 | -0.010836 | 2.1882e-05 | 1.3832e-05 | 0.065526 | 0.065526 | 0.065526 | 0.98174 | -0.3497 | 0.9812 | -0.36032 | 18.0017
16 | 0.043206 | 0.010836 | -0.043187 | -0.010824 | 1.9327e-05 | 1.2218e-05 | 0.065526 | 0.065526 | 0.065526 | 0.9812 | -0.36032 | 0.98072 | -0.36971 | 18.0017
17 | 0.11726 | 0.029537 | -0.11709 | -0.029427 | 0.00017311 | 0.00011061 | 0.17789 | 0.17789 | 0.17789 | 0.98116 | -0.36065 | 0.97958 | -0.39157 | 48.8709
18 | -0.11726 | -0.029537 | 0.11754 | 0.029717 | 0.00028115 | 0.00017964 | 0.17789 | 0.17789 | 0.17789 | 0.98116 | -0.36065 | 0.98373 | -0.31065 | 48.8709
19 | 0.081706 | 0.020559 | -0.081591 | -0.020486 | 0.00011463 | 7.3114e-05 | 0.12414 | 0.12414 | 0.12414 | 0.97958 | -0.39157 | 0.97808 | -0.42097 | 34.1055
20 | 0.062152 | 0.015604 | -0.062145 | -0.0156 | 7.0387e-06 | 4.4785e-06 | 0.094609 | 0.094609 | 0.094609 | 0.97764 | -0.42966 | 0.97751 | -0.43203 | 25.9914
21 | -0.062152 | -0.015604 | 0.062178 | 0.015621 | 2.5755e-05 | 1.6387e-05 | 0.094609 | 0.094609 | 0.094609 | 0.97764 | -0.42966 | 0.97808 | -0.42097 | 25.9914
22 | 0.021121 | 0.0052963 | -0.021114 | -0.0052918 | 7.4444e-06 | 4.5238e-06 | 0.032152 | 0.032153 | 0.032153 | 0.97751 | -0.43203 | 0.97714 | -0.43943 | 8.8331
23 | 0.041024 | 0.010303 | -0.041002 | -0.01029 | 2.1428e-05 | 1.3531e-05 | 0.062456 | 0.062456 | 0.062456 | 0.97751 | -0.43203 | 0.97696 | -0.44299 | 17.1583
24 | 0.041002 | 0.01029 | -0.040967 | -0.010267 | 3.5864e-05 | 2.2646e-05 | 0.062456 | 0.062456 | 0.062456 | 0.97696 | -0.44299 | 0.97602 | -0.46134 | 17.1583
25 | 0.010386 | 0.0026032 | -0.010385 | -0.0026028 | 8.4437e-07 | 4.2766e-07 | 0.015816 | 0.015816 | 0.015816 | 0.97714 | -0.43943 | 0.97705 | -0.44114 | 4.3451

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.58601 | 0.15015

## res_load
| p_mw | q_mvar
0 | 0.098124 | 0.024592
1 | 0.032832 | 0.0082285
2 | 0.018426 | 0.0046181
3 | 0.019647 | 0.004924
4 | 0.095778 | 0.024004
5 | 0.093519 | 0.023438
6 | 0.035382 | 0.0088675
7 | 0.016784 | 0.0042065
8 | 0.019414 | 0.0048655
9 | 0.040967 | 0.010267
10 | 0.010728 | 0.0026886
11 | 0.039672 | 0.0099427
12 | 0.043187 | 0.010824
13 | 0.010385 | 0.0026028

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1