## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-21_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-21_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-21_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-21_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-21_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-21_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-21_0_3_node_25 | 0.4 | n |  | TRUE
7 | bus_LV_261-21_0_3_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_261-21_0_3_node_29 | 0.4 | n |  | TRUE
9 | bus_LV_261-21_0_3_node_10 | 0.4 | n |  | TRUE
10 | bus_LV_261-21_0_3_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_261-21_0_3_node_23 | 0.4 | n |  | TRUE
12 | bus_LV_261-21_0_3_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_261-21_0_3_node_22 | 0.4 | n |  | TRUE
14 | bus_LV_261-21_0_3_node_13 | 0.4 | n |  | TRUE
15 | bus_LV_261-21_0_3_node_18 | 0.4 | n |  | TRUE
16 | bus_LV_261-21_0_3_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_261-21_0_3_node_21 | 0.4 | n |  | TRUE
18 | bus_LV_261-21_0_3_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_261-21_0_3_node_35 | 0.4 | n |  | TRUE
20 | bus_LV_261-21_0_3_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_261-21_0_3_node_31 | 0.4 | n |  | TRUE
22 | bus_LV_261-21_0_3_node_32 | 0.4 | n |  | TRUE
23 | bus_LV_261-21_0_3_node_28 | 0.4 | n |  | TRUE
24 | bus_LV_261-21_0_3_node_27 | 0.4 | n |  | TRUE
25 | bus_LV_261-21_0_3_node_30 | 0.4 | n |  | TRUE
26 | bus_LV_261-21_0_3_node_33 | 0.4 | n |  | TRUE
27 | bus_LV_261-21_0_3_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_261-21_0_3_node_34 | 0.4 | n |  | TRUE
29 | bus_LV_261-21_0_3_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_261-21_0_3_node_24 | 0.4 | n |  | TRUE
31 | bus_MV_535_0_node_43 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-21_0_3_load_0 | 0 | 0.041255 | 0.01034 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-21_0_3_load_1 | 1 | 0.0038272 | 0.00095918 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-21_0_3_load_3 | 3 | 0.002041 | 0.00051153 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-21_0_3_load_4 | 4 | 0.012732 | 0.0031909 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-21_0_3_load_5 | 5 | 0.005311 | 0.0013311 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-21_0_3_load_25 | 6 | 0.0059507 | 0.0014914 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-21_0_3_load_29 | 8 | 0.0068175 | 0.0017086 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-21_0_3_load_23 | 11 | 0.010615 | 0.0026603 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-21_0_3_load_6 | 12 | 0.036163 | 0.0090634 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-21_0_3_load_22 | 13 | 0.019656 | 0.0049264 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-21_0_3_load_21 | 17 | 0.012113 | 0.0030358 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-21_0_3_load_35 | 19 | 0.011344 | 0.0028432 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-21_0_3_load_31 | 21 | 0.0083713 | 0.0020981 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-21_0_3_load_32 | 22 | 0.014003 | 0.0035096 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-21_0_3_load_28 | 23 | 0.015391 | 0.0038573 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-21_0_3_load_27 | 24 | 0.019059 | 0.0047766 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-21_0_3_load_30 | 25 | 0.012212 | 0.0030605 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-21_0_3_load_33 | 26 | 0.011537 | 0.0028915 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-21_0_3_load_20 | 27 | 0.039032 | 0.0097824 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-21_0_3_load_34 | 28 | 0.014206 | 0.0035605 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-21_0_3_load_26 | 29 | 0.031221 | 0.0078247 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-21_0_3_load_24 | 30 | 0.0131 | 0.0032832 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 26 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-21_0_3_line_0 |  | 0 | 1 | 0.0096477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-21_0_3_line_1 |  | 0 | 2 | 0.0082131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-21_0_3_line_2 |  | 1 | 3 | 0.015178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-21_0_3_line_3 |  | 2 | 4 | 0.02446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-21_0_3_line_4 |  | 2 | 5 | 0.014267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-21_0_3_line_5 |  | 5 | 6 | 0.00070677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-21_0_3_line_6 |  | 6 | 11 | 0.016245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-21_0_3_line_7 |  | 7 | 8 | 0.013679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-21_0_3_line_8 |  | 7 | 9 | 0.02269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-21_0_3_line_9 |  | 7 | 10 | 0.006644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-21_0_3_line_10 |  | 8 | 26 | 0.01195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-21_0_3_line_11 |  | 9 | 13 | 0.0079584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-21_0_3_line_12 |  | 10 | 12 | 0.028668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-21_0_3_line_13 |  | 11 | 30 | 0.0035705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-21_0_3_line_14 |  | 14 | 15 | 0.010229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-21_0_3_line_15 |  | 14 | 16 | 0.017955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-21_0_3_line_16 |  | 14 | 17 | 0.0032642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-21_0_3_line_17 |  | 15 | 25 | 0.0090862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-21_0_3_line_18 |  | 16 | 18 | 0.004223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_261-21_0_3_line_19 |  | 16 | 19 | 0.017152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_261-21_0_3_line_20 |  | 17 | 27 | 0.026576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-21_0_3_line_21 |  | 18 | 24 | 0.007328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_261-21_0_3_line_22 |  | 19 | 28 | 0.01135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_261-21_0_3_line_23 |  | 20 | 21 | 0.010756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-21_0_3_line_24 |  | 20 | 22 | 0.020823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-21_0_3_line_25 |  | 20 | 23 | 0.021942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_261-21_0_3_line_26 |  | 21 | 29 | 0.0038882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-21_0_3_line_27 |  | 23 | 24 | 0.014039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_261-21_0_3_line_28 |  | 26 | 28 | 0.011338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_261-21_0_3_line_29 |  | 29 | 30 | 0.017472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-21_0_3_trafo_33 | 0.63 MVA 20/0.4 kV | 31 | 26 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2682063.9743 | 1247957.0186 | 2682068.8972 | 1247965.3158
1 | 2682059.7834 | 1247949.9552 | 2682063.9743 | 1247957.0186
2 | 2682068.8972 | 1247965.3158 | 2682076.6421 | 1247978.3693
3 | 2682059.7834 | 1247949.9552 | 2682047.9035 | 1247928.5738
4 | 2682059.7834 | 1247949.9552 | 2682071.4107 | 1247941.6869
5 | 2682071.9867 | 1247941.2773 | 2682071.4107 | 1247941.6869
6 | 2682071.9867 | 1247941.2773 | 2682085.2252 | 1247931.8632
7 | 2682030.9772 | 1247898.0852 | 2682043.4767 | 1247892.5293
8 | 2682030.9772 | 1247898.0852 | 2682027.358 | 1247891.0856 | 2682023.0653 | 1247882.5422 | 2682027.8754 | 1247880.4405
9 | 2682030.9772 | 1247898.0852 | 2682025.0367 | 1247901.0942
10 | 2682043.4767 | 1247892.5293 | 2682054.3966 | 1247887.6755
11 | 2682027.8754 | 1247880.4405 | 2682024.4318 | 1247873.2657
12 | 2682025.0367 | 1247901.0942 | 2681999.3741 | 1247913.8726
13 | 2682088.1351 | 1247929.7939 | 2682085.2252 | 1247931.8632
14 | 2682083.2326 | 1247845.9922 | 2682085.2789 | 1247850.3905 | 2682085.3578 | 1247852.3263 | 2682083.3777 | 1247855.1454
15 | 2682083.3777 | 1247855.1454 | 2682086.8373 | 1247862.7545 | 2682090.8024 | 1247871.4935
16 | 2682083.3777 | 1247855.1454 | 2682080.4984 | 1247856.6833
17 | 2682083.2326 | 1247845.9922 | 2682079.4611 | 1247837.7257
18 | 2682090.8024 | 1247871.4935 | 2682092.8444 | 1247871.8443 | 2682094.842 | 1247872.6726
19 | 2682090.8024 | 1247871.4935 | 2682075.1288 | 1247878.4603
20 | 2682056.3845 | 1247867.8258 | 2682075.3423 | 1247859.4374 | 2682080.4984 | 1247856.6833
21 | 2682094.842 | 1247872.6726 | 2682095.5765 | 1247873.6279 | 2682096.2121 | 1247874.6374 | 2682098.2474 | 1247879.1277
22 | 2682075.1288 | 1247878.4603 | 2682064.7571 | 1247883.0704
23 | 2682114.3087 | 1247911.1815 | 2682105.5429 | 1247917.415
24 | 2682114.3087 | 1247911.1815 | 2682116.9566 | 1247914.6874 | 2682123.914 | 1247929.5715
25 | 2682114.3087 | 1247911.1815 | 2682110.4742 | 1247906.1024 | 2682104.0431 | 1247891.9141
26 | 2682105.5429 | 1247917.415 | 2682102.3742 | 1247919.6683
27 | 2682104.0431 | 1247891.9141 | 2682098.2474 | 1247879.1277
28 | 2682054.3966 | 1247887.6755 | 2682064.7571 | 1247883.0704
29 | 2682088.1351 | 1247929.7939 | 2682102.3742 | 1247919.6683

## bus_geodata
| x | y | coords
0 | 2682063.9743 | 1247957.0186
1 | 2682068.8972 | 1247965.3158
2 | 2682059.7834 | 1247949.9552
3 | 2682076.6421 | 1247978.3693
4 | 2682047.9035 | 1247928.5738
5 | 2682071.4107 | 1247941.6869
6 | 2682071.9867 | 1247941.2773
7 | 2682030.9772 | 1247898.0852
8 | 2682043.4767 | 1247892.5293
9 | 2682027.8754 | 1247880.4405
10 | 2682025.0367 | 1247901.0942
11 | 2682085.2252 | 1247931.8632
12 | 2681999.3741 | 1247913.8726
13 | 2682024.4318 | 1247873.2657
14 | 2682083.3777 | 1247855.1454
15 | 2682083.2326 | 1247845.9922
16 | 2682090.8024 | 1247871.4935
17 | 2682080.4984 | 1247856.6833
18 | 2682094.842 | 1247872.6725
19 | 2682075.1288 | 1247878.4603
20 | 2682114.3087 | 1247911.1815
21 | 2682105.5429 | 1247917.415
22 | 2682123.914 | 1247929.5715
23 | 2682104.0431 | 1247891.9141
24 | 2682098.2474 | 1247879.1277
25 | 2682079.4611 | 1247837.7257
26 | 2682054.3966 | 1247887.6755
27 | 2682056.3845 | 1247867.8258
28 | 2682064.7571 | 1247883.0704
29 | 2682102.3742 | 1247919.6683
30 | 2682088.1351 | 1247929.7939
31 | 2682030.9772 | 1247898.0852

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98598 | -0.27004 | 0.041255 | 0.01034
1 | 0.98593 | -0.27106 | 0.0038272 | 0.00095918
2 | 0.98634 | -0.2631 | 0 | 0
3 | 0.9859 | -0.27161 | 0.002041 | 0.00051153
4 | 0.98605 | -0.26868 | 0.012732 | 0.0031909
5 | 0.98712 | -0.24782 | 0.005311 | 0.0013311
6 | 0.98717 | -0.24699 | 0.0059507 | 0.0014914
7 | 0.99863 | -0.026392 | 0 | 0
8 | 0.99932 | -0.013056 | 0.0068175 | 0.0017086
9 | 0.99822 | -0.03419 | 0 | 0
10 | 0.99841 | -0.030592 | 0 | 0
11 | 0.98823 | -0.22635 | 0.010615 | 0.0026603
12 | 0.99747 | -0.048737 | 0.036163 | 0.0090634
13 | 0.99808 | -0.036927 | 0.019656 | 0.0049264
14 | 0.99428 | -0.1096 | 0 | 0
15 | 0.99416 | -0.1118 | 0 | 0
16 | 0.99532 | -0.089561 | 0 | 0
17 | 0.99413 | -0.11254 | 0.012113 | 0.0030358
18 | 0.99496 | -0.096358 | 0 | 0
19 | 0.99725 | -0.052478 | 0.011344 | 0.0028432
20 | 0.9918 | -0.15727 | 0 | 0
21 | 0.99047 | -0.18292 | 0.0083713 | 0.0020981
22 | 0.99153 | -0.16243 | 0.014003 | 0.0035096
23 | 0.99329 | -0.12846 | 0.015391 | 0.0038573
24 | 0.99435 | -0.10816 | 0.019059 | 0.0047766
25 | 0.99406 | -0.11376 | 0.012212 | 0.0030605
26 | 1 | 0 | -0.33845 | -0.085332
27 | 0.99318 | -0.13085 | 0.039032 | 0.0097824
28 | 0.99859 | -0.026893 | 0.014206 | 0.0035605
29 | 0.99002 | -0.19163 | 0.031221 | 0.0078247
30 | 0.9885 | -0.22114 | 0.0131 | 0.0032832
31 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0058685 | 0.0014706 | -0.0058682 | -0.0014705 | 2.8378e-07 | 5.8579e-08 | 0.0088565 | 0.0088566 | 0.0088566 | 0.98598 | -0.27004 | 0.98593 | -0.27106 | 2.4331
1 | -0.047124 | -0.01181 | 0.047139 | 0.01182 | 1.5577e-05 | 9.8648e-06 | 0.071118 | 0.071118 | 0.071118 | 0.98598 | -0.27004 | 0.98634 | -0.2631 | 19.5379
2 | 0.0020411 | 0.00051137 | -0.002041 | -0.00051153 | 5.4011e-08 | -1.5899e-07 | 0.0030804 | 0.0030805 | 0.0030805 | 0.98593 | -0.27106 | 0.9859 | -0.27161 | 0.84629
3 | 0.012735 | 0.0031927 | -0.012732 | -0.0031909 | 3.386e-06 | 1.8549e-06 | 0.019213 | 0.019213 | 0.019213 | 0.98634 | -0.2631 | 0.98605 | -0.26868 | 5.2783
4 | -0.059875 | -0.015013 | 0.059918 | 0.015041 | 4.3657e-05 | 2.7758e-05 | 0.090331 | 0.090331 | 0.090331 | 0.98634 | -0.2631 | 0.98712 | -0.24782 | 24.8162
5 | -0.065229 | -0.016372 | 0.065232 | 0.016373 | 2.5629e-06 | 1.6312e-06 | 0.098337 | 0.098337 | 0.098337 | 0.98712 | -0.24782 | 0.98717 | -0.24699 | 27.0156
6 | -0.071182 | -0.017865 | 0.071253 | 0.017909 | 7.0144e-05 | 4.4684e-05 | 0.10731 | 0.10731 | 0.10731 | 0.98717 | -0.24699 | 0.98823 | -0.22635 | 29.4798
7 | -0.055868 | -0.01402 | 0.055904 | 0.014042 | 3.5553e-05 | 2.2575e-05 | 0.083253 | 0.083253 | 0.083253 | 0.99863 | -0.026392 | 0.99932 | -0.013056 | 22.8718
8 | 0.019666 | 0.0049323 | -0.019659 | -0.0049279 | 7.3075e-06 | 4.38e-06 | 0.029305 | 0.029305 | 0.029305 | 0.99863 | -0.026392 | 0.99822 | -0.03419 | 8.0509
9 | 0.036202 | 0.0090876 | -0.036195 | -0.009083 | 7.2512e-06 | 4.5539e-06 | 0.053948 | 0.053948 | 0.053948 | 0.99863 | -0.026392 | 0.99841 | -0.030592 | 14.8209
10 | -0.062721 | -0.015751 | 0.06276 | 0.015776 | 3.9097e-05 | 2.4865e-05 | 0.093405 | 0.093405 | 0.093405 | 0.99932 | -0.013056 | 1 | 0 | 25.6606
11 | 0.019659 | 0.0049279 | -0.019656 | -0.0049264 | 2.563e-06 | 1.5363e-06 | 0.029305 | 0.029305 | 0.029305 | 0.99822 | -0.03419 | 0.99808 | -0.036927 | 8.0509
12 | 0.036195 | 0.009083 | -0.036163 | -0.0090634 | 3.1288e-05 | 1.965e-05 | 0.053948 | 0.053948 | 0.053948 | 0.99841 | -0.030592 | 0.99747 | -0.048737 | 14.8209
13 | -0.081867 | -0.02057 | 0.081888 | 0.020583 | 2.0352e-05 | 1.298e-05 | 0.12329 | 0.12329 | 0.12329 | 0.98823 | -0.22635 | 0.9885 | -0.22114 | 33.8707
14 | 0.012214 | 0.0030618 | -0.012213 | -0.0030611 | 1.2817e-06 | 6.8766e-07 | 0.01828 | 0.01828 | 0.01828 | 0.99428 | -0.1096 | 0.99416 | -0.1118 | 5.0219
15 | -0.0634 | -0.015906 | 0.063461 | 0.015945 | 6.0626e-05 | 3.8567e-05 | 0.09489 | 0.09489 | 0.09489 | 0.99428 | -0.1096 | 0.99532 | -0.089561 | 26.0686
16 | 0.051186 | 0.012844 | -0.051179 | -0.01284 | 7.1842e-06 | 4.5556e-06 | 0.07661 | 0.07661 | 0.07661 | 0.99428 | -0.1096 | 0.99413 | -0.11254 | 21.0467
17 | 0.012213 | 0.0030611 | -0.012212 | -0.0030605 | 1.1385e-06 | 6.1087e-07 | 0.01828 | 0.01828 | 0.01828 | 0.99416 | -0.1118 | 0.99406 | -0.11376 | 5.0219
18 | 0.18392 | 0.046496 | -0.18386 | -0.046458 | 5.9926e-05 | 3.8243e-05 | 0.2751 | 0.2751 | 0.2751 | 0.99532 | -0.089561 | 0.99496 | -0.096358 | 37.7889
19 | -0.24738 | -0.062441 | 0.24782 | 0.062722 | 0.00044026 | 0.00028132 | 0.36999 | 0.36999 | 0.36999 | 0.99532 | -0.089561 | 0.99725 | -0.052478 | 50.8231
20 | 0.039066 | 0.0098038 | -0.039032 | -0.0097824 | 3.4082e-05 | 2.1468e-05 | 0.058479 | 0.058479 | 0.058479 | 0.99413 | -0.11254 | 0.99318 | -0.13085 | 16.0657
21 | 0.18386 | 0.046458 | -0.18375 | -0.046392 | 0.00010399 | 6.6361e-05 | 0.2751 | 0.2751 | 0.2751 | 0.99496 | -0.096358 | 0.99435 | -0.10816 | 37.7889
22 | -0.25916 | -0.065565 | 0.25948 | 0.065769 | 0.0003186 | 0.00020361 | 0.38692 | 0.38692 | 0.38692 | 0.99725 | -0.052478 | 0.99859 | -0.026893 | 53.1483
23 | 0.13493 | 0.034013 | -0.13477 | -0.033908 | 0.00016542 | 0.00010573 | 0.20251 | 0.20251 | 0.20251 | 0.9918 | -0.15727 | 0.99047 | -0.18292 | 55.6349
24 | 0.014007 | 0.0035115 | -0.014003 | -0.0035096 | 3.4486e-06 | 1.9385e-06 | 0.021015 | 0.021015 | 0.021015 | 0.9918 | -0.15727 | 0.99153 | -0.16243 | 5.7734
25 | -0.14894 | -0.037525 | 0.14914 | 0.037656 | 0.00020556 | 0.00013099 | 0.22353 | 0.22353 | 0.22353 | 0.9918 | -0.15727 | 0.99329 | -0.12846 | 30.7042
26 | 0.1264 | 0.03181 | -0.12634 | -0.031776 | 5.26e-05 | 3.3614e-05 | 0.18993 | 0.18993 | 0.18993 | 0.99047 | -0.18292 | 0.99002 | -0.19163 | 52.1798
27 | -0.16453 | -0.041513 | 0.1647 | 0.041615 | 0.00016005 | 0.00010207 | 0.24658 | 0.24658 | 0.24658 | 0.99329 | -0.12846 | 0.99435 | -0.10816 | 33.8712
28 | 0.27404 | 0.069556 | -0.27369 | -0.06933 | 0.00035403 | 0.00022628 | 0.40809 | 0.40809 | 0.40809 | 1 | 0 | 0.99859 | -0.026893 | 56.0561
29 | 0.095122 | 0.023951 | -0.094988 | -0.023866 | 0.000134 | 8.5537e-05 | 0.14301 | 0.14301 | 0.14301 | 0.99002 | -0.19163 | 0.9885 | -0.22114 | 39.2883

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.34999 | 0.088223

## res_load
| p_mw | q_mvar
0 | 0.041255 | 0.01034
1 | 0.0038272 | 0.00095918
2 | 0.002041 | 0.00051153
3 | 0.012732 | 0.0031909
4 | 0.005311 | 0.0013311
5 | 0.0059507 | 0.0014914
6 | 0.0068175 | 0.0017086
7 | 0.010615 | 0.0026603
8 | 0.036163 | 0.0090634
9 | 0.019656 | 0.0049264
10 | 0.012113 | 0.0030358
11 | 0.011344 | 0.0028432
12 | 0.0083713 | 0.0020981
13 | 0.014003 | 0.0035096
14 | 0.015391 | 0.0038573
15 | 0.019059 | 0.0047766
16 | 0.012212 | 0.0030605
17 | 0.011537 | 0.0028915
18 | 0.039032 | 0.0097824
19 | 0.014206 | 0.0035605
20 | 0.031221 | 0.0078247
21 | 0.0131 | 0.0032832

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1