## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-220_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-220_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-220_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-220_0_4_node_10 | 0.4 | n |  | TRUE
4 | bus_LV_261-220_0_4_node_11 | 0.4 | n |  | TRUE
5 | bus_LV_261-220_0_4_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_261-220_0_4_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_261-220_0_4_node_26 | 0.4 | n |  | TRUE
8 | bus_LV_261-220_0_4_node_25 | 0.4 | n |  | TRUE
9 | bus_LV_261-220_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_261-220_0_4_node_19 | 0.4 | n |  | TRUE
11 | bus_LV_261-220_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_261-220_0_4_node_18 | 0.4 | n |  | TRUE
13 | bus_LV_261-220_0_4_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_261-220_0_4_node_30 | 0.4 | n |  | TRUE
15 | bus_LV_261-220_0_4_node_29 | 0.4 | n |  | TRUE
16 | bus_LV_261-220_0_4_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_261-220_0_4_node_20 | 0.4 | n |  | TRUE
18 | bus_LV_261-220_0_4_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_261-220_0_4_node_23 | 0.4 | n |  | TRUE
20 | bus_LV_261-220_0_4_node_31 | 0.4 | n |  | TRUE
21 | bus_LV_261-220_0_4_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_261-220_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_261-220_0_4_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_261-220_0_4_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_261-220_0_4_node_14 | 0.4 | n |  | TRUE
26 | bus_MV_530_0_node_186 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-220_0_4_load_0 | 0 | 0.09769 | 0.024483 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-220_0_4_load_11 | 4 | 0.090905 | 0.022783 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-220_0_4_load_26 | 7 | 0.006647 | 0.0016659 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-220_0_4_load_25 | 8 | 0.0030313 | 0.00075972 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-220_0_4_load_19 | 10 | 0.0080235 | 0.0020109 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-220_0_4_load_18 | 12 | 0.010257 | 0.0025706 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-220_0_4_load_17 | 13 | 0.046553 | 0.011667 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-220_0_4_load_30 | 14 | 0.063645 | 0.015951 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-220_0_4_load_29 | 15 | 0.0053814 | 0.0013487 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-220_0_4_load_16 | 16 | 0.027417 | 0.0068713 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-220_0_4_load_20 | 17 | 0.0074403 | 0.0018647 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-220_0_4_load_15 | 18 | 0.0039277 | 0.00098438 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-220_0_4_load_31 | 20 | 0.071683 | 0.017965 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-220_0_4_load_13 | 22 | 0.0069817 | 0.0017498 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-220_0_4_load_12 | 23 | 0.0041259 | 0.001034 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-220_0_4_load_22 | 24 | 0.013099 | 0.0032829 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-220_0_4_load_14 | 25 | 0.012361 | 0.0030981 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-220_0_4_line_0 |  | 0 | 1 | 0.014344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_261-220_0_4_line_1 |  | 0 | 2 | 0.029366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_261-220_0_4_line_2 |  | 1 | 3 | 0.036791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_261-220_0_4_line_3 |  | 2 | 4 | 0.014859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-220_0_4_line_4 |  | 2 | 5 | 0.020273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-220_0_4_line_5 |  | 3 | 13 | 0.0011344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_261-220_0_4_line_6 |  | 3 | 16 | 0.033622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-220_0_4_line_7 |  | 5 | 14 | 0.014715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-220_0_4_line_8 |  | 5 | 15 | 0.01047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-220_0_4_line_9 |  | 6 | 7 | 0.0058619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-220_0_4_line_10 |  | 6 | 8 | 0.07469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-220_0_4_line_11 |  | 7 | 14 | 0.030502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-220_0_4_line_12 |  | 9 | 10 | 0.018309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-220_0_4_line_13 |  | 9 | 11 | 0.039108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-220_0_4_line_14 |  | 9 | 12 | 0.012786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-220_0_4_line_15 |  | 10 | 17 | 0.00072719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-220_0_4_line_16 |  | 11 | 13 | 0.026859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_261-220_0_4_line_17 |  | 12 | 18 | 0.022817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-220_0_4_line_18 |  | 17 | 21 | 0.0095431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-220_0_4_line_19 |  | 18 | 25 | 0.0035908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-220_0_4_line_20 |  | 19 | 20 | 0.026138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-220_0_4_line_21 |  | 19 | 21 | 0.066812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-220_0_4_line_22 |  | 21 | 24 | 0.012802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-220_0_4_line_23 |  | 22 | 23 | 0.018326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-220_0_4_line_24 |  | 23 | 25 | 0.0066814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-220_0_4_trafo_7 | 0.63 MVA 20/0.4 kV | 26 | 11 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2683042.9612 | 1249604.5875 | 2683039.1705 | 1249611.6063 | 2683037.1754 | 1249616.5709 | 2683036.8961 | 1249617.5484
1 | 2683030.1902 | 1249645.7169 | 2683035.6133 | 1249626.7455 | 2683034.8331 | 1249624.7664 | 2683036.8961 | 1249617.5484
2 | 2683042.9612 | 1249604.5875 | 2683043.9369 | 1249602.8554 | 2683045.9269 | 1249599.3251 | 2683047.7345 | 1249596.4261 | 2683057.0618 | 1249598.9698 | 2683061.5233 | 1249599.0434 | 2683064.7392 | 1249599.0996 | 2683069.9469 | 1249598.7279 | 2683074.7012 | 1249598.3831
3 | 2683030.1902 | 1249645.7169 | 2683045.0118 | 1249646.7715
4 | 2683010.8006 | 1249641.3533 | 2683014.8593 | 1249642.6889 | 2683018.5043 | 1249643.9075 | 2683022.4051 | 1249645.1964 | 2683025.7947 | 1249646.3225 | 2683027.387 | 1249646.3893 | 2683030.1902 | 1249645.7169
5 | 2683074.7012 | 1249598.3831 | 2683074.8816 | 1249599.5031
6 | 2683074.7012 | 1249598.3831 | 2683073.8676 | 1249585.1394 | 2683073.8926 | 1249576.3555 | 2683075.2501 | 1249564.8677
7 | 2683010.8006 | 1249641.3533 | 2683015.0149 | 1249627.2542
8 | 2683010.8006 | 1249641.3533 | 2683005.6606 | 1249650.4752
9 | 2683025.2146 | 1249592.3521 | 2683023.6456 | 1249598.0001
10 | 2683025.2146 | 1249592.3521 | 2683018.3402 | 1249586.6516 | 2683008.6717 | 1249587.9727 | 2682998.868 | 1249591.9384 | 2682990.8413 | 1249597.3412 | 2682983.5533 | 1249604.4555 | 2682976.8208 | 1249612.3338 | 2682971.1632 | 1249614.1004 | 2682965.0038 | 1249621.0347
11 | 2683015.0149 | 1249627.2542 | 2683022.1531 | 1249603.3729 | 2683023.6456 | 1249598.0001
12 | 2683107.7738 | 1249601.082 | 2683116.9537 | 1249609.2835 | 2683121.2627 | 1249613.457
13 | 2683079.3203 | 1249625.9906 | 2683087.394 | 1249624.2357 | 2683101.2737 | 1249608.5297 | 2683107.7738 | 1249601.082
14 | 2683107.7738 | 1249601.082 | 2683116.1207 | 1249591.397
15 | 2683121.2627 | 1249613.457 | 2683121.785 | 1249613.963
16 | 2683079.3203 | 1249625.9906 | 2683078.4243 | 1249621.4969 | 2683074.8816 | 1249599.5031
17 | 2683131.0168 | 1249574.1131 | 2683116.1207 | 1249591.397
18 | 2683126.9195 | 1249621.7547 | 2683126.0326 | 1249618.7733 | 2683123.8148 | 1249615.929 | 2683121.785 | 1249613.963
19 | 2683131.0168 | 1249574.1131 | 2683133.361 | 1249571.3931
20 | 2683105.2741 | 1249644.1678 | 2683112.6752 | 1249648.3747 | 2683114.0123 | 1249647.793 | 2683119.1777 | 1249647.7432 | 2683120.4205 | 1249647.9608 | 2683122.7298 | 1249650.2059 | 2683122.8801 | 1249651.3311 | 2683123.4748 | 1249654.6864 | 2683124.4923 | 1249656.4352
21 | 2683124.4923 | 1249656.4352 | 2683125.0893 | 1249657.4777 | 2683127.1654 | 1249659.1192 | 2683130.3328 | 1249659.9308 | 2683140.7316 | 1249662.523 | 2683142.2196 | 1249655.4942 | 2683139.6182 | 1249650.9322 | 2683126.1677 | 1249640.8916 | 2683124.4743 | 1249637.8101 | 2683126.9195 | 1249621.7547
22 | 2683139.2257 | 1249618.1023 | 2683126.9195 | 1249621.7547
23 | 2683137.7229 | 1249566.332 | 2683142.0693 | 1249561.2889 | 2683149.6855 | 1249552.4484
24 | 2683137.7229 | 1249566.332 | 2683133.361 | 1249571.3931

## bus_geodata
| x | y | coords
0 | 2683036.8961 | 1249617.5484
1 | 2683042.9612 | 1249604.5875
2 | 2683030.1902 | 1249645.7169
3 | 2683074.7012 | 1249598.3831
4 | 2683045.0118 | 1249646.7715
5 | 2683010.8006 | 1249641.3533
6 | 2683025.2146 | 1249592.3521
7 | 2683023.6456 | 1249598.0001
8 | 2682965.0038 | 1249621.0347
9 | 2683107.7738 | 1249601.082
10 | 2683121.2627 | 1249613.457
11 | 2683079.3203 | 1249625.9906
12 | 2683116.1207 | 1249591.397
13 | 2683074.8816 | 1249599.5031
14 | 2683015.0149 | 1249627.2542
15 | 2683005.6606 | 1249650.4752
16 | 2683075.2501 | 1249564.8677
17 | 2683121.785 | 1249613.963
18 | 2683131.0168 | 1249574.1131
19 | 2683124.4923 | 1249656.4352
20 | 2683105.2741 | 1249644.1678
21 | 2683126.9195 | 1249621.7547
22 | 2683149.6855 | 1249552.4484
23 | 2683137.7229 | 1249566.332
24 | 2683139.2257 | 1249618.1023
25 | 2683133.361 | 1249571.3931
26 | 2683073.7583 | 1249625.7791

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99293 | -0.13557 | 0.09769 | 0.024483
1 | 0.9941 | -0.113 | 0 | 0
2 | 0.99065 | -0.1797 | 0 | 0
3 | 0.9971 | -0.055359 | 0 | 0
4 | 0.98941 | -0.20372 | 0.090905 | 0.022783
5 | 0.98918 | -0.20808 | 0 | 0
6 | 0.98791 | -0.23291 | 0 | 0
7 | 0.98792 | -0.23259 | 0.006647 | 0.0016659
8 | 0.9877 | -0.23696 | 0.0030313 | 0.00075972
9 | 0.99506 | -0.094467 | 0 | 0
10 | 0.99337 | -0.12683 | 0.0080235 | 0.0020109
11 | 1 | 0 | -0.48471 | -0.12257
12 | 0.99462 | -0.10295 | 0.010257 | 0.0025706
13 | 0.9972 | -0.053406 | 0.046553 | 0.011667
14 | 0.98819 | -0.22732 | 0.063645 | 0.015951
15 | 0.98913 | -0.20908 | 0.0053814 | 0.0013487
16 | 0.99626 | -0.071533 | 0.027417 | 0.0068713
17 | 0.99331 | -0.12802 | 0.0074403 | 0.0018647
18 | 0.99405 | -0.11397 | 0.0039277 | 0.00098438
19 | 0.98816 | -0.22743 | 0 | 0
20 | 0.98644 | -0.26093 | 0.071683 | 0.017965
21 | 0.99257 | -0.14232 | 0 | 0
22 | 0.99379 | -0.11902 | 0.0069817 | 0.0017498
23 | 0.9939 | -0.11676 | 0.0041259 | 0.001034
24 | 0.99241 | -0.14529 | 0.013099 | 0.0032829
25 | 0.99397 | -0.11545 | 0.012361 | 0.0030981
26 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.26794 | -0.067398 | 0.26823 | 0.067583 | 0.00028922 | 0.00018454 | 0.40162 | 0.40162 | 0.40162 | 0.99293 | -0.13557 | 0.9941 | -0.113 | 36.7787
1 | 0.17025 | 0.042915 | -0.16989 | -0.042686 | 0.00035866 | 0.00022879 | 0.25522 | 0.25522 | 0.25522 | 0.99293 | -0.13557 | 0.99065 | -0.1797 | 35.0584
2 | -0.26823 | -0.067583 | 0.26897 | 0.068056 | 0.00074181 | 0.00047332 | 0.40162 | 0.40162 | 0.40162 | 0.9941 | -0.113 | 0.9971 | -0.055359 | 36.7787
3 | 0.091009 | 0.022849 | -0.090905 | -0.022783 | 0.00010415 | 6.6465e-05 | 0.13672 | 0.13672 | 0.13672 | 0.99065 | -0.1797 | 0.98941 | -0.20372 | 37.5592
4 | 0.078882 | 0.019837 | -0.078775 | -0.019769 | 0.00010677 | 6.8072e-05 | 0.11851 | 0.11851 | 0.11851 | 0.99065 | -0.1797 | 0.98918 | -0.20808 | 32.5576
5 | -0.29641 | -0.07494 | 0.29644 | 0.074958 | 2.7774e-05 | 1.7731e-05 | 0.44257 | 0.44257 | 0.44257 | 0.9971 | -0.055359 | 0.9972 | -0.053406 | 40.5286
6 | 0.027438 | 0.0068844 | -0.027417 | -0.0068713 | 2.1142e-05 | 1.3093e-05 | 0.040949 | 0.04095 | 0.04095 | 0.9971 | -0.055359 | 0.99626 | -0.071533 | 11.2499
7 | 0.073393 | 0.01842 | -0.073326 | -0.018377 | 6.7275e-05 | 4.2867e-05 | 0.11041 | 0.11041 | 0.11041 | 0.98918 | -0.20808 | 0.98819 | -0.22732 | 30.3335
8 | 0.0053817 | 0.0013487 | -0.0053814 | -0.0013487 | 2.5733e-07 | 3.029e-08 | 0.0080955 | 0.0080956 | 0.0080956 | 0.98918 | -0.20808 | 0.98913 | -0.20908 | 2.2241
9 | -0.0030319 | -0.00075913 | 0.0030319 | 0.00075909 | 4.5839e-08 | -4.572e-08 | 0.0045665 | 0.0045665 | 0.0045665 | 0.98791 | -0.23291 | 0.98792 | -0.23259 | 1.2545
10 | 0.0030319 | 0.00075913 | -0.0030313 | -0.00075972 | 5.841e-07 | -5.8229e-07 | 0.0045665 | 0.0045668 | 0.0045668 | 0.98791 | -0.23291 | 0.9877 | -0.23696 | 1.2546
11 | -0.009679 | -0.002425 | 0.0096814 | 0.0024262 | 2.4309e-06 | 1.1651e-06 | 0.014578 | 0.014578 | 0.014578 | 0.98792 | -0.23259 | 0.98819 | -0.22732 | 4.005
12 | 0.10088 | 0.025525 | -0.10072 | -0.025425 | 0.00015641 | 9.9868e-05 | 0.15094 | 0.15094 | 0.15094 | 0.99506 | -0.094467 | 0.99337 | -0.12683 | 41.466
13 | -0.13856 | -0.034982 | 0.13919 | 0.035385 | 0.0006302 | 0.00040282 | 0.2073 | 0.2073 | 0.2073 | 0.99506 | -0.094467 | 1 | 0 | 56.9497
14 | 0.037686 | 0.009457 | -0.037671 | -0.0094474 | 1.523e-05 | 9.5814e-06 | 0.056361 | 0.056361 | 0.056361 | 0.99506 | -0.094467 | 0.99462 | -0.10295 | 15.4838
15 | 0.092695 | 0.023414 | -0.09269 | -0.023411 | 5.2625e-06 | 3.3586e-06 | 0.13892 | 0.13892 | 0.13892 | 0.99337 | -0.12683 | 0.99331 | -0.12802 | 38.1641
16 | 0.34387 | 0.087188 | -0.34299 | -0.086625 | 0.00088026 | 0.00056231 | 0.51204 | 0.51204 | 0.51204 | 1 | 0 | 0.9972 | -0.053406 | 46.8899
17 | 0.027414 | 0.0068768 | -0.0274 | -0.0068679 | 1.4394e-05 | 8.9165e-06 | 0.041016 | 0.041016 | 0.041016 | 0.99462 | -0.10295 | 0.99405 | -0.11397 | 11.2681
18 | 0.08525 | 0.021546 | -0.085191 | -0.021509 | 5.8424e-05 | 3.7268e-05 | 0.12777 | 0.12777 | 0.12777 | 0.99331 | -0.12802 | 0.99257 | -0.14232 | 35.1021
19 | 0.023472 | 0.0058835 | -0.02347 | -0.0058825 | 1.6624e-06 | 1.0174e-06 | 0.035136 | 0.035136 | 0.035136 | 0.99405 | -0.11397 | 0.99397 | -0.11545 | 9.6528
20 | 0.071798 | 0.018039 | -0.071683 | -0.017965 | 0.00011461 | 7.3014e-05 | 0.10813 | 0.10813 | 0.10813 | 0.98816 | -0.22743 | 0.98644 | -0.26093 | 29.7065
21 | -0.071798 | -0.018039 | 0.072091 | 0.018225 | 0.00029295 | 0.00018663 | 0.10813 | 0.10813 | 0.10813 | 0.98816 | -0.22743 | 0.99257 | -0.14232 | 29.7065
22 | 0.013101 | 0.0032839 | -0.013099 | -0.0032829 | 1.8519e-06 | 1.0197e-06 | 0.01964 | 0.01964 | 0.01964 | 0.99257 | -0.14232 | 0.99241 | -0.14529 | 5.3957
23 | -0.0069817 | -0.0017498 | 0.0069825 | 0.00175 | 7.5103e-07 | 2.4318e-07 | 0.010454 | 0.010454 | 0.010454 | 0.99379 | -0.11902 | 0.9939 | -0.11676 | 2.8719
24 | -0.011108 | -0.0027841 | 0.011109 | 0.0027844 | 6.9298e-07 | 3.5691e-07 | 0.016631 | 0.016631 | 0.016631 | 0.9939 | -0.11676 | 0.99397 | -0.11545 | 4.5689

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.48471 | 0.12257

## res_load
| p_mw | q_mvar
0 | 0.09769 | 0.024483
1 | 0.090905 | 0.022783
2 | 0.006647 | 0.0016659
3 | 0.0030313 | 0.00075972
4 | 0.0080235 | 0.0020109
5 | 0.010257 | 0.0025706
6 | 0.046553 | 0.011667
7 | 0.063645 | 0.015951
8 | 0.0053814 | 0.0013487
9 | 0.027417 | 0.0068713
10 | 0.0074403 | 0.0018647
11 | 0.0039277 | 0.00098438
12 | 0.071683 | 0.017965
13 | 0.0069817 | 0.0017498
14 | 0.0041259 | 0.001034
15 | 0.013099 | 0.0032829
16 | 0.012361 | 0.0030981

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1