## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-221_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-221_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-221_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-221_0_5_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_261-221_0_5_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_261-221_0_5_node_41 | 0.4 | n |  | TRUE
6 | bus_LV_261-221_0_5_node_35 | 0.4 | n |  | TRUE
7 | bus_LV_261-221_0_5_node_32 | 0.4 | n |  | TRUE
8 | bus_LV_261-221_0_5_node_15 | 0.4 | n |  | TRUE
9 | bus_LV_261-221_0_5_node_28 | 0.4 | n |  | TRUE
10 | bus_LV_261-221_0_5_node_14 | 0.4 | n |  | TRUE
11 | bus_LV_261-221_0_5_node_53 | 0.4 | n |  | TRUE
12 | bus_LV_261-221_0_5_node_52 | 0.4 | n |  | TRUE
13 | bus_LV_261-221_0_5_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_261-221_0_5_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_261-221_0_5_node_34 | 0.4 | n |  | TRUE
16 | bus_LV_261-221_0_5_node_6 | 0.4 | n |  | TRUE
17 | bus_LV_261-221_0_5_node_7 | 0.4 | n |  | TRUE
18 | bus_LV_261-221_0_5_node_8 | 0.4 | n |  | TRUE
19 | bus_LV_261-221_0_5_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_261-221_0_5_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_261-221_0_5_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_261-221_0_5_node_33 | 0.4 | n |  | TRUE
23 | bus_LV_261-221_0_5_node_31 | 0.4 | n |  | TRUE
24 | bus_LV_261-221_0_5_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_261-221_0_5_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_261-221_0_5_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_261-221_0_5_node_61 | 0.4 | n |  | TRUE
28 | bus_LV_261-221_0_5_node_39 | 0.4 | n |  | TRUE
29 | bus_LV_261-221_0_5_node_50 | 0.4 | n |  | TRUE
30 | bus_LV_261-221_0_5_node_54 | 0.4 | n |  | TRUE
31 | bus_LV_261-221_0_5_node_58 | 0.4 | n |  | TRUE
32 | bus_LV_261-221_0_5_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_261-221_0_5_node_59 | 0.4 | n |  | TRUE
34 | bus_LV_261-221_0_5_node_56 | 0.4 | n |  | TRUE
35 | bus_LV_261-221_0_5_node_17 | 0.4 | n |  | TRUE
36 | bus_LV_261-221_0_5_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_261-221_0_5_node_29 | 0.4 | n |  | TRUE
38 | bus_LV_261-221_0_5_node_26 | 0.4 | n |  | TRUE
39 | bus_LV_261-221_0_5_node_44 | 0.4 | n |  | TRUE
40 | bus_LV_261-221_0_5_node_38 | 0.4 | n |  | TRUE
41 | bus_LV_261-221_0_5_node_27 | 0.4 | n |  | TRUE
42 | bus_LV_261-221_0_5_node_16 | 0.4 | n |  | TRUE
43 | bus_LV_261-221_0_5_node_57 | 0.4 | n |  | TRUE
44 | bus_LV_261-221_0_5_node_55 | 0.4 | n |  | TRUE
45 | bus_LV_261-221_0_5_node_36 | 0.4 | n |  | TRUE
46 | bus_LV_261-221_0_5_node_49 | 0.4 | n |  | TRUE
47 | bus_LV_261-221_0_5_node_47 | 0.4 | n |  | TRUE
48 | bus_LV_261-221_0_5_node_62 | 0.4 | n |  | TRUE
49 | bus_LV_261-221_0_5_node_46 | 0.4 | n |  | TRUE
50 | bus_LV_261-221_0_5_node_40 | 0.4 | n |  | TRUE
51 | bus_LV_261-221_0_5_node_48 | 0.4 | n |  | TRUE
52 | bus_LV_261-221_0_5_node_60 | 0.4 | n |  | TRUE
53 | bus_LV_261-221_0_5_node_51 | 0.4 | n |  | TRUE
54 | bus_LV_261-221_0_5_node_37 | 0.4 | n |  | TRUE
55 | bus_LV_261-221_0_5_node_45 | 0.4 | n |  | TRUE
56 | bus_MV_530_0_node_191 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-221_0_5_load_0 | 0 | 0.0047792 | 0.0011978 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-221_0_5_load_1 | 1 | 0.0034417 | 0.00086256 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-221_0_5_load_4 | 3 | 0.0047613 | 0.0011933 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-221_0_5_load_41 | 5 | 0.004471 | 0.0011205 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-221_0_5_load_14 | 10 | 0.0077644 | 0.0019459 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-221_0_5_load_53 | 11 | 0.0092116 | 0.0023087 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-221_0_5_load_52 | 12 | 0.0092444 | 0.0023169 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-221_0_5_load_13 | 13 | 0.0080112 | 0.0020078 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-221_0_5_load_12 | 14 | 0.0091341 | 0.0022892 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-221_0_5_load_6 | 16 | 0.030475 | 0.0076377 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-221_0_5_load_7 | 17 | 0.011454 | 0.0028705 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-221_0_5_load_11 | 21 | 0.0099574 | 0.0024956 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-221_0_5_load_31 | 23 | 0.0094903 | 0.0023785 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-221_0_5_load_19 | 25 | 0.0163 | 0.0040852 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-221_0_5_load_61 | 27 | 0.013187 | 0.0033049 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-221_0_5_load_54 | 30 | 0.0056229 | 0.0014092 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-221_0_5_load_58 | 31 | 0.0078963 | 0.001979 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-221_0_5_load_59 | 33 | 0.0045936 | 0.0011513 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-221_0_5_load_56 | 34 | 0.0029541 | 0.00074038 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-221_0_5_load_17 | 35 | 0.029888 | 0.0074906 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-221_0_5_load_29 | 37 | 0.0051628 | 0.0012939 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-221_0_5_load_26 | 38 | 0.0074838 | 0.0018756 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-221_0_5_load_44 | 39 | 0.0079779 | 0.0019995 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-221_0_5_load_27 | 41 | 0.0075559 | 0.0018937 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-221_0_5_load_16 | 42 | 0.015537 | 0.003894 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-221_0_5_load_57 | 43 | 0.0058282 | 0.0014607 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-221_0_5_load_55 | 44 | 0.0055718 | 0.0013964 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-221_0_5_load_36 | 45 | 0.015809 | 0.003962 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-221_0_5_load_49 | 46 | 0.013494 | 0.003382 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-221_0_5_load_62 | 48 | 0.011657 | 0.0029215 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-221_0_5_load_46 | 49 | 0.013504 | 0.0033845 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-221_0_5_load_60 | 52 | 0.013686 | 0.00343 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-221_0_5_load_51 | 53 | 0.0095258 | 0.0023874 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-221_0_5_load_45 | 55 | 0.015476 | 0.0038786 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 22 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-221_0_5_line_0 |  | 0 | 1 | 0.0056299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-221_0_5_line_1 |  | 0 | 2 | 0.0047866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-221_0_5_line_2 |  | 2 | 3 | 0.010901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-221_0_5_line_3 |  | 2 | 4 | 0.024962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-221_0_5_line_4 |  | 3 | 5 | 0.015704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-221_0_5_line_5 |  | 4 | 6 | 0.0097867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-221_0_5_line_6 |  | 4 | 7 | 0.01986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-221_0_5_line_7 |  | 6 | 11 | 0.027056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-221_0_5_line_8 |  | 6 | 12 | 0.012683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-221_0_5_line_9 |  | 7 | 15 | 0.015111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-221_0_5_line_10 |  | 8 | 9 | 0.004129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-221_0_5_line_11 |  | 8 | 10 | 0.025917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-221_0_5_line_12 |  | 9 | 39 | 0.015864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-221_0_5_line_13 |  | 9 | 40 | 0.042163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-221_0_5_line_14 |  | 9 | 41 | 0.014067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-221_0_5_line_15 |  | 10 | 14 | 0.030336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-221_0_5_line_16 |  | 12 | 53 | 0.0022076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-221_0_5_line_17 |  | 13 | 14 | 0.02811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-221_0_5_line_18 |  | 15 | 46 | 0.014336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-221_0_5_line_19 |  | 16 | 17 | 0.0052981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-221_0_5_line_20 |  | 16 | 18 | 0.013239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-221_0_5_line_21 |  | 17 | 19 | 0.013638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_261-221_0_5_line_22 |  | 18 | 20 | 0.001229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-221_0_5_line_23 |  | 18 | 21 | 0.03197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-221_0_5_line_24 |  | 19 | 22 | 0.024483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_261-221_0_5_line_25 |  | 19 | 23 | 0.011665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-221_0_5_line_26 |  | 20 | 24 | 0.030869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-221_0_5_line_27 |  | 20 | 25 | 0.032193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-221_0_5_line_28 |  | 21 | 26 | 0.0017566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-221_0_5_line_29 |  | 22 | 27 | 0.012663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-221_0_5_line_30 |  | 22 | 28 | 0.045691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-221_0_5_line_31 |  | 22 | 29 | 0.016886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-221_0_5_line_32 |  | 24 | 31 | 0.016078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-221_0_5_line_33 |  | 25 | 35 | 0.018594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-221_0_5_line_34 |  | 26 | 30 | 0.021603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-221_0_5_line_35 |  | 28 | 49 | 0.015144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-221_0_5_line_36 |  | 28 | 50 | 0.010992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-221_0_5_line_37 |  | 28 | 47 | 0.0182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-221_0_5_line_38 |  | 29 | 46 | 0.016353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-221_0_5_line_39 |  | 29 | 51 | 0.003086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-221_0_5_line_40 |  | 30 | 44 | 0.010819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-221_0_5_line_41 |  | 31 | 43 | 0.01394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-221_0_5_line_42 |  | 32 | 33 | 0.011711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-221_0_5_line_43 |  | 32 | 34 | 0.0059409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-221_0_5_line_44 |  | 34 | 43 | 0.0084521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-221_0_5_line_45 |  | 35 | 42 | 0.017441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-221_0_5_line_46 |  | 36 | 37 | 0.0032196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-221_0_5_line_47 |  | 36 | 38 | 0.011488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-221_0_5_line_48 |  | 38 | 41 | 0.018302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-221_0_5_line_49 |  | 40 | 45 | 0.018644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-221_0_5_line_50 |  | 45 | 54 | 0.0027629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-221_0_5_line_51 |  | 47 | 48 | 0.010781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-221_0_5_line_52 |  | 50 | 55 | 0.0057447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-221_0_5_line_53 |  | 50 | 54 | 0.011767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-221_0_5_line_54 |  | 51 | 52 | 0.009626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-221_0_5_trafo_33 | 0.63 MVA 20/0.4 kV | 56 | 22 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2683212.8142 | 1249805.0764 | 2683218.443 | 1249804.9627
1 | 2683208.0287 | 1249805.1731 | 2683212.8142 | 1249805.0764
2 | 2683208.0287 | 1249805.1731 | 2683210.2402 | 1249815.8472
3 | 2683183.0628 | 1249807.0464 | 2683188.1951 | 1249806.6626 | 2683208.0287 | 1249805.1731
4 | 2683214.1093 | 1249831.062 | 2683210.9561 | 1249819.3025 | 2683210.2402 | 1249815.8472
5 | 2683183.0628 | 1249807.0464 | 2683179.7218 | 1249807.3108 | 2683180.7501 | 1249813.6633
6 | 2683183.0628 | 1249807.0464 | 2683179.7218 | 1249807.3108 | 2683179.013 | 1249802.9421 | 2683178.5029 | 1249790.8704
7 | 2683180.7501 | 1249813.6633 | 2683183.8638 | 1249827.9732 | 2683187.2022 | 1249839.9266
8 | 2683180.7501 | 1249813.6633 | 2683172.9498 | 1249814.7769 | 2683168.4487 | 1249816.4558
9 | 2683178.5029 | 1249790.8704 | 2683178.715 | 1249775.7621
10 | 2683187.2999 | 1249674.1516 | 2683183.2818 | 1249673.15
11 | 2683187.2999 | 1249674.1516 | 2683185.5138 | 1249682.5105 | 2683183.4318 | 1249699.7545
12 | 2683183.2818 | 1249673.15 | 2683186.9335 | 1249657.7121
13 | 2683179.3709 | 1249715.0707 | 2683180.3549 | 1249693.3907 | 2683181.5015 | 1249683.7885 | 2683183.2818 | 1249673.15
14 | 2683183.2818 | 1249673.15 | 2683169.6337 | 1249669.7414
15 | 2683182.4135 | 1249730.0363 | 2683182.5318 | 1249707.2092 | 2683183.4318 | 1249699.7545
16 | 2683166.3804 | 1249817.2273 | 2683168.4487 | 1249816.4558
17 | 2683182.4135 | 1249730.0363 | 2683182.4126 | 1249730.2135 | 2683182.6742 | 1249758.1447
18 | 2683178.715 | 1249775.7621 | 2683164.3811 | 1249775.9723
19 | 2683113.8668 | 1249789.4753 | 2683119.1488 | 1249789.8881
20 | 2683100.6678 | 1249788.4437 | 2683113.8668 | 1249789.4753
21 | 2683132.7452 | 1249790.9508 | 2683119.1488 | 1249789.8881
22 | 2683100.481 | 1249787.229 | 2683100.6678 | 1249788.4437
23 | 2683100.6678 | 1249788.4437 | 2683104.6323 | 1249820.1673
24 | 2683132.7452 | 1249790.9508 | 2683133.2542 | 1249777.2812 | 2683134.5206 | 1249773.6629 | 2683136.318 | 1249771.4865 | 2683136.7007 | 1249767.3554
25 | 2683132.7452 | 1249790.9508 | 2683144.4104 | 1249790.9303
26 | 2683076.8801 | 1249802.1427 | 2683079.6831 | 1249798.7906 | 2683082.6756 | 1249795.3855 | 2683084.6339 | 1249789.8088 | 2683097.0528 | 1249787.7814 | 2683100.481 | 1249787.229
27 | 2683100.481 | 1249787.229 | 2683095.6726 | 1249755.3969
28 | 2683104.4115 | 1249821.9099 | 2683104.6323 | 1249820.1673
29 | 2683145.3271 | 1249775.7049 | 2683144.7488 | 1249772.7946 | 2683141.8634 | 1249770.7192 | 2683136.7007 | 1249767.3554
30 | 2683136.7007 | 1249767.3554 | 2683135.964 | 1249764.9656 | 2683135.5758 | 1249761.4242 | 2683135.4879 | 1249758.543 | 2683135.9206 | 1249756.2251 | 2683137.3564 | 1249752.9095 | 2683139.8255 | 1249751.8322 | 2683140.5096 | 1249748.8173 | 2683140.2024 | 1249745.4216 | 2683138.9031 | 1249742.2343 | 2683138.0867 | 1249739.6098 | 2683138.9754 | 1249737.0871 | 2683140.9799 | 1249735.2138 | 2683142.8438 | 1249733.6833 | 2683144.2907 | 1249732.2692 | 2683148.2487 | 1249728.3996
31 | 2683153.334 | 1249764.1753 | 2683136.7007 | 1249767.3554
32 | 2683076.8801 | 1249802.1427 | 2683081.7121 | 1249808.0926 | 2683085.0375 | 1249813.7879 | 2683085.3826 | 1249815.5726
33 | 2683095.6726 | 1249755.3969 | 2683094.8709 | 1249750.0895 | 2683093.2504 | 1249736.9628
34 | 2683104.4115 | 1249821.9099 | 2683106.0578 | 1249833.7306 | 2683108.1372 | 1249843.1726
35 | 2683162.523 | 1249729.2226 | 2683159.0071 | 1249727.4164 | 2683151.3742 | 1249729.5109 | 2683148.2487 | 1249728.3996
36 | 2683146.3317 | 1249717.5758 | 2683148.2487 | 1249728.3996
37 | 2683155.0403 | 1249738.9026 | 2683152.4165 | 1249737.02 | 2683148.03 | 1249734.8346 | 2683144.2907 | 1249732.2692 | 2683148.2487 | 1249728.3996
38 | 2683153.334 | 1249764.1753 | 2683157.3419 | 1249769.6578 | 2683159.5664 | 1249772.5578 | 2683162.596 | 1249774.5796 | 2683164.3811 | 1249775.9723
39 | 2683153.1885 | 1249761.0932 | 2683153.334 | 1249764.1753
40 | 2683108.1372 | 1249843.1726 | 2683109.4082 | 1249848.9445 | 2683110.5671 | 1249853.7148
41 | 2683085.3826 | 1249815.5726 | 2683088.0287 | 1249829.2588
42 | 2683090.7609 | 1249843.3901 | 2683085.1672 | 1249853.6782
43 | 2683090.7609 | 1249843.3901 | 2683089.6331 | 1249837.5572
44 | 2683089.6331 | 1249837.5572 | 2683088.0287 | 1249829.2588
45 | 2683091.1136 | 1249719.6531 | 2683093.2504 | 1249736.9628
46 | 2683140.7316 | 1249662.523 | 2683137.6076 | 1249661.7443
47 | 2683140.7316 | 1249662.523 | 2683151.8769 | 1249665.3066
48 | 2683169.6337 | 1249669.7414 | 2683151.8769 | 1249665.3066
49 | 2683179.3709 | 1249715.0707 | 2683160.7338 | 1249715.5644
50 | 2683157.9719 | 1249715.6376 | 2683160.7338 | 1249715.5644
51 | 2683155.0403 | 1249738.9026 | 2683158.8762 | 1249743.193 | 2683162.9265 | 1249746.1965
52 | 2683146.3317 | 1249717.5758 | 2683140.5891 | 1249717.4229
53 | 2683146.3317 | 1249717.5758 | 2683157.9719 | 1249715.6376
54 | 2683153.1885 | 1249761.0932 | 2683158.7395 | 1249761.538 | 2683162.822 | 1249761.7065

## bus_geodata
| x | y | coords
0 | 2683212.8142 | 1249805.0764
1 | 2683218.443 | 1249804.9627
2 | 2683208.0287 | 1249805.1731
3 | 2683210.2402 | 1249815.8472
4 | 2683183.0628 | 1249807.0464
5 | 2683214.1093 | 1249831.062
6 | 2683180.7501 | 1249813.6633
7 | 2683178.5029 | 1249790.8704
8 | 2683187.2999 | 1249674.1516
9 | 2683183.2818 | 1249673.15
10 | 2683183.4318 | 1249699.7545
11 | 2683187.2022 | 1249839.9266
12 | 2683168.4487 | 1249816.4558
13 | 2683182.6742 | 1249758.1447
14 | 2683182.4135 | 1249730.0363
15 | 2683178.715 | 1249775.7621
16 | 2683113.8668 | 1249789.4753
17 | 2683119.1488 | 1249789.8881
18 | 2683100.6678 | 1249788.4437
19 | 2683132.7452 | 1249790.9508
20 | 2683100.481 | 1249787.229
21 | 2683104.6323 | 1249820.1673
22 | 2683136.7007 | 1249767.3554
23 | 2683144.4104 | 1249790.9303
24 | 2683076.8801 | 1249802.1427
25 | 2683095.6726 | 1249755.3969
26 | 2683104.4115 | 1249821.9099
27 | 2683145.3271 | 1249775.7048
28 | 2683148.2487 | 1249728.3996
29 | 2683153.334 | 1249764.1753
30 | 2683108.1372 | 1249843.1726
31 | 2683085.3826 | 1249815.5726
32 | 2683090.7609 | 1249843.3901
33 | 2683085.1672 | 1249853.6782
34 | 2683089.6331 | 1249837.5572
35 | 2683093.2504 | 1249736.9628
36 | 2683140.7316 | 1249662.523
37 | 2683137.6076 | 1249661.7443
38 | 2683151.8769 | 1249665.3066
39 | 2683186.9335 | 1249657.7121
40 | 2683179.3709 | 1249715.0707
41 | 2683169.6337 | 1249669.7414
42 | 2683091.1136 | 1249719.6531
43 | 2683088.0287 | 1249829.2588
44 | 2683110.5671 | 1249853.7148
45 | 2683160.7338 | 1249715.5644
46 | 2683164.3811 | 1249775.9723
47 | 2683155.0403 | 1249738.9026
48 | 2683162.9265 | 1249746.1965
49 | 2683162.523 | 1249729.2226
50 | 2683146.3317 | 1249717.5758
51 | 2683153.1885 | 1249761.0932
52 | 2683162.822 | 1249761.7065
53 | 2683166.3804 | 1249817.2273
54 | 2683157.9719 | 1249715.6376
55 | 2683140.5891 | 1249717.4229
56 | 2683145.3271 | 1249775.7048

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99553 | -0.085884 | 0.0047792 | 0.0011978
1 | 0.99552 | -0.086225 | 0.0034417 | 0.00086256
2 | 0.99557 | -0.085192 | 0 | 0
3 | 0.99548 | -0.086962 | 0.0047613 | 0.0011933
4 | 0.99597 | -0.077533 | 0 | 0
5 | 0.99541 | -0.088197 | 0.004471 | 0.0011205
6 | 0.99572 | -0.082347 | 0 | 0
7 | 0.99679 | -0.06169 | 0 | 0
8 | 0.99061 | -0.18062 | 0 | 0
9 | 0.9907 | -0.17879 | 0 | 0
10 | 0.99002 | -0.19209 | 0.0077644 | 0.0019459
11 | 0.99549 | -0.086729 | 0.0092116 | 0.0023087
12 | 0.9955 | -0.086533 | 0.0092444 | 0.0023169
13 | 0.98934 | -0.20535 | 0.0080112 | 0.0020078
14 | 0.98954 | -0.20134 | 0.0091341 | 0.0022892
15 | 0.99741 | -0.049653 | 0 | 0
16 | 0.9967 | -0.063197 | 0.030475 | 0.0076377
17 | 0.99736 | -0.050691 | 0.011454 | 0.0028705
18 | 0.99545 | -0.087422 | 0 | 0
19 | 0.99826 | -0.033252 | 0 | 0
20 | 0.99535 | -0.089216 | 0 | 0
21 | 0.99483 | -0.099324 | 0.0099574 | 0.0024956
22 | 1 | 0 | -0.35431 | -0.089059
23 | 0.99816 | -0.035189 | 0.0094903 | 0.0023785
24 | 0.99475 | -0.10078 | 0 | 0
25 | 0.99354 | -0.12424 | 0.0163 | 0.0040852
26 | 0.99481 | -0.099671 | 0 | 0
27 | 0.99985 | -0.0029109 | 0.013187 | 0.0033049
28 | 0.99543 | -0.08764 | 0 | 0
29 | 0.99888 | -0.021397 | 0 | 0
30 | 0.99459 | -0.10393 | 0.0056229 | 0.0014092
31 | 0.99444 | -0.1068 | 0.0078963 | 0.001979
32 | 0.99419 | -0.1117 | 0 | 0
33 | 0.99414 | -0.11264 | 0.0045936 | 0.0011513
34 | 0.99421 | -0.11121 | 0.0029541 | 0.00074038
35 | 0.99277 | -0.13916 | 0.029888 | 0.0074906
36 | 0.99018 | -0.18901 | 0 | 0
37 | 0.99016 | -0.1893 | 0.0051628 | 0.0012939
38 | 0.99023 | -0.18795 | 0.0074838 | 0.0018756
39 | 0.99059 | -0.18104 | 0.0079779 | 0.0019995
40 | 0.99275 | -0.13912 | 0 | 0
41 | 0.99044 | -0.18384 | 0.0075559 | 0.0018937
42 | 0.99252 | -0.14396 | 0.015537 | 0.003894
43 | 0.99427 | -0.11009 | 0.0058282 | 0.0014607
44 | 0.99454 | -0.10499 | 0.0055718 | 0.0013964
45 | 0.99366 | -0.12163 | 0.015809 | 0.003962
46 | 0.99801 | -0.038247 | 0.013494 | 0.003382
47 | 0.99523 | -0.091372 | 0 | 0
48 | 0.99512 | -0.093584 | 0.011657 | 0.0029215
49 | 0.99524 | -0.091238 | 0.013504 | 0.0033845
50 | 0.99458 | -0.10397 | 0 | 0
51 | 0.99885 | -0.022135 | 0 | 0
52 | 0.99873 | -0.024437 | 0.013686 | 0.00343
53 | 0.99548 | -0.086903 | 0.0095258 | 0.0023874
54 | 0.99383 | -0.11827 | 0 | 0
55 | 0.9945 | -0.10554 | 0.015476 | 0.0038786
56 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0034417 | 0.00086252 | -0.0034417 | -0.00086256 | 5.5871e-08 | -3.7444e-08 | 0.0051443 | 0.0051443 | 0.0051443 | 0.99553 | -0.085884 | 0.99552 | -0.086225 | 1.4133
1 | -0.008221 | -0.0020603 | 0.0082212 | 0.0020604 | 2.7102e-07 | 1.1121e-07 | 0.012288 | 0.012288 | 0.012288 | 0.99553 | -0.085884 | 0.99557 | -0.085192 | 3.3758
2 | 0.0092333 | 0.0023141 | -0.0092325 | -0.0023138 | 7.7853e-07 | 3.5653e-07 | 0.0138 | 0.0138 | 0.0138 | 0.99557 | -0.085192 | 0.99548 | -0.086962 | 3.7913
3 | -0.017455 | -0.0043746 | 0.017461 | 0.0043783 | 6.3708e-06 | 3.7526e-06 | 0.026088 | 0.026088 | 0.026088 | 0.99557 | -0.085192 | 0.99597 | -0.077533 | 7.1671
4 | 0.0044713 | 0.0011205 | -0.004471 | -0.0011205 | 2.6305e-07 | -3.5795e-08 | 0.0066835 | 0.0066836 | 0.0066836 | 0.99548 | -0.086962 | 0.99541 | -0.088197 | 1.8361
5 | 0.027994 | 0.0070201 | -0.027988 | -0.0070161 | 6.4203e-06 | 3.9817e-06 | 0.041826 | 0.041826 | 0.041826 | 0.99597 | -0.077533 | 0.99572 | -0.082347 | 11.4906
6 | -0.045455 | -0.011398 | 0.045489 | 0.01142 | 3.435e-05 | 2.1725e-05 | 0.067914 | 0.067914 | 0.067914 | 0.99597 | -0.077533 | 0.99679 | -0.06169 | 18.6576
7 | 0.0092136 | 0.0023095 | -0.0092116 | -0.0023087 | 1.9235e-06 | 8.7922e-07 | 0.013769 | 0.013769 | 0.013769 | 0.99572 | -0.082347 | 0.99549 | -0.086729 | 3.7827
8 | 0.018774 | 0.0047066 | -0.01877 | -0.0047043 | 3.744e-06 | 2.2312e-06 | 0.028057 | 0.028057 | 0.028057 | 0.99572 | -0.082347 | 0.9955 | -0.086533 | 7.7079
9 | -0.045489 | -0.01142 | 0.045515 | 0.011437 | 2.6136e-05 | 1.653e-05 | 0.067914 | 0.067914 | 0.067914 | 0.99679 | -0.06169 | 0.99741 | -0.049653 | 18.6576
10 | -0.024932 | -0.0062564 | 0.024935 | 0.0062578 | 2.1721e-06 | 1.337e-06 | 0.037454 | 0.037454 | 0.037454 | 0.99061 | -0.18062 | 0.9907 | -0.17879 | 10.2896
11 | 0.024932 | 0.0062564 | -0.024919 | -0.006248 | 1.3634e-05 | 8.3922e-06 | 0.037454 | 0.037454 | 0.037454 | 0.99061 | -0.18062 | 0.99002 | -0.19209 | 10.2897
12 | 0.0079788 | 0.0019998 | -0.0079779 | -0.0019995 | 8.5437e-07 | 3.4255e-07 | 0.011984 | 0.011984 | 0.011984 | 0.9907 | -0.17879 | 0.99059 | -0.18104 | 3.2923
13 | -0.053124 | -0.013325 | 0.053224 | 0.013389 | 0.00010067 | 6.3886e-05 | 0.079794 | 0.079794 | 0.079794 | 0.9907 | -0.17879 | 0.99275 | -0.13912 | 21.9215
14 | 0.02021 | 0.0050675 | -0.020205 | -0.0050646 | 4.8611e-06 | 2.93e-06 | 0.030356 | 0.030356 | 0.030356 | 0.9907 | -0.17879 | 0.99044 | -0.18384 | 8.3396
15 | 0.017154 | 0.0043021 | -0.017147 | -0.0042976 | 7.5632e-06 | 4.4506e-06 | 0.025784 | 0.025785 | 0.025785 | 0.99002 | -0.19209 | 0.98954 | -0.20134 | 7.0837
16 | 0.0095259 | 0.0023875 | -0.0095258 | -0.0023874 | 1.6784e-07 | 7.8716e-08 | 0.014239 | 0.014239 | 0.014239 | 0.9955 | -0.086533 | 0.99548 | -0.086903 | 3.9118
17 | -0.0080112 | -0.0020078 | 0.0080127 | 0.0020084 | 1.5304e-06 | 6.1842e-07 | 0.012049 | 0.012049 | 0.012049 | 0.98934 | -0.20535 | 0.98954 | -0.20134 | 3.3102
18 | -0.045515 | -0.011437 | 0.04554 | 0.011452 | 2.4795e-05 | 1.5681e-05 | 0.067914 | 0.067914 | 0.067914 | 0.99741 | -0.049653 | 0.99801 | -0.038247 | 18.6576
19 | -0.13493 | -0.03393 | 0.13501 | 0.033982 | 8.065e-05 | 5.1547e-05 | 0.20148 | 0.20148 | 0.20148 | 0.9967 | -0.063197 | 0.99736 | -0.050691 | 55.3508
20 | 0.10445 | 0.026293 | -0.10433 | -0.026216 | 0.00012079 | 7.7134e-05 | 0.15598 | 0.15598 | 0.15598 | 0.9967 | -0.063197 | 0.99545 | -0.087422 | 42.8518
21 | -0.14646 | -0.036853 | 0.14658 | 0.03693 | 0.00012215 | 7.7823e-05 | 0.21857 | 0.21857 | 0.21857 | 0.99736 | -0.050691 | 0.99826 | -0.033252 | 30.0227
22 | 0.083164 | 0.020906 | -0.083157 | -0.020901 | 7.1251e-06 | 4.5441e-06 | 0.12434 | 0.12434 | 0.12434 | 0.99545 | -0.087422 | 0.99535 | -0.089216 | 34.1588
23 | 0.021167 | 0.0053098 | -0.021155 | -0.0053025 | 1.2004e-05 | 7.2671e-06 | 0.031642 | 0.031643 | 0.031643 | 0.99545 | -0.087422 | 0.99483 | -0.099324 | 8.693
24 | -0.15607 | -0.039309 | 0.15632 | 0.039468 | 0.0002486 | 0.00015846 | 0.23271 | 0.23271 | 0.23271 | 0.99826 | -0.033252 | 1 | 0 | 31.966
25 | 0.0094911 | 0.0023789 | -0.0094903 | -0.0023785 | 8.7557e-07 | 4.0787e-07 | 0.014148 | 0.014148 | 0.014148 | 0.99826 | -0.033252 | 0.99816 | -0.035189 | 3.8867
26 | 0.021293 | 0.0053434 | -0.021281 | -0.0053363 | 1.1731e-05 | 7.1072e-06 | 0.031835 | 0.031835 | 0.031835 | 0.99535 | -0.089216 | 0.99475 | -0.10078 | 8.7458
27 | 0.061864 | 0.015558 | -0.061761 | -0.015492 | 0.0001033 | 6.5696e-05 | 0.092504 | 0.092504 | 0.092504 | 0.99535 | -0.089216 | 0.99354 | -0.12424 | 25.4131
28 | 0.011197 | 0.002807 | -0.011197 | -0.0028069 | 1.8478e-07 | 9.5454e-08 | 0.016749 | 0.016749 | 0.016749 | 0.99483 | -0.099324 | 0.99481 | -0.099671 | 4.6013
29 | 0.013188 | 0.0033059 | -0.013187 | -0.0033049 | 1.8288e-06 | 1.0043e-06 | 0.019625 | 0.019625 | 0.019625 | 1 | 0 | 0.99985 | -0.0029109 | 5.3914
30 | 0.11031 | 0.027942 | -0.10985 | -0.027647 | 0.00046221 | 0.00029522 | 0.16424 | 0.16424 | 0.16424 | 1 | 0 | 0.99543 | -0.08764 | 45.1221
31 | 0.072844 | 0.018343 | -0.07277 | -0.018296 | 7.4441e-05 | 4.7421e-05 | 0.10842 | 0.10842 | 0.10842 | 1 | 0 | 0.99888 | -0.021397 | 29.7868
32 | 0.021281 | 0.0053363 | -0.021275 | -0.0053326 | 6.1102e-06 | 3.7019e-06 | 0.031835 | 0.031835 | 0.031835 | 0.99475 | -0.10078 | 0.99444 | -0.1068 | 8.7458
33 | 0.045461 | 0.011407 | -0.045429 | -0.011387 | 3.2329e-05 | 2.045e-05 | 0.068091 | 0.068091 | 0.068091 | 0.99354 | -0.12424 | 0.99277 | -0.13916 | 18.7064
34 | 0.011197 | 0.0028069 | -0.011195 | -0.0028057 | 2.2725e-06 | 1.174e-06 | 0.016749 | 0.016749 | 0.016749 | 0.99481 | -0.099671 | 0.99459 | -0.10393 | 4.6013
35 | 0.013507 | 0.0033858 | -0.013504 | -0.0033845 | 2.3151e-06 | 1.2848e-06 | 0.020191 | 0.020191 | 0.020191 | 0.99543 | -0.08764 | 0.99524 | -0.091238 | 5.5469
36 | 0.084679 | 0.021338 | -0.084613 | -0.021296 | 6.609e-05 | 4.2155e-05 | 0.12662 | 0.12662 | 0.12662 | 0.99543 | -0.08764 | 0.99458 | -0.10397 | 34.7866
37 | 0.01166 | 0.0029232 | -0.011658 | -0.0029221 | 2.0736e-06 | 1.0906e-06 | 0.017431 | 0.017431 | 0.017431 | 0.99543 | -0.08764 | 0.99523 | -0.091372 | 4.7887
38 | 0.059082 | 0.014865 | -0.059035 | -0.014834 | 4.7524e-05 | 3.0201e-05 | 0.088033 | 0.088033 | 0.088033 | 0.99888 | -0.021397 | 0.99801 | -0.038247 | 24.185
39 | 0.013688 | 0.0034311 | -0.013687 | -0.0034308 | 4.8116e-07 | 2.6755e-07 | 0.020391 | 0.020391 | 0.020391 | 0.99888 | -0.021397 | 0.99885 | -0.022135 | 5.6019
40 | 0.005572 | 0.0013965 | -0.0055718 | -0.0013964 | 2.8196e-07 | 4.0051e-08 | 0.0083364 | 0.0083364 | 0.0083364 | 0.99459 | -0.10393 | 0.99454 | -0.10499 | 2.2902
41 | 0.013379 | 0.0033536 | -0.013377 | -0.0033525 | 2.095e-06 | 1.16e-06 | 0.020019 | 0.020019 | 0.020019 | 0.99444 | -0.1068 | 0.99427 | -0.11009 | 5.4998
42 | 0.0045938 | 0.0011513 | -0.0045936 | -0.0011513 | 2.076e-07 | -1.898e-08 | 0.0068756 | 0.0068757 | 0.0068757 | 0.99419 | -0.1117 | 0.99414 | -0.11264 | 1.8889
43 | -0.0045938 | -0.0011513 | 0.0045939 | 0.0011512 | 1.0532e-07 | -9.6353e-09 | 0.0068756 | 0.0068756 | 0.0068756 | 0.99419 | -0.1117 | 0.99421 | -0.11121 | 1.8889
44 | -0.0075481 | -0.0018916 | 0.0075485 | 0.0018918 | 4.045e-07 | 1.4927e-07 | 0.011297 | 0.011297 | 0.011297 | 0.99421 | -0.11121 | 0.99427 | -0.11009 | 3.1036
45 | 0.015541 | 0.003896 | -0.015537 | -0.003894 | 3.5488e-06 | 2.0458e-06 | 0.023294 | 0.023294 | 0.023294 | 0.99277 | -0.13916 | 0.99252 | -0.14396 | 6.3994
46 | 0.0051628 | 0.0012939 | -0.0051628 | -0.0012939 | 7.2678e-08 | 5.1012e-09 | 0.0077586 | 0.0077586 | 0.0077586 | 0.99018 | -0.18901 | 0.99016 | -0.1893 | 2.1315
47 | -0.0051628 | -0.0012939 | 0.0051631 | 0.0012939 | 2.5931e-07 | 1.8189e-08 | 0.0077586 | 0.0077585 | 0.0077586 | 0.99018 | -0.18901 | 0.99023 | -0.18795 | 2.1315
48 | -0.012647 | -0.0031696 | 0.012649 | 0.0031709 | 2.4788e-06 | 1.3509e-06 | 0.019004 | 0.019004 | 0.019004 | 0.99023 | -0.18795 | 0.99044 | -0.18384 | 5.221
49 | -0.053224 | -0.013389 | 0.053269 | 0.013417 | 4.4515e-05 | 2.8248e-05 | 0.079794 | 0.079794 | 0.079794 | 0.99275 | -0.13912 | 0.99366 | -0.12163 | 21.9215
50 | -0.069077 | -0.017379 | 0.069089 | 0.017386 | 1.1092e-05 | 7.0631e-06 | 0.10347 | 0.10347 | 0.10347 | 0.99366 | -0.12163 | 0.99383 | -0.11827 | 28.4252
51 | 0.011658 | 0.0029221 | -0.011657 | -0.0029215 | 1.2284e-06 | 6.4607e-07 | 0.017431 | 0.017431 | 0.017431 | 0.99523 | -0.091372 | 0.99512 | -0.093584 | 4.7887
52 | 0.015477 | 0.0038793 | -0.015476 | -0.0038786 | 1.1551e-06 | 6.647e-07 | 0.023156 | 0.023156 | 0.023156 | 0.99458 | -0.10397 | 0.9945 | -0.10554 | 6.3614
53 | 0.069136 | 0.017416 | -0.069089 | -0.017386 | 4.724e-05 | 3.0081e-05 | 0.10347 | 0.10347 | 0.10347 | 0.99458 | -0.10397 | 0.99383 | -0.11827 | 28.4252
54 | 0.013687 | 0.0034308 | -0.013686 | -0.00343 | 1.5009e-06 | 8.3458e-07 | 0.020391 | 0.020391 | 0.020391 | 0.99885 | -0.022135 | 0.99873 | -0.024437 | 5.6019

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.35431 | 0.089059

## res_load
| p_mw | q_mvar
0 | 0.0047792 | 0.0011978
1 | 0.0034417 | 0.00086256
2 | 0.0047613 | 0.0011933
3 | 0.004471 | 0.0011205
4 | 0.0077644 | 0.0019459
5 | 0.0092116 | 0.0023087
6 | 0.0092444 | 0.0023169
7 | 0.0080112 | 0.0020078
8 | 0.0091341 | 0.0022892
9 | 0.030475 | 0.0076377
10 | 0.011454 | 0.0028705
11 | 0.0099574 | 0.0024956
12 | 0.0094903 | 0.0023785
13 | 0.0163 | 0.0040852
14 | 0.013187 | 0.0033049
15 | 0.0056229 | 0.0014092
16 | 0.0078963 | 0.001979
17 | 0.0045936 | 0.0011513
18 | 0.0029541 | 0.00074038
19 | 0.029888 | 0.0074906
20 | 0.0051628 | 0.0012939
21 | 0.0074838 | 0.0018756
22 | 0.0079779 | 0.0019995
23 | 0.0075559 | 0.0018937
24 | 0.015537 | 0.003894
25 | 0.0058282 | 0.0014607
26 | 0.0055718 | 0.0013964
27 | 0.015809 | 0.003962
28 | 0.013494 | 0.003382
29 | 0.011657 | 0.0029215
30 | 0.013504 | 0.0033845
31 | 0.013686 | 0.00343
32 | 0.0095258 | 0.0023874
33 | 0.015476 | 0.0038786

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1