## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-226_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-226_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-226_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_261-226_0_4_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_261-226_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-226_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-226_0_4_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_261-226_0_4_node_23 | 0.4 | n |  | TRUE
8 | bus_LV_261-226_0_4_node_27 | 0.4 | n |  | TRUE
9 | bus_LV_261-226_0_4_node_32 | 0.4 | n |  | TRUE
10 | bus_LV_261-226_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_261-226_0_4_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_261-226_0_4_node_19 | 0.4 | n |  | TRUE
13 | bus_LV_261-226_0_4_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_261-226_0_4_node_20 | 0.4 | n |  | TRUE
15 | bus_LV_261-226_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_261-226_0_4_node_25 | 0.4 | n |  | TRUE
17 | bus_LV_261-226_0_4_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_261-226_0_4_node_24 | 0.4 | n |  | TRUE
19 | bus_LV_261-226_0_4_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_261-226_0_4_node_30 | 0.4 | n |  | TRUE
21 | bus_LV_261-226_0_4_node_29 | 0.4 | n |  | TRUE
22 | bus_LV_261-226_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_261-226_0_4_node_28 | 0.4 | n |  | TRUE
24 | bus_LV_261-226_0_4_node_26 | 0.4 | n |  | TRUE
25 | bus_LV_261-226_0_4_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_261-226_0_4_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_261-226_0_4_node_33 | 0.4 | n |  | TRUE
28 | bus_LV_261-226_0_4_node_34 | 0.4 | n |  | TRUE
29 | bus_LV_261-226_0_4_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_261-226_0_4_node_31 | 0.4 | n |  | TRUE
31 | bus_LV_261-226_0_4_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_261-226_0_4_node_22 | 0.4 | n |  | TRUE
33 | bus_MV_538_0_node_25 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-226_0_4_load_0 | 0 | 0.088091 | 0.022078 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-226_0_4_load_1 | 1 | 0.0462 | 0.011579 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-226_0_4_load_23 | 7 | 0.029494 | 0.0073918 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-226_0_4_load_27 | 8 | 0.0071437 | 0.0017904 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-226_0_4_load_32 | 9 | 0.033174 | 0.0083142 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-226_0_4_load_19 | 12 | 0.012278 | 0.0030772 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-226_0_4_load_20 | 14 | 0.033463 | 0.0083866 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-226_0_4_load_25 | 16 | 0.020179 | 0.0050574 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-226_0_4_load_24 | 18 | 0.014719 | 0.0036889 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-226_0_4_load_30 | 20 | 0.0074675 | 0.0018715 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-226_0_4_load_29 | 21 | 0.013991 | 0.0035065 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-226_0_4_load_28 | 23 | 0.015708 | 0.0039367 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-226_0_4_load_26 | 24 | 0.0088646 | 0.0022217 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-226_0_4_load_33 | 27 | 0.026212 | 0.0065694 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-226_0_4_load_34 | 28 | 0.011958 | 0.0029969 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-226_0_4_load_31 | 30 | 0.039214 | 0.0098281 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-226_0_4_load_21 | 31 | 0.013604 | 0.0034095 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-226_0_4_load_22 | 32 | 0.013622 | 0.0034141 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 32 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-226_0_4_line_0 |  | 0 | 1 | 0.025078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-226_0_4_line_1 |  | 1 | 2 | 0.02027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-226_0_4_line_2 |  | 2 | 6 | 0.0086099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-226_0_4_line_3 |  | 3 | 4 | 0.0083526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-226_0_4_line_4 |  | 3 | 5 | 0.041055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-226_0_4_line_5 |  | 4 | 7 | 0.0096525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_261-226_0_4_line_6 |  | 4 | 8 | 0.018797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_261-226_0_4_line_7 |  | 5 | 9 | 0.029213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-226_0_4_line_8 |  | 6 | 11 | 0.002309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-226_0_4_line_9 |  | 7 | 31 | 0.017573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_261-226_0_4_line_10 |  | 8 | 22 | 0.018303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_261-226_0_4_line_11 |  | 9 | 30 | 0.024375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-226_0_4_line_12 |  | 10 | 11 | 0.0078567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-226_0_4_line_13 |  | 10 | 12 | 0.015051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-226_0_4_line_14 |  | 11 | 16 | 0.009537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_261-226_0_4_line_15 |  | 13 | 14 | 0.019536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-226_0_4_line_16 |  | 13 | 15 | 0.0087337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-226_0_4_line_17 |  | 15 | 17 | 0.017163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_261-226_0_4_line_18 |  | 15 | 18 | 0.0098668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_261-226_0_4_line_19 |  | 16 | 18 | 0.023243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_261-226_0_4_line_20 |  | 17 | 24 | 0.0064252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-226_0_4_line_21 |  | 17 | 19 | 0.015182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_261-226_0_4_line_22 |  | 19 | 20 | 0.018167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-226_0_4_line_23 |  | 19 | 21 | 0.0079675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_261-226_0_4_line_24 |  | 21 | 23 | 0.020774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_261-226_0_4_line_25 |  | 22 | 23 | 0.011471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_261-226_0_4_line_26 |  | 25 | 26 | 0.006811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-226_0_4_line_27 |  | 25 | 27 | 0.0098592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-226_0_4_line_28 |  | 26 | 28 | 0.044937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-226_0_4_line_29 |  | 27 | 29 | 0.01293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-226_0_4_line_30 |  | 29 | 30 | 0.025176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-226_0_4_line_31 |  | 31 | 32 | 0.018034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-226_0_4_trafo_22 | 0.63 MVA 20/0.4 kV | 33 | 32 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2682604.529 | 1247145.8427 | 2682588.6699 | 1247126.4155
1 | 2682575.8517 | 1247110.7132 | 2682588.6699 | 1247126.4155
2 | 2682569.4116 | 1247116.4277 | 2682570.1612 | 1247115.7599 | 2682572.0197 | 1247114.1179 | 2682575.0638 | 1247111.4139 | 2682575.8517 | 1247110.7132
3 | 2682618.0054 | 1247175.5589 | 2682620.925 | 1247173.1201 | 2682624.44 | 1247170.2336
4 | 2682624.44 | 1247170.2336 | 2682649.8009 | 1247149.4717 | 2682652.7199 | 1247147.0773 | 2682656.2043 | 1247144.2237
5 | 2682618.0054 | 1247175.5589 | 2682611.9303 | 1247168.058
6 | 2682618.0054 | 1247175.5589 | 2682616.5304 | 1247176.7837 | 2682603.498 | 1247187.5119
7 | 2682656.2043 | 1247144.2237 | 2682637.6321 | 1247121.674
8 | 2682567.2125 | 1247117.0309 | 2682568.1936 | 1247116.5553 | 2682569.4116 | 1247116.4277
9 | 2682611.9303 | 1247168.058 | 2682600.8699 | 1247154.4016
10 | 2682589.2388 | 1247198.9644 | 2682590.6026 | 1247198.1272 | 2682603.498 | 1247187.5119
11 | 2682622.1361 | 1247102.8592 | 2682637.6321 | 1247121.674
12 | 2682561.8537 | 1247111.2854 | 2682562.3971 | 1247111.8601 | 2682564.4365 | 1247114.0456 | 2682566.6321 | 1247116.4001 | 2682567.2125 | 1247117.0309
13 | 2682561.8537 | 1247111.2854 | 2682551.3083 | 1247122.0244
14 | 2682567.2125 | 1247117.0309 | 2682566.2889 | 1247117.7185 | 2682560.4549 | 1247123.7419
15 | 2682530.2606 | 1247143.4582 | 2682529.3186 | 1247143.8454 | 2682528.5815 | 1247143.6127 | 2682514.7538 | 1247132.4918
16 | 2682530.2606 | 1247143.4582 | 2682531.1225 | 1247143.9483 | 2682534.0753 | 1247145.6351 | 2682536.9006 | 1247147.2534 | 2682537.8449 | 1247147.7891
17 | 2682537.8449 | 1247147.7891 | 2682538.3657 | 1247148.9083 | 2682549.7371 | 1247160.097
18 | 2682537.8449 | 1247147.7891 | 2682538.2457 | 1247146.6717 | 2682544.2844 | 1247140.4371
19 | 2682544.2844 | 1247140.4371 | 2682560.4549 | 1247123.7419
20 | 2682549.7371 | 1247160.097 | 2682550.671 | 1247159.2094 | 2682554.2099 | 1247155.4861
21 | 2682560.5796 | 1247170.7558 | 2682549.7371 | 1247160.097
22 | 2682560.5796 | 1247170.7558 | 2682561.4377 | 1247169.8893 | 2682570.1874 | 1247161.0491 | 2682573.3748 | 1247157.8244
23 | 2682560.5796 | 1247170.7558 | 2682566.2579 | 1247176.3448
24 | 2682566.2579 | 1247176.3448 | 2682581.0635 | 1247190.9176
25 | 2682589.2388 | 1247198.9644 | 2682581.0635 | 1247190.9176
26 | 2682627.0742 | 1247065.271 | 2682623.6815 | 1247065.3349 | 2682620.4255 | 1247066.4348
27 | 2682620.4255 | 1247066.4348 | 2682613.5354 | 1247073.4867
28 | 2682627.0742 | 1247065.271 | 2682661.6401 | 1247082.6988 | 2682666.9454 | 1247085.9571
29 | 2682606.1306 | 1247083.4259 | 2682605.9711 | 1247081.867 | 2682606.4705 | 1247080.7176 | 2682613.5354 | 1247073.4867
30 | 2682606.1306 | 1247083.4259 | 2682622.1361 | 1247102.8592
31 | 2682600.8699 | 1247154.4016 | 2682589.5195 | 1247140.3872

## bus_geodata
| x | y | coords
0 | 2682604.529 | 1247145.8427
1 | 2682588.6699 | 1247126.4155
2 | 2682575.8516 | 1247110.7132
3 | 2682624.44 | 1247170.2336
4 | 2682618.0054 | 1247175.5589
5 | 2682656.2043 | 1247144.2237
6 | 2682569.4116 | 1247116.4277
7 | 2682611.9303 | 1247168.058
8 | 2682603.498 | 1247187.5119
9 | 2682637.6321 | 1247121.674
10 | 2682561.8537 | 1247111.2854
11 | 2682567.2125 | 1247117.0309
12 | 2682551.3083 | 1247122.0244
13 | 2682530.2606 | 1247143.4582
14 | 2682514.7538 | 1247132.4918
15 | 2682537.8449 | 1247147.7891
16 | 2682560.4549 | 1247123.7419
17 | 2682549.7371 | 1247160.097
18 | 2682544.2844 | 1247140.4371
19 | 2682560.5796 | 1247170.7558
20 | 2682573.3748 | 1247157.8244
21 | 2682566.2579 | 1247176.3448
22 | 2682589.2388 | 1247198.9644
23 | 2682581.0635 | 1247190.9176
24 | 2682554.2099 | 1247155.4861
25 | 2682620.4255 | 1247066.4348
26 | 2682627.0742 | 1247065.271
27 | 2682613.5354 | 1247073.4867
28 | 2682666.9454 | 1247085.9571
29 | 2682606.1306 | 1247083.4259
30 | 2682622.1361 | 1247102.8592
31 | 2682600.8699 | 1247154.4016
32 | 2682589.5195 | 1247140.3872
33 | 2682569.4116 | 1247116.4277

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98173 | -0.35207 | 0.088091 | 0.022078
1 | 0.98377 | -0.3122 | 0.0462 | 0.011579
2 | 0.98628 | -0.2633 | 0 | 0
3 | 0.99491 | -0.096919 | 0 | 0
4 | 0.99576 | -0.080672 | 0 | 0
5 | 0.99074 | -0.17718 | 0 | 0
6 | 0.98735 | -0.24261 | 0 | 0
7 | 0.9966 | -0.064622 | 0.029494 | 0.0073918
8 | 0.9946 | -0.10285 | 0.0071437 | 0.0017904
9 | 0.98776 | -0.23471 | 0.033174 | 0.0083142
10 | 0.98755 | -0.23879 | 0 | 0
11 | 0.98763 | -0.23706 | 0 | 0
12 | 0.98738 | -0.24209 | 0.012278 | 0.0030772
13 | 0.98932 | -0.20454 | 0 | 0
14 | 0.98872 | -0.21619 | 0.033463 | 0.0083866
15 | 0.98959 | -0.19934 | 0 | 0
16 | 0.98828 | -0.22458 | 0.020179 | 0.0050574
17 | 0.99044 | -0.18294 | 0 | 0
18 | 0.98917 | -0.20731 | 0.014719 | 0.0036889
19 | 0.99122 | -0.16786 | 0 | 0
20 | 0.99109 | -0.17026 | 0.0074675 | 0.0018715
21 | 0.99164 | -0.15969 | 0.013991 | 0.0035065
22 | 0.9935 | -0.12391 | 0 | 0
23 | 0.99281 | -0.13714 | 0.015708 | 0.0039367
24 | 0.99038 | -0.18395 | 0.0088646 | 0.0022217
25 | 0.98458 | -0.2967 | 0 | 0
26 | 0.98451 | -0.29816 | 0 | 0
27 | 0.98469 | -0.29458 | 0.026212 | 0.0065694
28 | 0.98401 | -0.30783 | 0.011958 | 0.0029969
29 | 0.98514 | -0.28571 | 0 | 0
30 | 0.98603 | -0.26846 | 0.039214 | 0.0098281
31 | 0.99825 | -0.033204 | 0.013604 | 0.0034095
32 | 1 | 0 | -0.42841 | -0.10889
33 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.088091 | -0.022078 | 0.088259 | 0.022185 | 0.00016766 | 0.00010699 | 0.13352 | 0.13352 | 0.13352 | 0.98173 | -0.35207 | 0.98377 | -0.3122 | 36.6816
1 | -0.13446 | -0.033764 | 0.13477 | 0.033965 | 0.00031448 | 0.00020101 | 0.2034 | 0.2034 | 0.2034 | 0.98377 | -0.3122 | 0.98628 | -0.2633 | 55.8797
2 | -0.13477 | -0.033965 | 0.13491 | 0.03405 | 0.00013358 | 8.5381e-05 | 0.2034 | 0.2034 | 0.2034 | 0.98628 | -0.2633 | 0.98735 | -0.24261 | 55.8796
3 | -0.11147 | -0.028291 | 0.11156 | 0.028346 | 8.7193e-05 | 5.5695e-05 | 0.16685 | 0.16685 | 0.16685 | 0.99491 | -0.096919 | 0.99576 | -0.080672 | 45.8368
4 | 0.11147 | 0.028291 | -0.11104 | -0.028017 | 0.00042857 | 0.00027376 | 0.16685 | 0.16685 | 0.16685 | 0.99491 | -0.096919 | 0.99074 | -0.17718 | 45.8369
5 | -0.38206 | -0.097061 | 0.38235 | 0.09725 | 0.00029545 | 0.00018858 | 0.57139 | 0.57139 | 0.57139 | 0.99576 | -0.080672 | 0.9966 | -0.064622 | 39.2438
6 | 0.2705 | 0.068715 | -0.27021 | -0.068531 | 0.0002884 | 0.0001836 | 0.40454 | 0.40454 | 0.40454 | 0.99576 | -0.080672 | 0.9946 | -0.10285 | 27.7847
7 | 0.11104 | 0.028017 | -0.11074 | -0.027822 | 0.00030496 | 0.0001948 | 0.16685 | 0.16685 | 0.16685 | 0.99074 | -0.17718 | 0.98776 | -0.23471 | 45.8369
8 | -0.13491 | -0.03405 | 0.13494 | 0.034073 | 3.5823e-05 | 2.2897e-05 | 0.2034 | 0.2034 | 0.2034 | 0.98735 | -0.24261 | 0.98763 | -0.23706 | 55.8796
9 | -0.41185 | -0.10464 | 0.41247 | 0.10504 | 0.000624 | 0.00039844 | 0.61543 | 0.61543 | 0.61543 | 0.9966 | -0.064622 | 0.99825 | -0.033204 | 42.2683
10 | 0.26307 | 0.066741 | -0.2628 | -0.066571 | 0.00026618 | 0.0001694 | 0.39386 | 0.39386 | 0.39386 | 0.9946 | -0.10285 | 0.9935 | -0.12391 | 27.0507
11 | 0.077565 | 0.019508 | -0.07744 | -0.019428 | 0.00012485 | 7.9592e-05 | 0.11687 | 0.11687 | 0.11687 | 0.98776 | -0.23471 | 0.98603 | -0.26846 | 32.1076
12 | -0.01228 | -0.0030783 | 0.012281 | 0.0030788 | 1.0088e-06 | 5.4508e-07 | 0.018504 | 0.018504 | 0.018504 | 0.98755 | -0.23879 | 0.98763 | -0.23706 | 5.0834
13 | 0.01228 | 0.0030783 | -0.012278 | -0.0030772 | 1.9325e-06 | 1.0443e-06 | 0.018504 | 0.018504 | 0.018504 | 0.98755 | -0.23879 | 0.98738 | -0.24209 | 5.0835
14 | -0.14722 | -0.037152 | 0.14731 | 0.037208 | 8.8054e-05 | 5.611e-05 | 0.22191 | 0.22191 | 0.22191 | 0.98763 | -0.23706 | 0.98828 | -0.22458 | 30.4815
15 | 0.033482 | 0.0083983 | -0.033463 | -0.0083866 | 1.8581e-05 | 1.1641e-05 | 0.050362 | 0.050362 | 0.050362 | 0.98932 | -0.20454 | 0.98872 | -0.21619 | 13.8357
16 | -0.033482 | -0.0083983 | 0.03349 | 0.0084035 | 8.3068e-06 | 5.2042e-06 | 0.050362 | 0.050362 | 0.050362 | 0.98932 | -0.20454 | 0.98959 | -0.19934 | 13.8356
17 | -0.21591 | -0.054489 | 0.21608 | 0.054597 | 0.00016974 | 0.00010775 | 0.32479 | 0.32479 | 0.32479 | 0.98959 | -0.19934 | 0.99044 | -0.18294 | 22.3071
18 | 0.18242 | 0.046086 | -0.18235 | -0.046042 | 6.9664e-05 | 4.4078e-05 | 0.27443 | 0.27443 | 0.27443 | 0.98959 | -0.19934 | 0.98917 | -0.20731 | 18.8482
19 | -0.16749 | -0.042265 | 0.16763 | 0.042353 | 0.00013869 | 8.757e-05 | 0.25229 | 0.25229 | 0.25229 | 0.98828 | -0.22458 | 0.98917 | -0.20731 | 17.3275
20 | 0.0088651 | 0.0022219 | -0.0088646 | -0.0022217 | 4.2742e-07 | 1.9086e-07 | 0.013319 | 0.013319 | 0.013319 | 0.99044 | -0.18294 | 0.99038 | -0.18395 | 3.659
21 | -0.22494 | -0.056819 | 0.22511 | 0.056922 | 0.00016271 | 0.00010335 | 0.33811 | 0.33811 | 0.33811 | 0.99044 | -0.18294 | 0.99122 | -0.16786 | 23.2218
22 | 0.0074684 | 0.0018718 | -0.0074675 | -0.0018715 | 8.5634e-07 | 3.1392e-07 | 0.011212 | 0.011212 | 0.011212 | 0.99122 | -0.16786 | 0.99109 | -0.17026 | 3.0801
23 | -0.23257 | -0.058794 | 0.23267 | 0.058852 | 9.1147e-05 | 5.7923e-05 | 0.34932 | 0.34932 | 0.34932 | 0.99122 | -0.16786 | 0.99164 | -0.15969 | 23.9918
24 | -0.24666 | -0.062359 | 0.24692 | 0.062528 | 0.00026708 | 0.00016986 | 0.37032 | 0.37032 | 0.37032 | 0.99164 | -0.15969 | 0.99281 | -0.13714 | 25.4338
25 | 0.2628 | 0.066571 | -0.26263 | -0.066465 | 0.00016682 | 0.00010617 | 0.39386 | 0.39386 | 0.39386 | 0.9935 | -0.12391 | 0.99281 | -0.13714 | 27.0507
26 | 0.011964 | 0.0030003 | -0.011963 | -0.0029999 | 8.3512e-07 | 4.4786e-07 | 0.018082 | 0.018082 | 0.018082 | 0.98458 | -0.2967 | 0.98451 | -0.29816 | 4.9677
27 | -0.011964 | -0.0030003 | 0.011965 | 0.0030009 | 1.2089e-06 | 6.4827e-07 | 0.018082 | 0.018082 | 0.018082 | 0.98458 | -0.2967 | 0.98469 | -0.29458 | 4.9676
28 | 0.011963 | 0.0029999 | -0.011958 | -0.0029969 | 5.5099e-06 | 2.9552e-06 | 0.018082 | 0.018082 | 0.018082 | 0.98451 | -0.29816 | 0.98401 | -0.30783 | 4.9677
29 | -0.038178 | -0.0095704 | 0.038194 | 0.0095806 | 1.6139e-05 | 1.0164e-05 | 0.057693 | 0.057693 | 0.057693 | 0.98469 | -0.29458 | 0.98514 | -0.28571 | 15.8498
30 | -0.038194 | -0.0095806 | 0.038225 | 0.0096003 | 3.1424e-05 | 1.9791e-05 | 0.057693 | 0.057693 | 0.057693 | 0.98514 | -0.28571 | 0.98603 | -0.26846 | 15.8497
31 | -0.42607 | -0.10845 | 0.42676 | 0.10889 | 0.00068325 | 0.00043634 | 0.6357 | 0.6357 | 0.6357 | 0.99825 | -0.033204 | 1 | 0 | 43.661

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.44203 | 0.1123

## res_load
| p_mw | q_mvar
0 | 0.088091 | 0.022078
1 | 0.0462 | 0.011579
2 | 0.029494 | 0.0073918
3 | 0.0071437 | 0.0017904
4 | 0.033174 | 0.0083142
5 | 0.012278 | 0.0030772
6 | 0.033463 | 0.0083866
7 | 0.020179 | 0.0050574
8 | 0.014719 | 0.0036889
9 | 0.0074675 | 0.0018715
10 | 0.013991 | 0.0035065
11 | 0.015708 | 0.0039367
12 | 0.0088646 | 0.0022217
13 | 0.026212 | 0.0065694
14 | 0.011958 | 0.0029969
15 | 0.039214 | 0.0098281
16 | 0.013604 | 0.0034095
17 | 0.013622 | 0.0034141

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1