## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-240_1_2_node_24 | 0.4 | n |  | TRUE
1 | bus_LV_261-240_1_2_node_25 | 0.4 | n |  | TRUE
2 | bus_LV_261-240_1_2_node_26 | 0.4 | n |  | TRUE
3 | bus_LV_261-240_1_2_node_28 | 0.4 | n |  | TRUE
4 | bus_LV_261-240_1_2_node_29 | 0.4 | n |  | TRUE
5 | bus_LV_261-240_1_2_node_34 | 0.4 | n |  | TRUE
6 | bus_LV_261-240_1_2_node_30 | 0.4 | n |  | TRUE
7 | bus_LV_261-240_1_2_node_31 | 0.4 | n |  | TRUE
8 | bus_LV_261-240_1_2_node_32 | 0.4 | n |  | TRUE
9 | bus_LV_261-240_1_2_node_33 | 0.4 | n |  | TRUE
10 | bus_LV_261-240_1_2_node_35 | 0.4 | n |  | TRUE
11 | bus_LV_261-240_1_2_node_36 | 0.4 | n |  | TRUE
12 | bus_LV_261-240_1_2_node_43 | 0.4 | n |  | TRUE
13 | bus_LV_261-240_1_2_node_72 | 0.4 | n |  | TRUE
14 | bus_LV_261-240_1_2_node_38 | 0.4 | n |  | TRUE
15 | bus_LV_261-240_1_2_node_37 | 0.4 | n |  | TRUE
16 | bus_LV_261-240_1_2_node_39 | 0.4 | n |  | TRUE
17 | bus_LV_261-240_1_2_node_41 | 0.4 | n |  | TRUE
18 | bus_LV_261-240_1_2_node_40 | 0.4 | n |  | TRUE
19 | bus_LV_261-240_1_2_node_45 | 0.4 | n |  | TRUE
20 | bus_LV_261-240_1_2_node_50 | 0.4 | n |  | TRUE
21 | bus_LV_261-240_1_2_node_78 | 0.4 | n |  | TRUE
22 | bus_LV_261-240_1_2_node_42 | 0.4 | n |  | TRUE
23 | bus_LV_261-240_1_2_node_44 | 0.4 | n |  | TRUE
24 | bus_LV_261-240_1_2_node_51 | 0.4 | n |  | TRUE
25 | bus_LV_261-240_1_2_node_64 | 0.4 | n |  | TRUE
26 | bus_LV_261-240_1_2_node_74 | 0.4 | n |  | TRUE
27 | bus_LV_261-240_1_2_node_73 | 0.4 | n |  | TRUE
28 | bus_LV_261-240_1_2_node_76 | 0.4 | n |  | TRUE
29 | bus_LV_261-240_1_2_node_75 | 0.4 | n |  | TRUE
30 | bus_LV_261-240_1_2_node_80 | 0.4 | n |  | TRUE
31 | bus_LV_261-240_1_2_node_81 | 0.4 | n |  | TRUE
32 | bus_LV_261-240_1_2_node_82 | 0.4 | n |  | TRUE
33 | bus_LV_261-240_1_2_node_83 | 0.4 | n |  | TRUE
34 | bus_LV_261-240_1_2_node_84 | 0.4 | n |  | TRUE
35 | bus_LV_261-240_1_2_node_85 | 0.4 | n |  | TRUE
36 | bus_MV_524_0_node_40 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-240_1_2_load_24 | 0 | 0.0045628 | 0.0011436 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-240_1_2_load_25 | 1 | 0.0065512 | 0.0016419 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-240_1_2_load_28 | 3 | 0.0056503 | 0.0014161 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-240_1_2_load_29 | 4 | 0.0057199 | 0.0014335 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-240_1_2_load_30 | 6 | 0.0056291 | 0.0014108 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-240_1_2_load_36 | 11 | 0.0057278 | 0.0014355 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-240_1_2_load_43 | 12 | 0.02339 | 0.0058622 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-240_1_2_load_38 | 14 | 0.0058666 | 0.0014703 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-240_1_2_load_37 | 15 | 0.0058057 | 0.001455 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-240_1_2_load_45 | 19 | 0.0020552 | 0.00051507 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-240_1_2_load_50 | 20 | 0.025092 | 0.0062886 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-240_1_2_load_78 | 21 | 0.0029828 | 0.00074756 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-240_1_2_load_42 | 22 | 0.028563 | 0.0071585 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-240_1_2_load_51 | 24 | 0.022379 | 0.0056088 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-240_1_2_load_74 | 26 | 0.0044417 | 0.0011132 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-240_1_2_load_73 | 27 | 0.0038835 | 0.00097329 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-240_1_2_load_80 | 30 | 0.011441 | 0.0028673 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-240_1_2_load_82 | 32 | 0.0093633 | 0.0023467 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-240_1_2_load_84 | 34 | 0.013816 | 0.0034627 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-240_1_2_load_85 | 35 | 0.025392 | 0.0063638 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-240_1_2_line_0 |  | 0 | 1 | 0.025742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-240_1_2_line_1 |  | 0 | 2 | 0.013331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-240_1_2_line_2 |  | 2 | 3 | 0.012554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-240_1_2_line_3 |  | 2 | 4 | 0.02096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-240_1_2_line_4 |  | 3 | 5 | 0.018772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-240_1_2_line_5 |  | 5 | 13 | 0.00662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-240_1_2_line_6 |  | 5 | 7 | 0.005992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-240_1_2_line_7 |  | 6 | 7 | 0.033807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-240_1_2_line_8 |  | 6 | 8 | 0.019974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-240_1_2_line_9 |  | 7 | 9 | 0.032314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-240_1_2_line_10 |  | 8 | 10 | 0.020152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-240_1_2_line_11 |  | 8 | 11 | 0.021939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-240_1_2_line_12 |  | 9 | 12 | 0.030432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-240_1_2_line_13 |  | 10 | 14 | 0.0077875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-240_1_2_line_14 |  | 11 | 15 | 0.026724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-240_1_2_line_15 |  | 12 | 22 | 0.017842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-240_1_2_line_16 |  | 13 | 28 | 0.054754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-240_1_2_line_17 |  | 13 | 26 | 0.028864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-240_1_2_line_18 |  | 14 | 16 | 0.0021942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-240_1_2_line_19 |  | 16 | 17 | 0.042965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-240_1_2_line_20 |  | 17 | 21 | 0.035577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-240_1_2_line_21 |  | 18 | 19 | 0.011939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-240_1_2_line_22 |  | 18 | 20 | 0.0048786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-240_1_2_line_23 |  | 19 | 23 | 0.0047888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-240_1_2_line_24 |  | 20 | 24 | 0.047386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-240_1_2_line_25 |  | 22 | 23 | 0.035488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-240_1_2_line_26 |  | 25 | 26 | 0.025464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-240_1_2_line_27 |  | 25 | 27 | 0.016206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-240_1_2_line_28 |  | 28 | 32 | 0.007271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-240_1_2_line_29 |  | 28 | 29 | 0.02584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-240_1_2_line_30 |  | 29 | 30 | 0.004443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-240_1_2_line_31 |  | 29 | 31 | 0.026887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-240_1_2_line_32 |  | 31 | 33 | 0.013417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-240_1_2_line_33 |  | 31 | 34 | 0.005329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-240_1_2_line_34 |  | 33 | 35 | 0.008333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-240_1_2_trafo_43 | 0.63 MVA 20/0.4 kV | 36 | 12 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2680204.4257 | 1252680.6346 | 2680190.6601 | 1252689.3912 | 2680183.373 | 1252683.4109
1 | 2680173.0678 | 1252674.9535 | 2680183.373 | 1252683.4109
2 | 2680173.0678 | 1252674.9535 | 2680162.6303 | 1252681.9284
3 | 2680173.0678 | 1252674.9535 | 2680190.4948 | 1252663.3084
4 | 2680147.0222 | 1252692.3586 | 2680162.6303 | 1252681.9284
5 | 2680151.3006 | 1252697.4202 | 2680147.0222 | 1252692.3586
6 | 2680143.4651 | 1252687.5291 | 2680147.0222 | 1252692.3586
7 | 2680143.4651 | 1252687.5291 | 2680129.7478 | 1252668.9186 | 2680124.6587 | 1252659.5209
8 | 2680115.1473 | 1252641.9567 | 2680124.6587 | 1252659.5209
9 | 2680143.4651 | 1252687.5291 | 2680117.5214 | 1252706.8927
10 | 2680100.6049 | 1252627.9831 | 2680108.3079 | 1252634.8478 | 2680115.1473 | 1252641.9567
11 | 2680115.1473 | 1252641.9567 | 2680133.3657 | 1252629.7331
12 | 2680117.5214 | 1252706.8927 | 2680102.686 | 1252687.2553 | 2680098.9386 | 1252690.3514 | 2680098.3638 | 1252689.5828
13 | 2680100.6049 | 1252627.9831 | 2680094.4878 | 1252623.1637
14 | 2680133.3657 | 1252629.7331 | 2680155.5575 | 1252614.8435
15 | 2680095.279 | 1252675.9619 | 2680095.5585 | 1252676.3397 | 2680091.385 | 1252680.2529 | 2680098.3638 | 1252689.5828
16 | 2680151.3006 | 1252697.4202 | 2680134.9153 | 1252704.2037 | 2680130.6212 | 1252707.5481 | 2680127.4721 | 1252712.1645 | 2680126.2134 | 1252719.2972 | 2680126.3219 | 1252729.6842 | 2680134.6148 | 1252728.64
17 | 2680151.3006 | 1252697.4202 | 2680153.7665 | 1252700.3446 | 2680168.8514 | 1252720.329
18 | 2680092.7643 | 1252621.8058 | 2680094.4878 | 1252623.1637
19 | 2680092.7643 | 1252621.8058 | 2680077.4637 | 1252609.7567 | 2680070.1598 | 1252604.0649 | 2680058.3834 | 1252595.9331
20 | 2680082.877 | 1252580.5749 | 2680078.3907 | 1252575.8107 | 2680069.0342 | 1252581.8221 | 2680063.2451 | 1252586.892 | 2680058.3834 | 1252595.9331
21 | 2680062.3332 | 1252656.0089 | 2680064.6217 | 1252659.22 | 2680064.7075 | 1252662.9239 | 2680067.0593 | 1252666.5134
22 | 2680062.3332 | 1252656.0089 | 2680059.5041 | 1252652.0344
23 | 2680069.6838 | 1252670.519 | 2680067.0593 | 1252666.5134
24 | 2680059.5041 | 1252652.0344 | 2680064.0905 | 1252647.7154 | 2680063.9806 | 1252645.8013 | 2680069.5347 | 1252641.362 | 2680067.7724 | 1252639.4145 | 2680060.4283 | 1252644.5191 | 2680049.8128 | 1252626.9959
25 | 2680069.6838 | 1252670.519 | 2680074.042 | 1252673.5913 | 2680086.6575 | 1252664.3104 | 2680095.279 | 1252675.9619
26 | 2680184.1926 | 1252740.6529 | 2680168.8514 | 1252720.329
27 | 2680184.1926 | 1252740.6529 | 2680198.2731 | 1252732.6298
28 | 2680134.6148 | 1252728.64 | 2680141.8494 | 1252727.726
29 | 2680112.1762 | 1252739.9561 | 2680126.3219 | 1252729.6842 | 2680134.6148 | 1252728.64
30 | 2680112.1762 | 1252739.9561 | 2680107.9898 | 1252741.4784
31 | 2680112.1762 | 1252739.9561 | 2680122.3443 | 1252764.8566
32 | 2680122.3443 | 1252764.8566 | 2680128.5413 | 1252762.5386 | 2680135.2316 | 1252761.1281
33 | 2680117.7271 | 1252767.5406 | 2680122.3443 | 1252764.8566
34 | 2680135.2316 | 1252761.1281 | 2680143.5707 | 1252760.5738

## bus_geodata
| x | y | coords
0 | 2680183.373 | 1252683.4109
1 | 2680204.4257 | 1252680.6346
2 | 2680173.0678 | 1252674.9535
3 | 2680162.6303 | 1252681.9284
4 | 2680190.4948 | 1252663.3084
5 | 2680147.0222 | 1252692.3586
6 | 2680124.6587 | 1252659.5209
7 | 2680143.4651 | 1252687.5291
8 | 2680115.1473 | 1252641.9567
9 | 2680117.5214 | 1252706.8927
10 | 2680100.6049 | 1252627.9831
11 | 2680133.3657 | 1252629.7331
12 | 2680098.3638 | 1252689.5828
13 | 2680151.3006 | 1252697.4202
14 | 2680094.4878 | 1252623.1637
15 | 2680155.5575 | 1252614.8435
16 | 2680092.7643 | 1252621.8058
17 | 2680058.3834 | 1252595.9331
18 | 2680062.3332 | 1252656.0089
19 | 2680067.0593 | 1252666.5134
20 | 2680059.5041 | 1252652.0344
21 | 2680082.877 | 1252580.5749
22 | 2680095.279 | 1252675.9619
23 | 2680069.6838 | 1252670.519
24 | 2680049.8128 | 1252626.9959
25 | 2680184.1926 | 1252740.6529
26 | 2680168.8514 | 1252720.329
27 | 2680198.2731 | 1252732.6298
28 | 2680134.6148 | 1252728.64
29 | 2680112.1762 | 1252739.9561
30 | 2680107.9898 | 1252741.4784
31 | 2680122.3443 | 1252764.8566
32 | 2680141.8494 | 1252727.726
33 | 2680135.2316 | 1252761.1281
34 | 2680117.7271 | 1252767.5406
35 | 2680143.5707 | 1252760.5738
36 | 2680117.5214 | 1252706.8927

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99207 | -0.15211 | 0.0045628 | 0.0011436
1 | 0.99191 | -0.1551 | 0.0065512 | 0.0016419
2 | 0.9922 | -0.14949 | 0 | 0
3 | 0.9924 | -0.14574 | 0.0056503 | 0.0014161
4 | 0.99209 | -0.15161 | 0.0057199 | 0.0014335
5 | 0.99278 | -0.13828 | 0 | 0
6 | 0.99248 | -0.14421 | 0.0056291 | 0.0014108
7 | 0.99328 | -0.12866 | 0 | 0
8 | 0.9921 | -0.15142 | 0 | 0
9 | 0.99674 | -0.062183 | 0 | 0
10 | 0.99194 | -0.15458 | 0 | 0
11 | 0.99187 | -0.1559 | 0.0057278 | 0.0014355
12 | 1 | 0 | -0.19791 | -0.049701
13 | 0.99237 | -0.14628 | 0 | 0
14 | 0.99188 | -0.1558 | 0.0058666 | 0.0014703
15 | 0.99173 | -0.15865 | 0.0058057 | 0.001455
16 | 0.99187 | -0.15591 | 0 | 0
17 | 0.99175 | -0.15819 | 0 | 0
18 | 0.9964 | -0.069183 | 0 | 0
19 | 0.99692 | -0.059238 | 0.0020552 | 0.00051507
20 | 0.99619 | -0.07325 | 0.025092 | 0.0062886
21 | 0.99166 | -0.16007 | 0.0029828 | 0.00074756
22 | 0.99873 | -0.024316 | 0.028563 | 0.0071585
23 | 0.99713 | -0.055079 | 0 | 0
24 | 0.99522 | -0.091893 | 0.022379 | 0.0056088
25 | 0.99206 | -0.15229 | 0 | 0
26 | 0.99215 | -0.15054 | 0.0044417 | 0.0011132
27 | 0.992 | -0.1534 | 0.0038835 | 0.00097329
28 | 0.98935 | -0.20462 | 0 | 0
29 | 0.98815 | -0.22795 | 0 | 0
30 | 0.9881 | -0.22886 | 0.011441 | 0.0028673
31 | 0.98718 | -0.24679 | 0 | 0
32 | 0.98929 | -0.20583 | 0.0093633 | 0.0023467
33 | 0.98686 | -0.25288 | 0 | 0
34 | 0.98711 | -0.24811 | 0.013816 | 0.0034627
35 | 0.98667 | -0.25667 | 0.025392 | 0.0063638
36 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0065522 | 0.0016422 | -0.0065512 | -0.0016419 | 9.3234e-07 | 2.6438e-07 | 0.0098277 | 0.0098278 | 0.0098278 | 0.99207 | -0.15211 | 0.99191 | -0.1551 | 2.7
1 | -0.011115 | -0.0027857 | 0.011116 | 0.0027864 | 1.3895e-06 | 7.1712e-07 | 0.016672 | 0.016672 | 0.016672 | 0.99207 | -0.15211 | 0.9922 | -0.14949 | 4.5801
2 | -0.016837 | -0.0042201 | 0.01684 | 0.0042218 | 3.0015e-06 | 1.7588e-06 | 0.025251 | 0.02525 | 0.025251 | 0.9922 | -0.14949 | 0.9924 | -0.14574 | 6.937
3 | 0.0057204 | 0.0014336 | -0.0057199 | -0.0014335 | 5.7849e-07 | 9.9558e-08 | 0.008579 | 0.0085791 | 0.0085791 | 0.9922 | -0.14949 | 0.99209 | -0.15161 | 2.3569
4 | -0.02249 | -0.0056379 | 0.022498 | 0.0056428 | 8.0056e-06 | 4.8809e-06 | 0.033723 | 0.033723 | 0.033723 | 0.9924 | -0.14574 | 0.99278 | -0.13828 | 9.2645
5 | 0.068639 | 0.017317 | -0.068613 | -0.017301 | 2.6296e-05 | 1.6744e-05 | 0.10292 | 0.10292 | 0.10292 | 0.99278 | -0.13828 | 0.99237 | -0.14628 | 28.2747
6 | -0.091137 | -0.02296 | 0.091179 | 0.022987 | 4.1954e-05 | 2.6773e-05 | 0.13664 | 0.13664 | 0.13664 | 0.99278 | -0.13828 | 0.99328 | -0.12866 | 37.5391
7 | -0.026025 | -0.006525 | 0.026044 | 0.006537 | 1.9302e-05 | 1.1916e-05 | 0.03902 | 0.039019 | 0.03902 | 0.99248 | -0.14421 | 0.99328 | -0.12866 | 10.7197
8 | 0.020396 | 0.0051143 | -0.020389 | -0.00511 | 7.0044e-06 | 4.2248e-06 | 0.03058 | 0.03058 | 0.03058 | 0.99248 | -0.14421 | 0.9921 | -0.15142 | 8.4011
9 | -0.11722 | -0.029524 | 0.1176 | 0.029763 | 0.00037392 | 0.00023889 | 0.17566 | 0.17566 | 0.17566 | 0.99328 | -0.12866 | 0.99674 | -0.062183 | 48.2587
10 | 0.0088519 | 0.002218 | -0.0088505 | -0.0022174 | 1.332e-06 | 5.9232e-07 | 0.013276 | 0.013276 | 0.013276 | 0.9921 | -0.15142 | 0.99194 | -0.15458 | 3.6474
11 | 0.011537 | 0.002892 | -0.011534 | -0.0028907 | 2.4634e-06 | 1.2933e-06 | 0.017304 | 0.017304 | 0.017304 | 0.9921 | -0.15142 | 0.99187 | -0.1559 | 4.7538
12 | -0.1176 | -0.029763 | 0.11795 | 0.029988 | 0.00035214 | 0.00022497 | 0.17566 | 0.17566 | 0.17566 | 0.99674 | -0.062183 | 1 | 0 | 48.2587
13 | 0.0088505 | 0.0022174 | -0.00885 | -0.0022172 | 5.1475e-07 | 2.2892e-07 | 0.013276 | 0.013277 | 0.013277 | 0.99194 | -0.15458 | 0.99188 | -0.1558 | 3.6474
14 | 0.0058064 | 0.0014552 | -0.0058057 | -0.001455 | 7.6043e-07 | 1.418e-07 | 0.0087109 | 0.008711 | 0.008711 | 0.99187 | -0.1559 | 0.99173 | -0.15865 | 2.3931
15 | 0.078315 | 0.019714 | -0.078224 | -0.019656 | 9.0909e-05 | 5.7948e-05 | 0.11656 | 0.11656 | 0.11656 | 1 | 0 | 0.99873 | -0.024316 | 32.023
16 | 0.060286 | 0.015214 | -0.060118 | -0.015107 | 0.00016792 | 0.00010676 | 0.090433 | 0.090433 | 0.090433 | 0.99237 | -0.14628 | 0.98935 | -0.20462 | 24.8443
17 | 0.0083274 | 0.002087 | -0.0083257 | -0.0020863 | 1.6876e-06 | 7.0726e-07 | 0.012487 | 0.012487 | 0.012487 | 0.99237 | -0.14628 | 0.99215 | -0.15054 | 3.4304
18 | 0.0029834 | 0.00074691 | -0.0029834 | -0.00074693 | 1.6481e-08 | -1.7772e-08 | 0.0044754 | 0.0044755 | 0.0044755 | 0.99188 | -0.1558 | 0.99187 | -0.15591 | 1.2295
19 | 0.0029834 | 0.00074693 | -0.0029831 | -0.00074728 | 3.2273e-07 | -3.4793e-07 | 0.0044755 | 0.0044757 | 0.0044757 | 0.99187 | -0.15591 | 0.99175 | -0.15819 | 1.2296
20 | 0.0029831 | 0.00074728 | -0.0029828 | -0.00074756 | 2.6726e-07 | -2.8799e-07 | 0.0044757 | 0.0044758 | 0.0044758 | 0.99175 | -0.15819 | 0.99166 | -0.16007 | 1.2296
21 | -0.0475 | -0.011915 | 0.047523 | 0.01193 | 2.2532e-05 | 1.4265e-05 | 0.07094 | 0.07094 | 0.07094 | 0.9964 | -0.069183 | 0.99692 | -0.059238 | 19.4891
22 | 0.0475 | 0.011915 | -0.047491 | -0.01191 | 9.2069e-06 | 5.8289e-06 | 0.07094 | 0.070941 | 0.070941 | 0.9964 | -0.069183 | 0.99619 | -0.07325 | 19.4892
23 | -0.049578 | -0.012445 | 0.049588 | 0.012451 | 9.8359e-06 | 6.2326e-06 | 0.074008 | 0.074008 | 0.074008 | 0.99692 | -0.059238 | 0.99713 | -0.055079 | 20.3319
24 | 0.022399 | 0.0056209 | -0.022379 | -0.0056088 | 1.9895e-05 | 1.2116e-05 | 0.03346 | 0.033461 | 0.033461 | 0.99619 | -0.07325 | 0.99522 | -0.091893 | 9.1925
25 | 0.049661 | 0.012497 | -0.049588 | -0.012451 | 7.2891e-05 | 4.6186e-05 | 0.074008 | 0.074008 | 0.074008 | 0.99873 | -0.024316 | 0.99713 | -0.055079 | 20.3319
26 | -0.0038837 | -0.00097321 | 0.003884 | 0.00097309 | 3.2402e-07 | -1.2144e-07 | 0.0058252 | 0.0058251 | 0.0058252 | 0.99206 | -0.15229 | 0.99215 | -0.15054 | 1.6003
27 | 0.0038837 | 0.00097321 | -0.0038835 | -0.00097329 | 2.0622e-07 | -7.7253e-08 | 0.0058252 | 0.0058253 | 0.0058253 | 0.99206 | -0.15229 | 0.992 | -0.1534 | 1.6003
28 | 0.0093638 | 0.0023469 | -0.0093633 | -0.0023467 | 5.4082e-07 | 2.5276e-07 | 0.014084 | 0.014084 | 0.014084 | 0.98935 | -0.20462 | 0.98929 | -0.20583 | 3.8691
29 | 0.050754 | 0.01276 | -0.050697 | -0.012724 | 5.6486e-05 | 3.582e-05 | 0.07635 | 0.07635 | 0.07635 | 0.98935 | -0.20462 | 0.98815 | -0.22795 | 20.9753
30 | 0.011441 | 0.0028675 | -0.011441 | -0.0028673 | 4.9456e-07 | 2.5961e-07 | 0.017229 | 0.017229 | 0.017229 | 0.98815 | -0.22795 | 0.9881 | -0.22886 | 4.7332
31 | 0.039256 | 0.0098566 | -0.039221 | -0.0098344 | 3.5242e-05 | 2.2211e-05 | 0.059121 | 0.059121 | 0.059121 | 0.98815 | -0.22795 | 0.98718 | -0.24679 | 16.2421
32 | 0.025404 | 0.0063712 | -0.025396 | -0.0063666 | 7.3782e-06 | 4.5505e-06 | 0.038294 | 0.038294 | 0.038294 | 0.98718 | -0.24679 | 0.98686 | -0.25288 | 10.5203
33 | 0.013817 | 0.0034632 | -0.013816 | -0.0034627 | 8.6685e-07 | 4.8666e-07 | 0.020827 | 0.020827 | 0.020827 | 0.98718 | -0.24679 | 0.98711 | -0.24811 | 5.7218
34 | 0.025396 | 0.0063666 | -0.025392 | -0.0063638 | 4.5824e-06 | 2.8263e-06 | 0.038294 | 0.038294 | 0.038294 | 0.98686 | -0.25288 | 0.98667 | -0.25667 | 10.5203

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.2213 | 0.055564

## res_load
| p_mw | q_mvar
0 | 0.0045628 | 0.0011436
1 | 0.0065512 | 0.0016419
2 | 0.0056503 | 0.0014161
3 | 0.0057199 | 0.0014335
4 | 0.0056291 | 0.0014108
5 | 0.0057278 | 0.0014355
6 | 0.02339 | 0.0058622
7 | 0.0058666 | 0.0014703
8 | 0.0058057 | 0.001455
9 | 0.0020552 | 0.00051507
10 | 0.025092 | 0.0062886
11 | 0.0029828 | 0.00074756
12 | 0.028563 | 0.0071585
13 | 0.022379 | 0.0056088
14 | 0.0044417 | 0.0011132
15 | 0.0038835 | 0.00097329
16 | 0.011441 | 0.0028673
17 | 0.0093633 | 0.0023467
18 | 0.013816 | 0.0034627
19 | 0.025392 | 0.0063638

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1