## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-243_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-243_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-243_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-243_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-243_0_6_node_8 | 0.4 | n |  | TRUE
5 | bus_LV_261-243_0_6_node_36 | 0.4 | n |  | TRUE
6 | bus_LV_261-243_0_6_node_35 | 0.4 | n |  | TRUE
7 | bus_LV_261-243_0_6_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_261-243_0_6_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_261-243_0_6_node_87 | 0.4 | n |  | TRUE
10 | bus_LV_261-243_0_6_node_85 | 0.4 | n |  | TRUE
11 | bus_LV_261-243_0_6_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_261-243_0_6_node_46 | 0.4 | n |  | TRUE
13 | bus_LV_261-243_0_6_node_45 | 0.4 | n |  | TRUE
14 | bus_LV_261-243_0_6_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_261-243_0_6_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_261-243_0_6_node_44 | 0.4 | n |  | TRUE
17 | bus_LV_261-243_0_6_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_261-243_0_6_node_80 | 0.4 | n |  | TRUE
19 | bus_LV_261-243_0_6_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_261-243_0_6_node_42 | 0.4 | n |  | TRUE
21 | bus_LV_261-243_0_6_node_43 | 0.4 | n |  | TRUE
22 | bus_LV_261-243_0_6_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_261-243_0_6_node_72 | 0.4 | n |  | TRUE
24 | bus_LV_261-243_0_6_node_81 | 0.4 | n |  | TRUE
25 | bus_LV_261-243_0_6_node_84 | 0.4 | n |  | TRUE
26 | bus_LV_261-243_0_6_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_261-243_0_6_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_261-243_0_6_node_48 | 0.4 | n |  | TRUE
29 | bus_LV_261-243_0_6_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_261-243_0_6_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_261-243_0_6_node_57 | 0.4 | n |  | TRUE
32 | bus_LV_261-243_0_6_node_17 | 0.4 | n |  | TRUE
33 | bus_LV_261-243_0_6_node_51 | 0.4 | n |  | TRUE
34 | bus_LV_261-243_0_6_node_50 | 0.4 | n |  | TRUE
35 | bus_LV_261-243_0_6_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_261-243_0_6_node_59 | 0.4 | n |  | TRUE
37 | bus_LV_261-243_0_6_node_19 | 0.4 | n |  | TRUE
38 | bus_LV_261-243_0_6_node_28 | 0.4 | n |  | TRUE
39 | bus_LV_261-243_0_6_node_79 | 0.4 | n |  | TRUE
40 | bus_LV_261-243_0_6_node_98 | 0.4 | n |  | TRUE
41 | bus_LV_261-243_0_6_node_27 | 0.4 | n |  | TRUE
42 | bus_LV_261-243_0_6_node_61 | 0.4 | n |  | TRUE
43 | bus_LV_261-243_0_6_node_22 | 0.4 | n |  | TRUE
44 | bus_LV_261-243_0_6_node_49 | 0.4 | n |  | TRUE
45 | bus_LV_261-243_0_6_node_89 | 0.4 | n |  | TRUE
46 | bus_LV_261-243_0_6_node_90 | 0.4 | n |  | TRUE
47 | bus_LV_261-243_0_6_node_24 | 0.4 | n |  | TRUE
48 | bus_LV_261-243_0_6_node_26 | 0.4 | n |  | TRUE
49 | bus_LV_261-243_0_6_node_25 | 0.4 | n |  | TRUE
50 | bus_LV_261-243_0_6_node_95 | 0.4 | n |  | TRUE
51 | bus_LV_261-243_0_6_node_30 | 0.4 | n |  | TRUE
52 | bus_LV_261-243_0_6_node_94 | 0.4 | n |  | TRUE
53 | bus_LV_261-243_0_6_node_55 | 0.4 | n |  | TRUE
54 | bus_LV_261-243_0_6_node_64 | 0.4 | n |  | TRUE
55 | bus_LV_261-243_0_6_node_29 | 0.4 | n |  | TRUE
56 | bus_LV_261-243_0_6_node_60 | 0.4 | n |  | TRUE
57 | bus_LV_261-243_0_6_node_58 | 0.4 | n |  | TRUE
58 | bus_LV_261-243_0_6_node_65 | 0.4 | n |  | TRUE
59 | bus_LV_261-243_0_6_node_31 | 0.4 | n |  | TRUE
60 | bus_LV_261-243_0_6_node_37 | 0.4 | n |  | TRUE
61 | bus_LV_261-243_0_6_node_66 | 0.4 | n |  | TRUE
62 | bus_LV_261-243_0_6_node_32 | 0.4 | n |  | TRUE
63 | bus_LV_261-243_0_6_node_67 | 0.4 | n |  | TRUE
64 | bus_LV_261-243_0_6_node_33 | 0.4 | n |  | TRUE
65 | bus_LV_261-243_0_6_node_83 | 0.4 | n |  | TRUE
66 | bus_LV_261-243_0_6_node_82 | 0.4 | n |  | TRUE
67 | bus_LV_261-243_0_6_node_78 | 0.4 | n |  | TRUE
68 | bus_LV_261-243_0_6_node_54 | 0.4 | n |  | TRUE
69 | bus_LV_261-243_0_6_node_38 | 0.4 | n |  | TRUE
70 | bus_LV_261-243_0_6_node_52 | 0.4 | n |  | TRUE
71 | bus_LV_261-243_0_6_node_91 | 0.4 | n |  | TRUE
72 | bus_LV_261-243_0_6_node_88 | 0.4 | n |  | TRUE
73 | bus_LV_261-243_0_6_node_86 | 0.4 | n |  | TRUE
74 | bus_LV_261-243_0_6_node_47 | 0.4 | n |  | TRUE
75 | bus_LV_261-243_0_6_node_76 | 0.4 | n |  | TRUE
76 | bus_LV_261-243_0_6_node_97 | 0.4 | n |  | TRUE
77 | bus_LV_261-243_0_6_node_56 | 0.4 | n |  | TRUE
78 | bus_LV_261-243_0_6_node_99 | 0.4 | n |  | TRUE
79 | bus_LV_261-243_0_6_node_62 | 0.4 | n |  | TRUE
80 | bus_LV_261-243_0_6_node_63 | 0.4 | n |  | TRUE
81 | bus_LV_261-243_0_6_node_92 | 0.4 | n |  | TRUE
82 | bus_LV_261-243_0_6_node_93 | 0.4 | n |  | TRUE
83 | bus_LV_261-243_0_6_node_96 | 0.4 | n |  | TRUE
84 | bus_LV_261-243_0_6_node_68 | 0.4 | n |  | TRUE
85 | bus_LV_261-243_0_6_node_71 | 0.4 | n |  | TRUE
86 | bus_LV_261-243_0_6_node_73 | 0.4 | n |  | TRUE
87 | bus_LV_261-243_0_6_node_69 | 0.4 | n |  | TRUE
88 | bus_LV_261-243_0_6_node_53 | 0.4 | n |  | TRUE
89 | bus_LV_261-243_0_6_node_75 | 0.4 | n |  | TRUE
90 | bus_LV_261-243_0_6_node_74 | 0.4 | n |  | TRUE
91 | bus_LV_261-243_0_6_node_100 | 0.4 | n |  | TRUE
92 | bus_LV_261-243_0_6_node_70 | 0.4 | n |  | TRUE
93 | bus_LV_261-243_0_6_node_77 | 0.4 | n |  | TRUE
94 | bus_MV_524_0_node_164 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-243_0_6_load_0 | 0 | 0.0092466 | 0.0023174 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-243_0_6_load_3 | 3 | 0.015847 | 0.0039716 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-243_0_6_load_87 | 9 | 0.010197 | 0.0025555 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-243_0_6_load_85 | 10 | 0.019168 | 0.004804 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-243_0_6_load_46 | 12 | 0.0037227 | 0.000933 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-243_0_6_load_45 | 13 | 0.0032293 | 0.00080933 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-243_0_6_load_44 | 16 | 0.0054023 | 0.0013539 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-243_0_6_load_80 | 18 | 0.0082839 | 0.0020761 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-243_0_6_load_42 | 20 | 0.003079 | 0.00077166 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-243_0_6_load_43 | 21 | 0.0053945 | 0.001352 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-243_0_6_load_81 | 24 | 0.0089739 | 0.0022491 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-243_0_6_load_84 | 25 | 0.003234 | 0.00081052 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-243_0_6_load_48 | 28 | 0.0066883 | 0.0016762 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-243_0_6_load_57 | 31 | 0.0059821 | 0.0014993 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-243_0_6_load_51 | 33 | 0.0092536 | 0.0023192 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-243_0_6_load_50 | 34 | 0.013465 | 0.0033747 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-243_0_6_load_59 | 36 | 0.0088125 | 0.0022086 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-243_0_6_load_98 | 40 | 0.0048785 | 0.0012227 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-243_0_6_load_61 | 42 | 0.0019967 | 0.00050043 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-243_0_6_load_49 | 44 | 0.037053 | 0.0092865 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-243_0_6_load_89 | 45 | 0.0036762 | 0.00092135 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-243_0_6_load_90 | 46 | 0.011425 | 0.0028635 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-243_0_6_load_94 | 52 | 0.023572 | 0.0059077 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-243_0_6_load_55 | 53 | 0.010518 | 0.002636 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-243_0_6_load_64 | 54 | 0.0019831 | 0.00049702 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-243_0_6_load_60 | 56 | 0.0078134 | 0.0019582 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-243_0_6_load_58 | 57 | 0.0071807 | 0.0017997 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-243_0_6_load_65 | 58 | 0.09701 | 0.024313 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-243_0_6_load_66 | 61 | 0.0013014 | 0.00032616 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-243_0_6_load_67 | 63 | 0.010374 | 0.0025999 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-243_0_6_load_82 | 66 | 0.013868 | 0.0034756 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-243_0_6_load_78 | 67 | 0.0051822 | 0.0012988 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-243_0_6_load_52 | 70 | 0.0029143 | 0.00073038 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-243_0_6_load_91 | 71 | 0.006378 | 0.0015985 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-243_0_6_load_88 | 72 | 0.010407 | 0.0026081 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-243_0_6_load_86 | 73 | 0.0082879 | 0.0020771 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-243_0_6_load_47 | 74 | 0.0044164 | 0.0011068 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-243_0_6_load_76 | 75 | 0.010281 | 0.0025767 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-243_0_6_load_97 | 76 | 0.0052778 | 0.0013228 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-243_0_6_load_56 | 77 | 0.0084702 | 0.0021228 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-243_0_6_load_99 | 78 | 0.02809 | 0.0070399 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-243_0_6_load_62 | 79 | 0.004002 | 0.001003 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-243_0_6_load_63 | 80 | 0.00082857 | 0.00020766 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-243_0_6_load_96 | 83 | 0.0081324 | 0.0020382 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-243_0_6_load_73 | 86 | 0.0099093 | 0.0024835 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-243_0_6_load_69 | 87 | 0.010426 | 0.002613 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-243_0_6_load_53 | 88 | 0.0029152 | 0.00073061 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-243_0_6_load_75 | 89 | 0.010207 | 0.0025581 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-243_0_6_load_74 | 90 | 0.01027 | 0.0025738 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-243_0_6_load_100 | 91 | 0.015373 | 0.0038528 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-243_0_6_load_77 | 93 | 0.013853 | 0.0034719 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 49 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-243_0_6_line_0 |  | 0 | 1 | 0.024271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-243_0_6_line_1 |  | 0 | 2 | 0.022578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-243_0_6_line_2 |  | 1 | 3 | 0.012999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-243_0_6_line_3 |  | 1 | 4 | 0.01163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-243_0_6_line_4 |  | 2 | 5 | 0.017522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_261-243_0_6_line_5 |  | 2 | 6 | 0.034092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_261-243_0_6_line_6 |  | 2 | 7 | 0.02816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-243_0_6_line_7 |  | 4 | 17 | 0.025239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-243_0_6_line_8 |  | 4 | 13 | 0.010336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-243_0_6_line_9 |  | 5 | 68 | 0.02484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-243_0_6_line_10 |  | 5 | 52 | 0.015495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_261-243_0_6_line_11 |  | 6 | 39 | 0.01492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_261-243_0_6_line_12 |  | 6 | 67 | 0.0081827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-243_0_6_line_13 |  | 7 | 25 | 0.0023452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-243_0_6_line_14 |  | 8 | 9 | 0.016519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-243_0_6_line_15 |  | 8 | 10 | 0.0044818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-243_0_6_line_16 |  | 9 | 72 | 0.016225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-243_0_6_line_17 |  | 10 | 73 | 0.0028242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-243_0_6_line_18 |  | 11 | 12 | 0.017472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-243_0_6_line_19 |  | 11 | 13 | 0.012651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-243_0_6_line_20 |  | 12 | 74 | 0.0032867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-243_0_6_line_21 |  | 14 | 15 | 0.009502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-243_0_6_line_22 |  | 14 | 16 | 0.011798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-243_0_6_line_23 |  | 15 | 18 | 0.020483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-243_0_6_line_24 |  | 17 | 18 | 0.012099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-243_0_6_line_25 |  | 19 | 20 | 0.022937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-243_0_6_line_26 |  | 19 | 21 | 0.0084869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-243_0_6_line_27 |  | 20 | 45 | 0.0043446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-243_0_6_line_28 |  | 21 | 73 | 0.0049447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-243_0_6_line_29 |  | 22 | 23 | 0.051946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-243_0_6_line_30 |  | 22 | 24 | 0.019759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-243_0_6_line_31 |  | 23 | 75 | 0.012588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-243_0_6_line_32 |  | 23 | 62 | 0.008977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-243_0_6_line_33 |  | 25 | 65 | 0.02683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-243_0_6_line_34 |  | 26 | 27 | 0.085496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-243_0_6_line_35 |  | 26 | 28 | 0.042378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-243_0_6_line_36 |  | 27 | 45 | 0.017483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-243_0_6_line_37 |  | 27 | 46 | 0.020288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-243_0_6_line_38 |  | 27 | 43 | 0.050899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-243_0_6_line_39 |  | 29 | 30 | 0.003295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-243_0_6_line_40 |  | 29 | 31 | 0.027816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-243_0_6_line_41 |  | 30 | 35 | 0.012884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-243_0_6_line_42 |  | 30 | 36 | 0.02956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-243_0_6_line_43 |  | 31 | 77 | 0.01498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-243_0_6_line_44 |  | 32 | 33 | 0.004034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-243_0_6_line_45 |  | 32 | 34 | 0.019584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-243_0_6_line_46 |  | 34 | 47 | 0.014115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-243_0_6_line_47 |  | 35 | 41 | 0.006402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-243_0_6_line_48 |  | 35 | 42 | 0.027517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-243_0_6_line_49 |  | 36 | 57 | 0.033959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-243_0_6_line_50 |  | 37 | 38 | 0.04002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-243_0_6_line_51 |  | 37 | 39 | 0.023755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-243_0_6_line_52 |  | 37 | 40 | 0.01522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-243_0_6_line_53 |  | 38 | 47 | 0.023059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-243_0_6_line_54 |  | 39 | 72 | 0.013375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-243_0_6_line_55 |  | 40 | 78 | 0.012238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-243_0_6_line_56 |  | 41 | 54 | 0.045119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-243_0_6_line_57 |  | 42 | 79 | 0.042953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-243_0_6_line_58 |  | 43 | 44 | 0.029484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-243_0_6_line_59 |  | 47 | 48 | 0.020845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-243_0_6_line_60 |  | 48 | 53 | 0.010912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-243_0_6_line_61 |  | 49 | 50 | 0.030697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-243_0_6_line_62 |  | 49 | 51 | 0.064702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-243_0_6_line_63 |  | 49 | 52 | 0.029652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_261-243_0_6_line_64 |  | 50 | 76 | 0.024345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-243_0_6_line_65 |  | 51 | 58 | 0.024415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-243_0_6_line_66 |  | 53 | 77 | 0.03415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-243_0_6_line_67 |  | 54 | 80 | 0.013483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-243_0_6_line_68 |  | 55 | 56 | 0.014898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-243_0_6_line_69 |  | 55 | 57 | 0.02345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-243_0_6_line_70 |  | 56 | 83 | 0.041173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-243_0_6_line_71 |  | 59 | 60 | 0.029997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-243_0_6_line_72 |  | 59 | 61 | 0.041319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-243_0_6_line_73 |  | 60 | 69 | 0.046918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-243_0_6_line_74 |  | 60 | 70 | 0.047434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-243_0_6_line_75 |  | 62 | 63 | 0.012524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-243_0_6_line_76 |  | 63 | 84 | 0.028516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-243_0_6_line_77 |  | 64 | 65 | 0.031487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-243_0_6_line_78 |  | 64 | 66 | 0.014737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-243_0_6_line_79 |  | 65 | 85 | 0.008281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-243_0_6_line_80 |  | 68 | 88 | 0.016317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_261-243_0_6_line_81 |  | 69 | 71 | 0.0042782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-243_0_6_line_82 |  | 70 | 88 | 0.024619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_261-243_0_6_line_83 |  | 71 | 81 | 0.018653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_261-243_0_6_line_84 |  | 81 | 82 | 0.01161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_261-243_0_6_line_85 |  | 82 | 91 | 0.0052458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_261-243_0_6_line_86 |  | 84 | 87 | 0.012175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_261-243_0_6_line_87 |  | 84 | 92 | 0.008225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_261-243_0_6_line_88 |  | 85 | 93 | 0.0078544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_261-243_0_6_line_89 |  | 86 | 87 | 0.00022646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_261-243_0_6_line_90 |  | 89 | 90 | 0.00048336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_261-243_0_6_line_91 |  | 90 | 92 | 0.011584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_261-243_0_6_line_92 |  | 92 | 93 | 0.031218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-243_0_6_trafo_25 | 0.63 MVA 20/0.4 kV | 94 | 49 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2680588.9188 | 1252628.9826 | 2680586.1179 | 1252637.9289 | 2680585.9306 | 1252641.707 | 2680587.8075 | 1252650.1944 | 2680588.5263 | 1252652.5061
1 | 2680598.7619 | 1252672.0819 | 2680595.6359 | 1252669.4263 | 2680591.7552 | 1252662.8908 | 2680588.5263 | 1252652.5061
2 | 2680588.9188 | 1252628.9826 | 2680591.8688 | 1252624.0524 | 2680591.6436 | 1252616.8019
3 | 2680577.3847 | 1252627.5024 | 2680583.0213 | 1252628.1239 | 2680588.9188 | 1252628.9826
4 | 2680598.7619 | 1252672.0819 | 2680601.3445 | 1252673.0733 | 2680603.8304 | 1252673.4074 | 2680605.8981 | 1252678.4059 | 2680608.5138 | 1252684.724
5 | 2680598.7619 | 1252672.0819 | 2680601.3445 | 1252673.0733 | 2680603.8304 | 1252673.4074 | 2680607.1537 | 1252672.652 | 2680630.3505 | 1252662.2821
6 | 2680578.0649 | 1252687.3229 | 2680587.0882 | 1252679.751 | 2680586.104 | 1252677.2135 | 2680591.4382 | 1252675.0956 | 2680598.7619 | 1252672.0819
7 | 2680573.503 | 1252602.7312 | 2680576.6321 | 1252613.4817 | 2680577.0341 | 1252618.8801 | 2680577.3847 | 1252627.5024
8 | 2680577.3847 | 1252627.5024 | 2680577.6506 | 1252637.8348
9 | 2680608.5138 | 1252684.724 | 2680606.5285 | 1252688.0883 | 2680606.4506 | 1252693.2578 | 2680612.7895 | 1252707.6992
10 | 2680608.5138 | 1252684.724 | 2680610.3082 | 1252683.7476 | 2680622.6184 | 1252678.3234
11 | 2680643.9724 | 1252656.1963 | 2680632.2488 | 1252661.4295 | 2680630.3505 | 1252662.2821
12 | 2680630.3505 | 1252662.2821 | 2680629.6968 | 1252660.9611 | 2680628.8632 | 1252660.6607 | 2680626.3969 | 1252659.9933 | 2680625.4171 | 1252658.7902 | 2680625.2139 | 1252657.0861
13 | 2680578.0649 | 1252687.3229 | 2680576.2729 | 1252688.8356
14 | 2680623.7965 | 1252614.8576 | 2680631.3906 | 1252626.9144 | 2680632.2867 | 1252629
15 | 2680623.7965 | 1252614.8576 | 2680621.8759 | 1252611.807 | 2680621.5157 | 1252611.0075
16 | 2680632.2867 | 1252629 | 2680638.6921 | 1252643.9073
17 | 2680621.5157 | 1252611.0075 | 2680620.3557 | 1252608.4325
18 | 2680578.5441 | 1252650.4464 | 2680569.6334 | 1252653.6164 | 2680566.703 | 1252653.2207 | 2680562.0974 | 1252655.3101
19 | 2680578.5441 | 1252650.4464 | 2680577.7697 | 1252642.4632 | 2680577.6506 | 1252637.8348
20 | 2680562.0974 | 1252655.3101 | 2680559.1043 | 1252656.6678
21 | 2680542.4559 | 1252612.1049 | 2680538.0737 | 1252613.5798 | 2680533.6379 | 1252615.6655
22 | 2680533.6379 | 1252615.6655 | 2680538.4354 | 1252626.4443
23 | 2680542.4559 | 1252612.1049 | 2680544.2019 | 1252611.3503 | 2680552.2525 | 1252607.6125 | 2680561.7108 | 1252605.4399
24 | 2680573.503 | 1252602.7312 | 2680561.7108 | 1252605.4399
25 | 2680614.9574 | 1252596.1345 | 2680634.999 | 1252584.9802
26 | 2680614.9574 | 1252596.1345 | 2680616.9971 | 1252600.977 | 2680618.3247 | 1252603.9241
27 | 2680634.999 | 1252584.9802 | 2680638.7952 | 1252582.8673
28 | 2680620.3557 | 1252608.4325 | 2680618.3247 | 1252603.9241
29 | 2680587.5056 | 1252784.3791 | 2680588.6471 | 1252784.239 | 2680613.2249 | 1252773.8322 | 2680622.1193 | 1252796.2366
30 | 2680622.1193 | 1252796.2366 | 2680603.8612 | 1252803.7916
31 | 2680587.5056 | 1252784.3791 | 2680582.7195 | 1252772.7366
32 | 2680587.5056 | 1252784.3791 | 2680584.1344 | 1252784.778 | 2680581.6857 | 1252786.1457 | 2680579.2373 | 1252787.5023
33 | 2680553.4376 | 1252702.4549 | 2680567.9797 | 1252695.8365 | 2680576.2729 | 1252688.8356
34 | 2680715.8441 | 1252516.4485 | 2680692.9195 | 1252535.039 | 2680670.6604 | 1252551.8818 | 2680668.8991 | 1252554.8601 | 2680668.5058 | 1252558.2461 | 2680662.6242 | 1252562.8584 | 2680659.1992 | 1252565.536 | 2680652.3573 | 1252571.9476
35 | 2680715.8441 | 1252516.4485 | 2680734.8871 | 1252537.9017 | 2680739.1468 | 1252538.7715 | 2680746.3517 | 1252532.8215
36 | 2680652.3573 | 1252571.9476 | 2680642.1818 | 1252580.9825 | 2680638.7952 | 1252582.8673
37 | 2680652.3573 | 1252571.9476 | 2680656.0547 | 1252574.7667 | 2680659.5026 | 1252575.9479 | 2680666.9857 | 1252585.3213
38 | 2680652.3573 | 1252571.9476 | 2680659.1992 | 1252565.536 | 2680662.6242 | 1252562.8584 | 2680682.6716 | 1252587.0382 | 2680687.3883 | 1252583.7222
39 | 2680776.0227 | 1252710.7244 | 2680778.0856 | 1252713.2989
40 | 2680776.0227 | 1252710.7244 | 2680761.5932 | 1252686.9433
41 | 2680778.0856 | 1252713.2989 | 2680778.9247 | 1252714.856 | 2680781.3463 | 1252719.3479 | 2680782.8717 | 1252723.1493 | 2680783.587 | 1252724.927
42 | 2680778.0856 | 1252713.2989 | 2680782.9135 | 1252712.8978 | 2680787.9731 | 1252710.4427 | 2680790.0303 | 1252707.9022 | 2680797.1489 | 1252693.7709
43 | 2680753.1219 | 1252674.5883 | 2680761.5932 | 1252686.9433 | 2680761.5932 | 1252686.9433
44 | 2680748.7409 | 1252612.7907 | 2680751.9262 | 1252610.3154
45 | 2680748.7409 | 1252612.7907 | 2680745.403 | 1252609.0758 | 2680742.3207 | 1252605.987 | 2680733.7165 | 1252611.5128
46 | 2680721.8402 | 1252619.14 | 2680733.7165 | 1252611.5128
47 | 2680784.4816 | 1252731.2662 | 2680783.587 | 1252724.927
48 | 2680783.587 | 1252724.927 | 2680787.7763 | 1252721.5483 | 2680793.3777 | 1252717.555 | 2680796.1678 | 1252713.8458 | 2680800.8408 | 1252704.3153
49 | 2680812.9294 | 1252663.7061 | 2680811.4206 | 1252666.7854 | 2680801.5571 | 1252685.0201 | 2680797.1489 | 1252693.7709
50 | 2680665.6235 | 1252646.2836 | 2680686.69 | 1252636.6299 | 2680697.0269 | 1252631.8115 | 2680701.1897 | 1252628.1655
51 | 2680643.9724 | 1252656.1963 | 2680665.6235 | 1252646.2836
52 | 2680665.6235 | 1252646.2836 | 2680662.6175 | 1252640.9165 | 2680658.9804 | 1252632.6091
53 | 2680701.1897 | 1252628.1655 | 2680706.4825 | 1252625.2131 | 2680710.4293 | 1252623.0208 | 2680715.722 | 1252620.0796 | 2680717.0908 | 1252619.3199 | 2680718.7002 | 1252619.731 | 2680720.318 | 1252619.5307 | 2680721.8402 | 1252619.14
54 | 2680643.9724 | 1252656.1963 | 2680638.6921 | 1252643.9073
55 | 2680654.6831 | 1252621.1604 | 2680657.3038 | 1252628.7795 | 2680658.9804 | 1252632.6091
56 | 2680784.4816 | 1252731.2662 | 2680790.1088 | 1252729.2525 | 2680819.9811 | 1252726.3243 | 2680829.096 | 1252725.8638
57 | 2680800.8408 | 1252704.3153 | 2680803.1 | 1252699.7076 | 2680811.7805 | 1252685.2041 | 2680820.4281 | 1252666.1562
58 | 2680687.3883 | 1252583.7222 | 2680710.8194 | 1252565.826
59 | 2680721.8402 | 1252619.14 | 2680722.5653 | 1252620.2063 | 2680724.5111 | 1252623.0682 | 2680726.938 | 1252626.6262 | 2680727.6113 | 1252627.6139 | 2680727.0884 | 1252629.4303 | 2680726.5666 | 1252631.1689 | 2680726.3216 | 1252633.0893 | 2680726.4616 | 1252635.5485 | 2680726.9415 | 1252637.9902
60 | 2680726.9415 | 1252637.9902 | 2680728.0546 | 1252640.485 | 2680730.3869 | 1252643.7859 | 2680732.8662 | 1252647.0992
61 | 2680654.6125 | 1252695.6038 | 2680656.1956 | 1252687.4192 | 2680654.8393 | 1252678.95 | 2680649.6627 | 1252666.17
62 | 2680649.6627 | 1252666.17 | 2680652.7438 | 1252664.911 | 2680656.4731 | 1252674.2465 | 2680664.1325 | 1252694.7883 | 2680671.2962 | 1252705.7385 | 2680677.4164 | 1252710.7366 | 2680681.6316 | 1252713.7629 | 2680684.7526 | 1252714.5616
63 | 2680649.6627 | 1252666.17 | 2680646.7632 | 1252667.387 | 2680635.8641 | 1252672.487 | 2680622.6184 | 1252678.3234
64 | 2680654.6125 | 1252695.6038 | 2680655.3049 | 1252697.4034 | 2680656.4612 | 1252698.9426 | 2680658.0001 | 1252700.0977 | 2680660.02 | 1252700.848 | 2680662.162 | 1252700.9439 | 2680664.2373 | 1252700.3939 | 2680675.5986 | 1252696.1685
65 | 2680684.7526 | 1252714.5616 | 2680689.8272 | 1252714.3305 | 2680707.9485 | 1252707.5875
66 | 2680732.8662 | 1252647.0992 | 2680749.6798 | 1252669.568 | 2680753.1219 | 1252674.5883
67 | 2680842.5615 | 1252725.1834 | 2680829.096 | 1252725.8638
68 | 2680824.1724 | 1252643.1862 | 2680813.8883 | 1252632.4064
69 | 2680824.1724 | 1252643.1862 | 2680819.9445 | 1252649.3887 | 2680812.9294 | 1252663.7061
70 | 2680785.4673 | 1252602.6155 | 2680813.8883 | 1252632.4064
71 | 2680653.8372 | 1252782.9917 | 2680661.7731 | 1252780.4534 | 2680669.5884 | 1252777.9134 | 2680679.5178 | 1252774.1792 | 2680682.1802 | 1252773.1925
72 | 2680682.1802 | 1252773.1925 | 2680676.6854 | 1252758.2954 | 2680674.3732 | 1252756.2958 | 2680669.711 | 1252755.6207 | 2680665.2644 | 1252757.3948 | 2680663.4939 | 1252761.0512 | 2680664.0459 | 1252765.9624 | 2680666.7596 | 1252768.7377
73 | 2680653.8372 | 1252782.9917 | 2680654.1724 | 1252783.8636 | 2680656.0812 | 1252788.8933 | 2680657.6514 | 1252792.7287 | 2680658.0676 | 1252793.7573 | 2680660.994 | 1252792.2182 | 2680676.9277 | 1252785.9305 | 2680687.6323 | 1252781.8065 | 2680688.7956 | 1252785.0469
74 | 2680653.8372 | 1252782.9917 | 2680652.7307 | 1252783.3324 | 2680651.5828 | 1252783.3946 | 2680650.4762 | 1252783.1905 | 2680649.4559 | 1252782.743 | 2680648.2658 | 1252781.4703 | 2680646.9432 | 1252778.8392 | 2680638.2483 | 1252759.5287 | 2680631.4403 | 1252750.1735 | 2680629.2481 | 1252745.1811
75 | 2680579.2373 | 1252787.5023 | 2680574.6424 | 1252775.8517
76 | 2680564.1804 | 1252749.3247 | 2680574.6424 | 1252775.8517
77 | 2680524.5784 | 1252715.2388 | 2680553.4376 | 1252702.4549
78 | 2680524.5784 | 1252715.2388 | 2680525.7447 | 1252718.268 | 2680529.8691 | 1252728.9933
79 | 2680553.4376 | 1252702.4549 | 2680554.5799 | 1252705.0279 | 2680555.0327 | 1252706.1348 | 2680556.9733 | 1252709.9418
80 | 2680612.7895 | 1252707.6992 | 2680619.3498 | 1252722.6394
81 | 2680688.7956 | 1252785.0469 | 2680692.7842 | 1252783.4998
82 | 2680619.3498 | 1252722.6394 | 2680629.2481 | 1252745.1811
83 | 2680710.1751 | 1252776.7542 | 2680692.7842 | 1252783.4998
84 | 2680714.4199 | 1252787.5645 | 2680710.1751 | 1252776.7542
85 | 2680714.4199 | 1252787.5645 | 2680719.3025 | 1252785.6465
86 | 2680564.1804 | 1252749.3247 | 2680557.8726 | 1252752.0076 | 2680552.9387 | 1252753.9986
87 | 2680571.7709 | 1252746.1033 | 2680564.1804 | 1252749.3247
88 | 2680556.9733 | 1252709.9418 | 2680559.9479 | 1252717.2112
89 | 2680552.9387 | 1252753.9986 | 2680552.7287 | 1252754.0833
90 | 2680582.5974 | 1252741.9836 | 2680583.0491 | 1252741.8117
91 | 2680571.7709 | 1252746.1033 | 2680582.5974 | 1252741.9836
92 | 2680571.7709 | 1252746.1033 | 2680559.9479 | 1252717.2112

## bus_geodata
| x | y | coords
0 | 2680588.5263 | 1252652.5061
1 | 2680588.9188 | 1252628.9826
2 | 2680598.7619 | 1252672.0819
3 | 2680591.6436 | 1252616.8019
4 | 2680577.3847 | 1252627.5024
5 | 2680608.5138 | 1252684.724
6 | 2680630.3505 | 1252662.2821
7 | 2680578.0649 | 1252687.3229
8 | 2680623.7965 | 1252614.8576
9 | 2680632.2867 | 1252629
10 | 2680621.5157 | 1252611.0075
11 | 2680578.5441 | 1252650.4464
12 | 2680562.0974 | 1252655.3101
13 | 2680577.6506 | 1252637.8348
14 | 2680533.6379 | 1252615.6655
15 | 2680542.4559 | 1252612.1049
16 | 2680538.4354 | 1252626.4443
17 | 2680573.503 | 1252602.7312
18 | 2680561.7108 | 1252605.4399
19 | 2680614.9574 | 1252596.1345
20 | 2680634.999 | 1252584.9802
21 | 2680618.3247 | 1252603.9241
22 | 2680622.1193 | 1252796.2366
23 | 2680587.5056 | 1252784.3791
24 | 2680603.8612 | 1252803.7916
25 | 2680576.2729 | 1252688.8356
26 | 2680715.8441 | 1252516.4485
27 | 2680652.3573 | 1252571.9476
28 | 2680746.3517 | 1252532.8215
29 | 2680776.0227 | 1252710.7244
30 | 2680778.0856 | 1252713.2989
31 | 2680761.5932 | 1252686.9433
32 | 2680748.7409 | 1252612.7907
33 | 2680751.9262 | 1252610.3154
34 | 2680733.7165 | 1252611.5128
35 | 2680783.587 | 1252724.927
36 | 2680797.1489 | 1252693.7709
37 | 2680665.6235 | 1252646.2836
38 | 2680701.1897 | 1252628.1655
39 | 2680643.9724 | 1252656.1963
40 | 2680658.9804 | 1252632.6091
41 | 2680784.4816 | 1252731.2662
42 | 2680800.8408 | 1252704.3153
43 | 2680687.3883 | 1252583.7222
44 | 2680710.8194 | 1252565.826
45 | 2680638.7952 | 1252582.8673
46 | 2680666.9857 | 1252585.3213
47 | 2680721.8402 | 1252619.14
48 | 2680726.9415 | 1252637.9902
49 | 2680649.6627 | 1252666.17
50 | 2680654.6125 | 1252695.6038
51 | 2680684.7526 | 1252714.5616
52 | 2680622.6184 | 1252678.3234
53 | 2680732.8662 | 1252647.0992
54 | 2680829.096 | 1252725.8638
55 | 2680824.1724 | 1252643.1862
56 | 2680813.8883 | 1252632.4064
57 | 2680812.9294 | 1252663.7061
58 | 2680707.9485 | 1252707.5875
59 | 2680682.1802 | 1252773.1925
60 | 2680653.8372 | 1252782.9917
61 | 2680666.7596 | 1252768.7377
62 | 2680579.2373 | 1252787.5023
63 | 2680574.6424 | 1252775.8517
64 | 2680524.5784 | 1252715.2388
65 | 2680553.4376 | 1252702.4549
66 | 2680529.8691 | 1252728.9933
67 | 2680625.2139 | 1252657.0861
68 | 2680612.7895 | 1252707.6992
69 | 2680688.7956 | 1252785.0469
70 | 2680629.2481 | 1252745.1811
71 | 2680692.7842 | 1252783.4998
72 | 2680638.6921 | 1252643.9073
73 | 2680620.3557 | 1252608.4325
74 | 2680559.1043 | 1252656.6678
75 | 2680582.7195 | 1252772.7366
76 | 2680675.5986 | 1252696.1685
77 | 2680753.1219 | 1252674.5883
78 | 2680654.6831 | 1252621.1604
79 | 2680820.4281 | 1252666.1562
80 | 2680842.5615 | 1252725.1834
81 | 2680710.1751 | 1252776.7542
82 | 2680714.4199 | 1252787.5645
83 | 2680785.4673 | 1252602.6155
84 | 2680564.1804 | 1252749.3247
85 | 2680556.9733 | 1252709.9418
86 | 2680552.7287 | 1252754.0833
87 | 2680552.9387 | 1252753.9986
88 | 2680619.3498 | 1252722.6394
89 | 2680583.0491 | 1252741.8117
90 | 2680582.5974 | 1252741.9836
91 | 2680719.3025 | 1252785.6465
92 | 2680571.7709 | 1252746.1033
93 | 2680559.948 | 1252717.2112
94 | 2680652.7438 | 1252664.911

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99228 | -0.14709 | 0.0092466 | 0.0023174
1 | 0.99137 | -0.16468 | 0 | 0
2 | 0.99331 | -0.12707 | 0 | 0
3 | 0.99118 | -0.16833 | 0.015847 | 0.0039716
4 | 0.9911 | -0.16985 | 0 | 0
5 | 0.99544 | -0.086547 | 0 | 0
6 | 0.98949 | -0.20021 | 0 | 0
7 | 0.99068 | -0.17764 | 0 | 0
8 | 0.9834 | -0.31806 | 0 | 0
9 | 0.98485 | -0.28988 | 0.010197 | 0.0025555
10 | 0.98301 | -0.32571 | 0.019168 | 0.004804
11 | 0.9909 | -0.17376 | 0 | 0
12 | 0.99077 | -0.17629 | 0.0037227 | 0.000933
13 | 0.991 | -0.17194 | 0.0032293 | 0.00080933
14 | 0.99049 | -0.1818 | 0 | 0
15 | 0.99053 | -0.18089 | 0 | 0
16 | 0.99043 | -0.18293 | 0.0054023 | 0.0013539
17 | 0.99079 | -0.17598 | 0 | 0
18 | 0.99064 | -0.17892 | 0.0082839 | 0.0020761
19 | 0.98201 | -0.34507 | 0 | 0
20 | 0.9807 | -0.37078 | 0.003079 | 0.00077166
21 | 0.9825 | -0.33558 | 0.0053945 | 0.001352
22 | 0.98279 | -0.33101 | 0 | 0
23 | 0.98322 | -0.3226 | 0 | 0
24 | 0.98263 | -0.33421 | 0.0089739 | 0.0022491
25 | 0.99046 | -0.18187 | 0.003234 | 0.00081052
26 | 0.97904 | -0.40332 | 0 | 0
27 | 0.97957 | -0.39292 | 0 | 0
28 | 0.97877 | -0.40847 | 0.0066883 | 0.0016762
29 | 0.97459 | -0.49007 | 0 | 0
30 | 0.97446 | -0.49253 | 0 | 0
31 | 0.97564 | -0.46929 | 0.0059821 | 0.0014993
32 | 0.97953 | -0.39321 | 0 | 0
33 | 0.97949 | -0.39389 | 0.0092536 | 0.0023192
34 | 0.9797 | -0.38992 | 0.013465 | 0.0033747
35 | 0.97436 | -0.49462 | 0 | 0
36 | 0.97358 | -0.50988 | 0.0088125 | 0.0022086
37 | 0.98518 | -0.28337 | 0 | 0
38 | 0.98189 | -0.34715 | 0 | 0
39 | 0.98786 | -0.23171 | 0 | 0
40 | 0.98472 | -0.29239 | 0.0048785 | 0.0012227
41 | 0.97434 | -0.49495 | 0 | 0
42 | 0.9742 | -0.49765 | 0.0019967 | 0.00050043
43 | 0.97781 | -0.42724 | 0 | 0
44 | 0.9768 | -0.44718 | 0.037053 | 0.0092865
45 | 0.98046 | -0.37541 | 0.0036762 | 0.00092135
46 | 0.97935 | -0.39713 | 0.011425 | 0.0028635
47 | 0.97999 | -0.3841 | 0 | 0
48 | 0.97872 | -0.409 | 0 | 0
49 | 1 | 0 | -0.55733 | -0.14213
50 | 0.99985 | -0.0028249 | 0 | 0
51 | 0.99426 | -0.11003 | 0 | 0
52 | 0.99695 | -0.057805 | 0.023572 | 0.0059077
53 | 0.97805 | -0.42206 | 0.010518 | 0.002636
54 | 0.97422 | -0.49728 | 0.0019831 | 0.00049702
55 | 0.9725 | -0.53123 | 0 | 0
56 | 0.97228 | -0.5356 | 0.0078134 | 0.0019582
57 | 0.97285 | -0.52434 | 0.0071807 | 0.0017997
58 | 0.9921 | -0.15188 | 0.09701 | 0.024313
59 | 0.99273 | -0.13878 | 0 | 0
60 | 0.99277 | -0.13809 | 0 | 0
61 | 0.99268 | -0.13973 | 0.0013014 | 0.00032616
62 | 0.98338 | -0.31949 | 0 | 0
63 | 0.9836 | -0.31514 | 0.010374 | 0.0025999
64 | 0.98764 | -0.23658 | 0 | 0
65 | 0.98804 | -0.22878 | 0 | 0
66 | 0.98745 | -0.24023 | 0.013868 | 0.0034756
67 | 0.98945 | -0.20097 | 0.0051822 | 0.0012988
68 | 0.99478 | -0.099178 | 0 | 0
69 | 0.99183 | -0.15615 | 0 | 0
70 | 0.99377 | -0.11876 | 0.0029143 | 0.00073038
71 | 0.99175 | -0.1578 | 0.006378 | 0.0015985
72 | 0.98643 | -0.25932 | 0.010407 | 0.0026081
73 | 0.98281 | -0.32957 | 0.0082879 | 0.0020771
74 | 0.99076 | -0.17655 | 0.0044164 | 0.0011068
75 | 0.9831 | -0.32494 | 0.010281 | 0.0025767
76 | 0.99974 | -0.0050655 | 0.0052778 | 0.0013228
77 | 0.97629 | -0.45647 | 0.0084702 | 0.0021228
78 | 0.9844 | -0.29857 | 0.02809 | 0.0070399
79 | 0.97404 | -0.50081 | 0.004002 | 0.001003
80 | 0.97421 | -0.49749 | 0.00082857 | 0.00020766
81 | 0.99149 | -0.16288 | 0 | 0
82 | 0.99132 | -0.16605 | 0 | 0
83 | 0.97197 | -0.54178 | 0.0081324 | 0.0020382
84 | 0.98438 | -0.29993 | 0 | 0
85 | 0.9874 | -0.24125 | 0 | 0
86 | 0.98415 | -0.30442 | 0.0099093 | 0.0024835
87 | 0.98415 | -0.30438 | 0.010426 | 0.002613
88 | 0.99435 | -0.10748 | 0.0029152 | 0.00073061
89 | 0.98454 | -0.29689 | 0.010207 | 0.0025581
90 | 0.98454 | -0.2968 | 0.01027 | 0.0025738
91 | 0.99125 | -0.16748 | 0.015373 | 0.0038528
92 | 0.98476 | -0.29254 | 0 | 0
93 | 0.98679 | -0.25309 | 0.013853 | 0.0034719
94 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.040954 | 0.010283 | -0.04092 | -0.010261 | 3.4337e-05 | 2.1662e-05 | 0.061422 | 0.061422 | 0.061422 | 0.99228 | -0.14709 | 0.99137 | -0.16468 | 16.8741
1 | -0.050201 | -0.0126 | 0.050249 | 0.01263 | 4.7991e-05 | 3.0422e-05 | 0.075288 | 0.075288 | 0.075288 | 0.99228 | -0.14709 | 0.99331 | -0.12707 | 20.6835
2 | 0.01585 | 0.0039732 | -0.015847 | -0.0039716 | 2.759e-06 | 1.5982e-06 | 0.02379 | 0.02379 | 0.02379 | 0.99137 | -0.16468 | 0.99118 | -0.16833 | 6.5358
3 | 0.025071 | 0.0062878 | -0.025064 | -0.006284 | 6.1764e-06 | 3.803e-06 | 0.037632 | 0.037632 | 0.037632 | 0.99137 | -0.16468 | 0.9911 | -0.16985 | 10.3384
4 | -0.3975 | -0.10116 | 0.39828 | 0.10166 | 0.00077806 | 0.00049728 | 0.59602 | 0.59602 | 0.59602 | 0.99331 | -0.12707 | 0.99544 | -0.086547 | 54.5804
5 | 0.24507 | 0.062616 | -0.2442 | -0.062064 | 0.00086353 | 0.00055178 | 0.36755 | 0.36755 | 0.36755 | 0.99331 | -0.12707 | 0.98949 | -0.20021 | 50.4872
6 | 0.10218 | 0.025913 | -0.10194 | -0.025755 | 0.00024779 | 0.00015822 | 0.15318 | 0.15318 | 0.15318 | 0.99331 | -0.12707 | 0.99068 | -0.17764 | 42.0835
7 | 0.013693 | 0.0034335 | -0.013689 | -0.0034313 | 4.0005e-06 | 2.2352e-06 | 0.020559 | 0.020559 | 0.020559 | 0.9911 | -0.16985 | 0.99079 | -0.17598 | 5.6481
8 | 0.011371 | 0.0028504 | -0.01137 | -0.0028499 | 1.1297e-06 | 5.8986e-07 | 0.017073 | 0.017073 | 0.017073 | 0.9911 | -0.16985 | 0.991 | -0.17194 | 4.6903
9 | 0.028974 | 0.0072938 | -0.028956 | -0.0072829 | 1.7483e-05 | 1.0866e-05 | 0.043322 | 0.043322 | 0.043322 | 0.99544 | -0.086547 | 0.99478 | -0.099178 | 11.9018
10 | -0.42725 | -0.10895 | 0.42785 | 0.10933 | 0.00059378 | 0.00037921 | 0.63934 | 0.63934 | 0.63934 | 0.99544 | -0.086547 | 0.99695 | -0.057805 | 43.9107
11 | 0.23902 | 0.060765 | -0.23866 | -0.060534 | 0.00036205 | 0.00023133 | 0.35975 | 0.35975 | 0.35975 | 0.98949 | -0.20021 | 0.98786 | -0.23171 | 49.4167
12 | 0.0051824 | 0.0012988 | -0.0051822 | -0.0012988 | 1.8637e-07 | 1.4173e-08 | 0.0077933 | 0.0077933 | 0.0077933 | 0.98949 | -0.20021 | 0.98945 | -0.20097 | 2.141
13 | 0.10194 | 0.025755 | -0.10192 | -0.025742 | 2.0636e-05 | 1.3177e-05 | 0.15318 | 0.15318 | 0.15318 | 0.99068 | -0.17764 | 0.99046 | -0.18187 | 42.0835
14 | -0.095108 | -0.023963 | 0.095237 | 0.024045 | 0.00012838 | 8.195e-05 | 0.14396 | 0.14396 | 0.14396 | 0.9834 | -0.31806 | 0.98485 | -0.28988 | 39.5486
15 | 0.095108 | 0.023963 | -0.095073 | -0.023941 | 3.4829e-05 | 2.2234e-05 | 0.14396 | 0.14396 | 0.14396 | 0.9834 | -0.31806 | 0.98301 | -0.32571 | 39.5486
16 | -0.10543 | -0.026601 | 0.10559 | 0.026699 | 0.00015452 | 9.8688e-05 | 0.15936 | 0.15936 | 0.15936 | 0.98485 | -0.28988 | 0.98643 | -0.25932 | 43.781
17 | 0.075905 | 0.019137 | -0.075891 | -0.019128 | 1.3992e-05 | 8.919e-06 | 0.11494 | 0.11494 | 0.11494 | 0.98301 | -0.32571 | 0.98281 | -0.32957 | 31.5772
18 | 0.0081401 | 0.0020402 | -0.0081391 | -0.0020398 | 9.7904e-07 | 4.0154e-07 | 0.012224 | 0.012224 | 0.012224 | 0.9909 | -0.17376 | 0.99077 | -0.17629 | 3.3582
19 | -0.0081401 | -0.0020402 | 0.0081408 | 0.0020405 | 7.0885e-07 | 2.9069e-07 | 0.012224 | 0.012224 | 0.012224 | 0.9909 | -0.17376 | 0.991 | -0.17194 | 3.3582
20 | 0.0044164 | 0.0011068 | -0.0044164 | -0.0011068 | 5.4225e-08 | -7.6222e-09 | 0.0066329 | 0.0066329 | 0.0066329 | 0.99077 | -0.17629 | 0.99076 | -0.17655 | 1.8222
21 | -0.0054026 | -0.001354 | 0.0054028 | 0.001354 | 2.3473e-07 | 2.7921e-08 | 0.0081163 | 0.0081163 | 0.0081163 | 0.99049 | -0.1818 | 0.99053 | -0.18089 | 2.2298
22 | 0.0054026 | 0.001354 | -0.0054023 | -0.0013539 | 2.9145e-07 | 3.4686e-08 | 0.0081163 | 0.0081164 | 0.0081164 | 0.99049 | -0.1818 | 0.99043 | -0.18293 | 2.2298
23 | -0.0054028 | -0.001354 | 0.0054033 | 0.0013541 | 5.0598e-07 | 6.0142e-08 | 0.0081163 | 0.0081162 | 0.0081163 | 0.99053 | -0.18089 | 0.99064 | -0.17892 | 2.2298
24 | 0.013689 | 0.0034313 | -0.013687 | -0.0034302 | 1.9178e-06 | 1.0716e-06 | 0.020559 | 0.020559 | 0.020559 | 0.99079 | -0.17598 | 0.99064 | -0.17892 | 5.6482
25 | 0.062161 | 0.015669 | -0.062085 | -0.01562 | 7.6361e-05 | 4.8581e-05 | 0.094223 | 0.094223 | 0.094223 | 0.98201 | -0.34507 | 0.9807 | -0.37078 | 25.8854
26 | -0.062161 | -0.015669 | 0.062189 | 0.015687 | 2.8255e-05 | 1.7976e-05 | 0.094223 | 0.094223 | 0.094223 | 0.98201 | -0.34507 | 0.9825 | -0.33558 | 25.8854
27 | 0.059006 | 0.014848 | -0.058993 | -0.01484 | 1.3065e-05 | 8.307e-06 | 0.089551 | 0.089551 | 0.089551 | 0.9807 | -0.37078 | 0.98046 | -0.37541 | 24.602
28 | -0.067584 | -0.017039 | 0.067603 | 0.017051 | 1.9441e-05 | 1.238e-05 | 0.10239 | 0.10239 | 0.10239 | 0.9825 | -0.33558 | 0.98281 | -0.32957 | 28.1299
29 | -0.0089752 | -0.0022497 | 0.0089788 | 0.0022513 | 3.5972e-06 | 1.6437e-06 | 0.013589 | 0.013589 | 0.013589 | 0.98279 | -0.33101 | 0.98322 | -0.3226 | 3.7333
30 | 0.0089752 | 0.0022497 | -0.0089739 | -0.0022491 | 1.3684e-06 | 6.2541e-07 | 0.013589 | 0.013589 | 0.013589 | 0.98279 | -0.33101 | 0.98263 | -0.33421 | 3.7333
31 | 0.010282 | 0.0025773 | -0.010281 | -0.0025767 | 1.1431e-06 | 5.7197e-07 | 0.015562 | 0.015562 | 0.015562 | 0.98322 | -0.3226 | 0.9831 | -0.32494 | 4.2752
32 | -0.019261 | -0.0048286 | 0.019264 | 0.0048303 | 2.8606e-06 | 1.7169e-06 | 0.029151 | 0.029151 | 0.029151 | 0.98322 | -0.3226 | 0.98338 | -0.31949 | 8.0084
33 | 0.098682 | 0.024931 | -0.098461 | -0.02479 | 0.00022135 | 0.00014132 | 0.14833 | 0.14833 | 0.14833 | 0.99046 | -0.18187 | 0.98804 | -0.22878 | 40.7487
34 | -0.0066899 | -0.0016768 | 0.0066932 | 0.0016778 | 3.3145e-06 | 1.0456e-06 | 0.010168 | 0.010168 | 0.010168 | 0.97904 | -0.40332 | 0.97957 | -0.39292 | 2.7934
35 | 0.0066899 | 0.0016768 | -0.0066883 | -0.0016762 | 1.643e-06 | 5.1876e-07 | 0.010168 | 0.010168 | 0.010168 | 0.97904 | -0.40332 | 0.97877 | -0.40847 | 2.7934
36 | -0.05527 | -0.013889 | 0.055317 | 0.013919 | 4.623e-05 | 2.9367e-05 | 0.083972 | 0.083972 | 0.083972 | 0.97957 | -0.39292 | 0.98046 | -0.37541 | 23.0693
37 | 0.011428 | 0.0028647 | -0.011425 | -0.0028635 | 2.2927e-06 | 1.212e-06 | 0.017359 | 0.01736 | 0.01736 | 0.97957 | -0.39292 | 0.97935 | -0.39713 | 4.7691
38 | 0.037149 | 0.0093469 | -0.037089 | -0.0093086 | 6.0813e-05 | 3.8281e-05 | 0.056445 | 0.056445 | 0.056445 | 0.97957 | -0.39292 | 0.97781 | -0.42724 | 15.507
39 | 0.04081 | 0.010248 | -0.040806 | -0.010245 | 4.7985e-06 | 3.03e-06 | 0.062317 | 0.062317 | 0.062317 | 0.97459 | -0.49007 | 0.97446 | -0.49253 | 17.1201
40 | -0.04081 | -0.010248 | 0.040851 | 0.010274 | 4.0509e-05 | 2.5578e-05 | 0.062317 | 0.062317 | 0.062317 | 0.97459 | -0.49007 | 0.97564 | -0.46929 | 17.1201
41 | 0.0088132 | 0.002208 | -0.0088123 | -0.0022076 | 8.7502e-07 | 3.9952e-07 | 0.013458 | 0.013458 | 0.013458 | 0.97446 | -0.49253 | 0.97436 | -0.49462 | 3.6971
42 | 0.031992 | 0.008037 | -0.031966 | -0.0080205 | 2.6463e-05 | 1.6568e-05 | 0.04886 | 0.04886 | 0.04886 | 0.97446 | -0.49253 | 0.97358 | -0.50988 | 13.423
43 | -0.046833 | -0.011773 | 0.046862 | 0.011791 | 2.8671e-05 | 1.8162e-05 | 0.071441 | 0.071441 | 0.071441 | 0.97564 | -0.46929 | 0.97629 | -0.45647 | 19.6266
44 | 0.0092539 | 0.0023193 | -0.0092536 | -0.0023192 | 2.9895e-07 | 1.4055e-07 | 0.014058 | 0.014058 | 0.014058 | 0.97953 | -0.39321 | 0.97949 | -0.39389 | 3.862
45 | -0.0092539 | -0.0023193 | 0.0092554 | 0.00232 | 1.4513e-06 | 6.8227e-07 | 0.014058 | 0.014058 | 0.014058 | 0.97953 | -0.39321 | 0.9797 | -0.38992 | 3.862
46 | -0.022721 | -0.0056947 | 0.022727 | 0.0056986 | 6.3034e-06 | 3.8564e-06 | 0.034509 | 0.034509 | 0.034509 | 0.9797 | -0.38992 | 0.97999 | -0.3841 | 9.4806
47 | 0.0028121 | 0.0007041 | -0.002812 | -0.00070415 | 4.4272e-08 | -5.1402e-08 | 0.0042943 | 0.0042943 | 0.0042943 | 0.97436 | -0.49462 | 0.97434 | -0.49495 | 1.1798
48 | 0.0060002 | 0.0015035 | -0.0059994 | -0.0015033 | 8.6645e-07 | 2.1185e-07 | 0.0091633 | 0.0091634 | 0.0091634 | 0.97436 | -0.49462 | 0.9742 | -0.49765 | 2.5174
49 | 0.023153 | 0.0058119 | -0.023137 | -0.0058021 | 1.595e-05 | 9.7862e-06 | 0.035391 | 0.035391 | 0.035391 | 0.97358 | -0.50988 | 0.97285 | -0.52434 | 9.7228
50 | 0.089218 | 0.022657 | -0.088945 | -0.022483 | 0.00027295 | 0.00017418 | 0.13486 | 0.13486 | 0.13486 | 0.98518 | -0.28337 | 0.98189 | -0.34715 | 37.0498
51 | -0.12221 | -0.030934 | 0.12251 | 0.031128 | 0.00030387 | 0.00019417 | 0.18469 | 0.18469 | 0.18469 | 0.98518 | -0.28337 | 0.98786 | -0.23171 | 50.7398
52 | 0.03299 | 0.0082766 | -0.032976 | -0.0082677 | 1.4173e-05 | 8.8771e-06 | 0.049832 | 0.049832 | 0.049832 | 0.98518 | -0.28337 | 0.98472 | -0.29239 | 13.6901
53 | 0.088945 | 0.022483 | -0.088788 | -0.022383 | 0.00015727 | 0.00010036 | 0.13486 | 0.13486 | 0.13486 | 0.98189 | -0.34715 | 0.97999 | -0.3841 | 37.0498
54 | 0.11615 | 0.029406 | -0.11599 | -0.029308 | 0.00015371 | 9.8206e-05 | 0.17506 | 0.17506 | 0.17506 | 0.98786 | -0.23171 | 0.98643 | -0.25932 | 48.0937
55 | 0.028098 | 0.007045 | -0.02809 | -0.0070399 | 8.2736e-06 | 5.1395e-06 | 0.04246 | 0.04246 | 0.04246 | 0.98472 | -0.29239 | 0.9844 | -0.29857 | 11.6648
56 | 0.002812 | 0.00070415 | -0.0028117 | -0.00070452 | 3.1203e-07 | -3.6217e-07 | 0.0042943 | 0.0042945 | 0.0042945 | 0.97434 | -0.49495 | 0.97422 | -0.49728 | 1.1798
57 | 0.0040026 | 0.0010029 | -0.004002 | -0.001003 | 6.0205e-07 | -1.4942e-07 | 0.0061136 | 0.0061138 | 0.0061138 | 0.9742 | -0.49765 | 0.97404 | -0.50081 | 1.6796
58 | 0.037089 | 0.0093086 | -0.037053 | -0.0092865 | 3.5227e-05 | 2.2176e-05 | 0.056445 | 0.056446 | 0.056446 | 0.97781 | -0.42724 | 0.9768 | -0.44718 | 15.507
59 | 0.066061 | 0.016684 | -0.065982 | -0.016634 | 7.8722e-05 | 5.012e-05 | 0.10035 | 0.10035 | 0.10035 | 0.97999 | -0.3841 | 0.97872 | -0.409 | 27.5693
60 | 0.065982 | 0.016634 | -0.065941 | -0.016608 | 4.1208e-05 | 2.6236e-05 | 0.10035 | 0.10035 | 0.10035 | 0.97872 | -0.409 | 0.97805 | -0.42206 | 27.5693
61 | 0.0052791 | 0.0013228 | -0.0052784 | -0.0013228 | 7.1033e-07 | 5.195e-08 | 0.0078553 | 0.0078555 | 0.0078555 | 1 | 0 | 0.99985 | -0.0028249 | 2.1581
62 | 0.097717 | 0.024765 | -0.097204 | -0.024437 | 0.00051367 | 0.00032791 | 0.1455 | 0.1455 | 0.1455 | 1 | 0 | 0.99426 | -0.11003 | 39.9731
63 | 0.45268 | 0.11605 | -0.45142 | -0.11524 | 0.0012648 | 0.00080792 | 0.67452 | 0.67452 | 0.67452 | 1 | 0 | 0.99695 | -0.057805 | 46.327
64 | 0.0052784 | 0.0013228 | -0.0052778 | -0.0013228 | 5.6336e-07 | 4.1296e-08 | 0.0078555 | 0.0078556 | 0.0078556 | 0.99985 | -0.0028249 | 0.99974 | -0.0050655 | 2.1581
65 | 0.097204 | 0.024437 | -0.09701 | -0.024313 | 0.00019383 | 0.00012374 | 0.1455 | 0.1455 | 0.1455 | 0.99426 | -0.11003 | 0.9921 | -0.15188 | 39.9731
66 | 0.055423 | 0.013972 | -0.055332 | -0.013914 | 9.1117e-05 | 5.7887e-05 | 0.08435 | 0.08435 | 0.08435 | 0.97805 | -0.42206 | 0.97629 | -0.45647 | 23.1732
67 | 0.00082858 | 0.0002075 | -0.00082857 | -0.00020766 | 8.0975e-09 | -1.627e-07 | 0.0012655 | 0.0012656 | 0.0012656 | 0.97422 | -0.49728 | 0.97421 | -0.49749 | 0.34768
68 | 0.015952 | 0.0039994 | -0.015948 | -0.0039974 | 3.3284e-06 | 1.9454e-06 | 0.024408 | 0.024408 | 0.024408 | 0.9725 | -0.53123 | 0.97228 | -0.5356 | 6.7055
69 | -0.015952 | -0.0039994 | 0.015957 | 0.0040024 | 5.2388e-06 | 3.0618e-06 | 0.024408 | 0.024408 | 0.024408 | 0.9725 | -0.53123 | 0.97285 | -0.52434 | 6.7055
70 | 0.0081348 | 0.0020392 | -0.0081324 | -0.0020382 | 2.3933e-06 | 1.0212e-06 | 0.01245 | 0.01245 | 0.01245 | 0.97228 | -0.5356 | 0.97197 | -0.54178 | 3.4204
71 | -0.0013015 | -0.00032567 | 0.0013015 | 0.00032531 | 4.2798e-08 | -3.6047e-07 | 0.0019506 | 0.0019505 | 0.0019506 | 0.99273 | -0.13878 | 0.99277 | -0.13809 | 0.53588
72 | 0.0013015 | 0.00032567 | -0.0013014 | -0.00032616 | 5.8962e-08 | -4.9647e-07 | 0.0019506 | 0.0019508 | 0.0019508 | 0.99273 | -0.13878 | 0.99268 | -0.13973 | 0.53593
73 | 0.021778 | 0.0054678 | -0.02176 | -0.0054564 | 1.8752e-05 | 1.1395e-05 | 0.032646 | 0.032646 | 0.032646 | 0.99277 | -0.13809 | 0.99183 | -0.15615 | 8.9688
74 | -0.02308 | -0.0057931 | 0.023101 | 0.0058061 | 2.1291e-05 | 1.3012e-05 | 0.034597 | 0.034596 | 0.034597 | 0.99277 | -0.13809 | 0.99377 | -0.11876 | 9.5046
75 | -0.019264 | -0.0048303 | 0.019268 | 0.0048327 | 3.9909e-06 | 2.3952e-06 | 0.029151 | 0.029151 | 0.029151 | 0.98338 | -0.31949 | 0.9836 | -0.31514 | 8.0084
76 | -0.029642 | -0.0074326 | 0.029663 | 0.007446 | 2.1504e-05 | 1.34e-05 | 0.044844 | 0.044844 | 0.044844 | 0.9836 | -0.31514 | 0.98438 | -0.29993 | 12.3198
77 | -0.01387 | -0.003477 | 0.013875 | 0.0034799 | 5.1565e-06 | 2.8971e-06 | 0.020898 | 0.020898 | 0.020898 | 0.98764 | -0.23658 | 0.98804 | -0.22878 | 5.7411
78 | 0.01387 | 0.003477 | -0.013868 | -0.0034756 | 2.4135e-06 | 1.3561e-06 | 0.020898 | 0.020898 | 0.020898 | 0.98764 | -0.23658 | 0.98745 | -0.24023 | 5.7412
79 | 0.084586 | 0.02131 | -0.084535 | -0.021278 | 5.0425e-05 | 3.2166e-05 | 0.12743 | 0.12743 | 0.12743 | 0.98804 | -0.22878 | 0.9874 | -0.24125 | 35.0076
80 | 0.028956 | 0.0072829 | -0.028945 | -0.0072758 | 1.1484e-05 | 7.1381e-06 | 0.043322 | 0.043322 | 0.043322 | 0.99478 | -0.099178 | 0.99435 | -0.10748 | 11.9018
81 | 0.02176 | 0.0054564 | -0.021758 | -0.0054554 | 1.7099e-06 | 1.0391e-06 | 0.032646 | 0.032646 | 0.032646 | 0.99183 | -0.15615 | 0.99175 | -0.1578 | 8.9688
82 | -0.026016 | -0.0065365 | 0.02603 | 0.0065452 | 1.4013e-05 | 8.6494e-06 | 0.03896 | 0.03896 | 0.03896 | 0.99377 | -0.11876 | 0.99435 | -0.10748 | 10.7033
83 | 0.01538 | 0.0038569 | -0.015376 | -0.0038547 | 3.7251e-06 | 2.1435e-06 | 0.023077 | 0.023077 | 0.023077 | 0.99175 | -0.1578 | 0.99149 | -0.16288 | 6.3398
84 | 0.015376 | 0.0038547 | -0.015374 | -0.0038534 | 2.3186e-06 | 1.3342e-06 | 0.023077 | 0.023077 | 0.023077 | 0.99149 | -0.16288 | 0.99132 | -0.16605 | 6.3398
85 | 0.015374 | 0.0038534 | -0.015373 | -0.0038528 | 1.0476e-06 | 6.0284e-07 | 0.023077 | 0.023077 | 0.023077 | 0.99132 | -0.16605 | 0.99125 | -0.16748 | 6.3398
86 | 0.02034 | 0.0050991 | -0.020335 | -0.0050965 | 4.3161e-06 | 2.6076e-06 | 0.030746 | 0.030747 | 0.030747 | 0.98438 | -0.29993 | 0.98415 | -0.30438 | 8.4468
87 | -0.050003 | -0.012545 | 0.050021 | 0.012556 | 1.7624e-05 | 1.1175e-05 | 0.07559 | 0.07559 | 0.07559 | 0.98438 | -0.29993 | 0.98476 | -0.29254 | 20.7666
88 | 0.084535 | 0.021278 | -0.084487 | -0.021247 | 4.7827e-05 | 3.0509e-05 | 0.12743 | 0.12743 | 0.12743 | 0.9874 | -0.24125 | 0.98679 | -0.25309 | 35.0077
89 | -0.0099093 | -0.0024835 | 0.0099093 | 0.0024835 | 1.9063e-08 | 9.3221e-09 | 0.014983 | 0.014983 | 0.014983 | 0.98415 | -0.30442 | 0.98415 | -0.30438 | 4.1161
90 | -0.010207 | -0.0025581 | 0.010207 | 0.0025581 | 4.3136e-08 | 2.146e-08 | 0.015427 | 0.015427 | 0.015427 | 0.98454 | -0.29689 | 0.98454 | -0.2968 | 4.2381
91 | -0.020477 | -0.005132 | 0.020481 | 0.0051345 | 4.1606e-06 | 2.5154e-06 | 0.030948 | 0.030948 | 0.030948 | 0.98454 | -0.2968 | 0.98476 | -0.29254 | 8.5023
92 | -0.070501 | -0.017691 | 0.070634 | 0.017775 | 0.00013288 | 8.4642e-05 | 0.10654 | 0.10654 | 0.10654 | 0.98476 | -0.29254 | 0.98679 | -0.25309 | 29.2688

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.55733 | 0.14213

## res_load
| p_mw | q_mvar
0 | 0.0092466 | 0.0023174
1 | 0.015847 | 0.0039716
2 | 0.010197 | 0.0025555
3 | 0.019168 | 0.004804
4 | 0.0037227 | 0.000933
5 | 0.0032293 | 0.00080933
6 | 0.0054023 | 0.0013539
7 | 0.0082839 | 0.0020761
8 | 0.003079 | 0.00077166
9 | 0.0053945 | 0.001352
10 | 0.0089739 | 0.0022491
11 | 0.003234 | 0.00081052
12 | 0.0066883 | 0.0016762
13 | 0.0059821 | 0.0014993
14 | 0.0092536 | 0.0023192
15 | 0.013465 | 0.0033747
16 | 0.0088125 | 0.0022086
17 | 0.0048785 | 0.0012227
18 | 0.0019967 | 0.00050043
19 | 0.037053 | 0.0092865
20 | 0.0036762 | 0.00092135
21 | 0.011425 | 0.0028635
22 | 0.023572 | 0.0059077
23 | 0.010518 | 0.002636
24 | 0.0019831 | 0.00049702
25 | 0.0078134 | 0.0019582
26 | 0.0071807 | 0.0017997
27 | 0.09701 | 0.024313
28 | 0.0013014 | 0.00032616
29 | 0.010374 | 0.0025999
30 | 0.013868 | 0.0034756
31 | 0.0051822 | 0.0012988
32 | 0.0029143 | 0.00073038
33 | 0.006378 | 0.0015985
34 | 0.010407 | 0.0026081
35 | 0.0082879 | 0.0020771
36 | 0.0044164 | 0.0011068
37 | 0.010281 | 0.0025767
38 | 0.0052778 | 0.0013228
39 | 0.0084702 | 0.0021228
40 | 0.02809 | 0.0070399
41 | 0.004002 | 0.001003
42 | 0.00082857 | 0.00020766
43 | 0.0081324 | 0.0020382
44 | 0.0099093 | 0.0024835
45 | 0.010426 | 0.002613
46 | 0.0029152 | 0.00073061
47 | 0.010207 | 0.0025581
48 | 0.01027 | 0.0025738
49 | 0.015373 | 0.0038528
50 | 0.013853 | 0.0034719

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1