## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-244_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-244_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-244_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_261-244_0_4_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_261-244_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-244_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_261-244_0_4_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_261-244_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_261-244_0_4_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_261-244_0_4_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_261-244_0_4_node_52 | 0.4 | n |  | TRUE
11 | bus_LV_261-244_0_4_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_261-244_0_4_node_30 | 0.4 | n |  | TRUE
13 | bus_LV_261-244_0_4_node_42 | 0.4 | n |  | TRUE
14 | bus_LV_261-244_0_4_node_38 | 0.4 | n |  | TRUE
15 | bus_LV_261-244_0_4_node_51 | 0.4 | n |  | TRUE
16 | bus_LV_261-244_0_4_node_33 | 0.4 | n |  | TRUE
17 | bus_LV_261-244_0_4_node_23 | 0.4 | n |  | TRUE
18 | bus_LV_261-244_0_4_node_24 | 0.4 | n |  | TRUE
19 | bus_LV_261-244_0_4_node_55 | 0.4 | n |  | TRUE
20 | bus_LV_261-244_0_4_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_261-244_0_4_node_57 | 0.4 | n |  | TRUE
22 | bus_LV_261-244_0_4_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_261-244_0_4_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_261-244_0_4_node_58 | 0.4 | n |  | TRUE
25 | bus_LV_261-244_0_4_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_261-244_0_4_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_261-244_0_4_node_12 | 0.4 | n |  | TRUE
28 | bus_LV_261-244_0_4_node_53 | 0.4 | n |  | TRUE
29 | bus_LV_261-244_0_4_node_47 | 0.4 | n |  | TRUE
30 | bus_LV_261-244_0_4_node_54 | 0.4 | n |  | TRUE
31 | bus_LV_261-244_0_4_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_261-244_0_4_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_261-244_0_4_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_261-244_0_4_node_45 | 0.4 | n |  | TRUE
35 | bus_LV_261-244_0_4_node_14 | 0.4 | n |  | TRUE
36 | bus_LV_261-244_0_4_node_28 | 0.4 | n |  | TRUE
37 | bus_LV_261-244_0_4_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_261-244_0_4_node_48 | 0.4 | n |  | TRUE
39 | bus_LV_261-244_0_4_node_50 | 0.4 | n |  | TRUE
40 | bus_LV_261-244_0_4_node_40 | 0.4 | n |  | TRUE
41 | bus_LV_261-244_0_4_node_59 | 0.4 | n |  | TRUE
42 | bus_LV_261-244_0_4_node_56 | 0.4 | n |  | TRUE
43 | bus_LV_261-244_0_4_node_44 | 0.4 | n |  | TRUE
44 | bus_LV_261-244_0_4_node_49 | 0.4 | n |  | TRUE
45 | bus_LV_261-244_0_4_node_39 | 0.4 | n |  | TRUE
46 | bus_LV_261-244_0_4_node_46 | 0.4 | n |  | TRUE
47 | bus_LV_261-244_0_4_node_34 | 0.4 | n |  | TRUE
48 | bus_LV_261-244_0_4_node_32 | 0.4 | n |  | TRUE
49 | bus_LV_261-244_0_4_node_35 | 0.4 | n |  | TRUE
50 | bus_LV_261-244_0_4_node_43 | 0.4 | n |  | TRUE
51 | bus_LV_261-244_0_4_node_36 | 0.4 | n |  | TRUE
52 | bus_LV_261-244_0_4_node_37 | 0.4 | n |  | TRUE
53 | bus_LV_261-244_0_4_node_41 | 0.4 | n |  | TRUE
54 | bus_MV_524_0_node_161 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-244_0_4_load_0 | 0 | 0.034849 | 0.008734 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-244_0_4_load_1 | 1 | 0.011781 | 0.0029526 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-244_0_4_load_4 | 4 | 0.024188 | 0.0060621 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-244_0_4_load_11 | 8 | 0.017007 | 0.0042623 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-244_0_4_load_8 | 9 | 0.02548 | 0.0063858 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-244_0_4_load_30 | 12 | 0.016951 | 0.0042483 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-244_0_4_load_42 | 13 | 0.013308 | 0.0033353 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-244_0_4_load_51 | 15 | 0.005747 | 0.0014403 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-244_0_4_load_55 | 19 | 0.00090529 | 0.00022689 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-244_0_4_load_57 | 21 | 0.047025 | 0.011785 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-244_0_4_load_58 | 24 | 0.028678 | 0.0071874 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-244_0_4_load_12 | 27 | 0.019098 | 0.0047864 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-244_0_4_load_53 | 28 | 0.003038 | 0.00076139 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-244_0_4_load_47 | 29 | 0.024275 | 0.0060839 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-244_0_4_load_54 | 30 | 0.011295 | 0.0028309 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-244_0_4_load_31 | 33 | 0.020441 | 0.0051231 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-244_0_4_load_45 | 34 | 0.019959 | 0.0050021 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-244_0_4_load_14 | 35 | 0.003696 | 0.00092631 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-244_0_4_load_28 | 36 | 0.024852 | 0.0062284 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-244_0_4_load_27 | 37 | 0.016923 | 0.0042413 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-244_0_4_load_50 | 39 | 0.023501 | 0.0058898 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-244_0_4_load_59 | 41 | 0.0287 | 0.0071929 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-244_0_4_load_56 | 42 | 0.019852 | 0.0049754 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-244_0_4_load_49 | 44 | 0.022583 | 0.0056599 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-244_0_4_load_34 | 47 | 0.010763 | 0.0026974 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-244_0_4_load_35 | 49 | 0.013655 | 0.0034222 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-244_0_4_load_36 | 51 | 0.023348 | 0.0058515 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-244_0_4_load_37 | 52 | 0.012932 | 0.0032411 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-244_0_4_load_41 | 53 | 0.020222 | 0.005068 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 38 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-244_0_4_line_0 |  | 0 | 1 | 0.012931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-244_0_4_line_1 |  | 1 | 2 | 0.018816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-244_0_4_line_2 |  | 2 | 5 | 0.06262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_261-244_0_4_line_3 |  | 2 | 3 | 0.015085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_261-244_0_4_line_4 |  | 3 | 4 | 0.0086298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_261-244_0_4_line_5 |  | 4 | 6 | 0.02079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-244_0_4_line_6 |  | 5 | 10 | 0.023747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_261-244_0_4_line_7 |  | 6 | 11 | 0.017383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-244_0_4_line_8 |  | 6 | 9 | 0.020086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-244_0_4_line_9 |  | 7 | 8 | 0.010706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-244_0_4_line_10 |  | 7 | 9 | 0.021735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-244_0_4_line_11 |  | 8 | 12 | 0.015473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-244_0_4_line_12 |  | 10 | 15 | 0.017726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-244_0_4_line_13 |  | 10 | 16 | 0.008078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_261-244_0_4_line_14 |  | 11 | 35 | 0.008184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-244_0_4_line_15 |  | 11 | 27 | 0.01863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-244_0_4_line_16 |  | 13 | 14 | 0.029202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-244_0_4_line_17 |  | 14 | 53 | 0.015922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_261-244_0_4_line_18 |  | 14 | 51 | 0.016974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_261-244_0_4_line_19 |  | 16 | 42 | 0.02904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_261-244_0_4_line_20 |  | 17 | 18 | 0.046846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-244_0_4_line_21 |  | 17 | 19 | 0.045636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-244_0_4_line_22 |  | 18 | 30 | 0.0006722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-244_0_4_line_23 |  | 18 | 28 | 0.0076242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-244_0_4_line_24 |  | 20 | 21 | 0.01301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-244_0_4_line_25 |  | 20 | 22 | 0.061856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-244_0_4_line_26 |  | 22 | 29 | 0.017489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-244_0_4_line_27 |  | 22 | 23 | 0.079758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-244_0_4_line_28 |  | 23 | 24 | 0.0087831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-244_0_4_line_29 |  | 24 | 41 | 0.015573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-244_0_4_line_30 |  | 25 | 26 | 0.058696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-244_0_4_line_31 |  | 25 | 27 | 0.025403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-244_0_4_line_32 |  | 26 | 28 | 0.028041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-244_0_4_line_33 |  | 29 | 40 | 0.015244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-244_0_4_line_34 |  | 31 | 32 | 0.031878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-244_0_4_line_35 |  | 31 | 33 | 0.028585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-244_0_4_line_36 |  | 32 | 34 | 0.024719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-244_0_4_line_37 |  | 34 | 46 | 0.034803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-244_0_4_line_38 |  | 35 | 36 | 0.016697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-244_0_4_line_39 |  | 36 | 37 | 0.022179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-244_0_4_line_40 |  | 38 | 39 | 0.017328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_261-244_0_4_line_41 |  | 39 | 53 | 0.00011817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_261-244_0_4_line_42 |  | 40 | 44 | 0.016771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-244_0_4_line_43 |  | 42 | 50 | 0.033206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_261-244_0_4_line_44 |  | 43 | 44 | 0.018655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_261-244_0_4_line_45 |  | 43 | 45 | 0.038483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_261-244_0_4_line_46 |  | 45 | 50 | 0.00141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_261-244_0_4_line_47 |  | 45 | 52 | 0.013875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_261-244_0_4_line_48 |  | 46 | 47 | 0.013657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-244_0_4_line_49 |  | 47 | 48 | 0.017177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-244_0_4_line_50 |  | 48 | 49 | 0.016364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-244_0_4_line_51 |  | 49 | 50 | 0.023158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-244_0_4_line_52 |  | 51 | 52 | 0.00048201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-244_0_4_trafo_48 | 0.63 MVA 20/0.4 kV | 54 | 38 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2680337.5399 | 1252776.4833 | 2680339.3317 | 1252775.6026 | 2680343.6014 | 1252774.0593 | 2680348.1959 | 1252774.1661 | 2680348.1946 | 1252775.9652
1 | 2680348.1803 | 1252794.7813 | 2680348.1946 | 1252775.9652
2 | 2680348.1803 | 1252794.7813 | 2680361.423 | 1252794.9054 | 2680366.5646 | 1252793.6186 | 2680377.1461 | 1252782.4205 | 2680379.7153 | 1252775.5057 | 2680383.5246 | 1252772.2995 | 2680389.9523 | 1252765.7818 | 2680394.9872 | 1252760.6908
3 | 2680348.1803 | 1252794.7813 | 2680333.0512 | 1252794.6427
4 | 2680333.0512 | 1252794.6427 | 2680332.9739 | 1252803.2721
5 | 2680332.7879 | 1252824.061 | 2680332.9739 | 1252803.2721
6 | 2680394.9872 | 1252760.6908 | 2680399.0042 | 1252756.6422 | 2680415.3868 | 1252748.9588
7 | 2680322.0276 | 1252837.3251 | 2680332.5974 | 1252825.8598 | 2680332.7879 | 1252824.061
8 | 2680332.7879 | 1252824.061 | 2680342.2544 | 1252824.3896 | 2680352.8602 | 1252823.9768
9 | 2680368.2755 | 1252838.8199 | 2680362.2464 | 1252847.667
10 | 2680368.2755 | 1252838.8199 | 2680353.905 | 1252823.9362 | 2680352.8602 | 1252823.9768
11 | 2680362.0982 | 1252863.139 | 2680362.2464 | 1252847.667
12 | 2680415.3868 | 1252748.9588 | 2680408.2734 | 1252732.7227
13 | 2680415.3868 | 1252748.9588 | 2680422.7601 | 1252745.612
14 | 2680322.0276 | 1252837.3251 | 2680327.4132 | 1252843.4874
15 | 2680322.0276 | 1252837.3251 | 2680320.197 | 1252839.3128 | 2680304.2807 | 1252839.9087
16 | 2680424.8641 | 1252816.838 | 2680411.1463 | 1252791.0584
17 | 2680424.8641 | 1252816.838 | 2680411.0303 | 1252824.7202
18 | 2680424.8641 | 1252816.838 | 2680439.7947 | 1252808.7637
19 | 2680422.7601 | 1252745.612 | 2680424.259 | 1252748.6012 | 2680436.2634 | 1252771.3208
20 | 2680280.5096 | 1252769.1672 | 2680275.5397 | 1252762.7951 | 2680269.5239 | 1252755.0857 | 2680269.539 | 1252753.9739 | 2680279.3587 | 1252745.5118 | 2680283.8634 | 1252733.3193 | 2680281.9976 | 1252732.8937
21 | 2680281.9976 | 1252732.8937 | 2680277.3112 | 1252733.4417 | 2680259.1266 | 1252742.1241 | 2680239.905 | 1252749.985
22 | 2680281.0412 | 1252768.7558 | 2680280.5096 | 1252769.1672
23 | 2680280.5096 | 1252769.1672 | 2680274.4784 | 1252773.8311
24 | 2680409.8031 | 1252886.7079 | 2680398.4101 | 1252892.9887
25 | 2680409.8031 | 1252886.7079 | 2680413.5383 | 1252894.5088 | 2680416.6351 | 1252900.9779 | 2680428.7695 | 1252895.4496 | 2680432.2246 | 1252893.8731 | 2680416.0913 | 1252869.8918
26 | 2680416.0913 | 1252869.8918 | 2680431.5408 | 1252861.6951
27 | 2680476.5379 | 1252871.1023 | 2680468.2331 | 1252880.2519 | 2680432.2246 | 1252893.8731 | 2680416.0913 | 1252869.8918
28 | 2680476.5379 | 1252871.1023 | 2680471.7982 | 1252870.026 | 2680468.2925 | 1252871.7861
29 | 2680454.3751 | 1252878.7737 | 2680468.2925 | 1252871.7861
30 | 2680281.4128 | 1252846.159 | 2680255.7458 | 1252793.3386
31 | 2680281.4128 | 1252846.159 | 2680289.5478 | 1252845.6133 | 2680299.3222 | 1252845.5012 | 2680304.2807 | 1252839.9087
32 | 2680255.7458 | 1252793.3386 | 2680255.769 | 1252791.6266 | 2680257.031 | 1252788.1633 | 2680258.9873 | 1252785.8103 | 2680274.4784 | 1252773.8311
33 | 2680445.0069 | 1252854.5507 | 2680431.5408 | 1252861.6951
34 | 2680466.3217 | 1252727.1452 | 2680479.8959 | 1252721.214 | 2680484.3798 | 1252720.0184 | 2680489.4698 | 1252718.6532 | 2680496.5414 | 1252719.739
35 | 2680466.3217 | 1252727.1452 | 2680476.3931 | 1252753.8973
36 | 2680496.5414 | 1252719.739 | 2680497.8378 | 1252723.1925 | 2680505.2278 | 1252742.8812
37 | 2680517.4579 | 1252775.4647 | 2680505.2278 | 1252742.8812
38 | 2680327.4132 | 1252843.4874 | 2680328.6265 | 1252844.8757 | 2680328.5892 | 1252859.7286
39 | 2680328.5892 | 1252859.7286 | 2680328.5335 | 1252881.9078
40 | 2680395.8721 | 1252833.3569 | 2680410.9276 | 1252824.7787
41 | 2680411.0303 | 1252824.7202 | 2680410.9276 | 1252824.7787
42 | 2680445.0069 | 1252854.5507 | 2680459.8759 | 1252846.7942
43 | 2680451.7761 | 1252800.6802 | 2680436.2634 | 1252771.3208
44 | 2680470.222 | 1252836.0793 | 2680472.2554 | 1252840.2767 | 2680469.3132 | 1252841.8713 | 2680459.8759 | 1252846.7942
45 | 2680470.222 | 1252836.0793 | 2680452.4232 | 1252801.9344
46 | 2680451.7761 | 1252800.6802 | 2680452.4232 | 1252801.9344
47 | 2680452.4232 | 1252801.9344 | 2680440.2187 | 1252808.5344
48 | 2680517.4579 | 1252775.4647 | 2680504.7292 | 1252780.4135
49 | 2680488.7192 | 1252786.6381 | 2680504.7292 | 1252780.4135
50 | 2680488.7192 | 1252786.6381 | 2680473.4229 | 1252792.4522
51 | 2680451.7761 | 1252800.6802 | 2680473.4229 | 1252792.4522
52 | 2680440.2187 | 1252808.5344 | 2680439.7947 | 1252808.7637

## bus_geodata
| x | y | coords
0 | 2680337.5399 | 1252776.4833
1 | 2680348.1946 | 1252775.9652
2 | 2680348.1803 | 1252794.7813
3 | 2680333.0512 | 1252794.6427
4 | 2680332.9739 | 1252803.2721
5 | 2680394.9872 | 1252760.6908
6 | 2680332.7879 | 1252824.061
7 | 2680368.2755 | 1252838.8199
8 | 2680362.2464 | 1252847.667
9 | 2680352.8602 | 1252823.9768
10 | 2680415.3868 | 1252748.9588
11 | 2680322.0276 | 1252837.3251
12 | 2680362.0982 | 1252863.139
13 | 2680411.1463 | 1252791.0584
14 | 2680424.8641 | 1252816.838
15 | 2680408.2734 | 1252732.7227
16 | 2680422.7601 | 1252745.612
17 | 2680281.9976 | 1252732.8937
18 | 2680280.5096 | 1252769.1672
19 | 2680239.905 | 1252749.985
20 | 2680409.8031 | 1252886.7079
21 | 2680398.4101 | 1252892.9887
22 | 2680416.0913 | 1252869.8918
23 | 2680476.5379 | 1252871.1023
24 | 2680468.2925 | 1252871.7861
25 | 2680281.4128 | 1252846.159
26 | 2680255.7458 | 1252793.3386
27 | 2680304.2807 | 1252839.9087
28 | 2680274.4784 | 1252773.8311
29 | 2680431.5408 | 1252861.6951
30 | 2680281.0412 | 1252768.7558
31 | 2680466.3217 | 1252727.1452
32 | 2680496.5414 | 1252719.739
33 | 2680476.3931 | 1252753.8973
34 | 2680505.2278 | 1252742.8812
35 | 2680327.4132 | 1252843.4874
36 | 2680328.5892 | 1252859.7286
37 | 2680328.5335 | 1252881.9078
38 | 2680395.8721 | 1252833.3569
39 | 2680410.9276 | 1252824.7787
40 | 2680445.0069 | 1252854.5507
41 | 2680454.3751 | 1252878.7737
42 | 2680436.2634 | 1252771.3208
43 | 2680470.222 | 1252836.0793
44 | 2680459.8759 | 1252846.7942
45 | 2680452.4232 | 1252801.9344
46 | 2680517.4579 | 1252775.4647
47 | 2680504.7292 | 1252780.4135
48 | 2680488.7192 | 1252786.6381
49 | 2680473.4229 | 1252792.4522
50 | 2680451.7761 | 1252800.6802
51 | 2680439.7947 | 1252808.7637
52 | 2680440.2187 | 1252808.5344
53 | 2680411.0303 | 1252824.7202
54 | 2680424.8641 | 1252816.838

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98337 | -0.31897 | 0.034849 | 0.008734
1 | 0.98379 | -0.31085 | 0.011781 | 0.0029526
2 | 0.9846 | -0.29506 | 0 | 0
3 | 0.98403 | -0.30615 | 0 | 0
4 | 0.98337 | -0.31885 | 0.024188 | 0.0060621
5 | 0.98764 | -0.23611 | 0 | 0
6 | 0.98069 | -0.37118 | 0 | 0
7 | 0.9789 | -0.40625 | 0 | 0
8 | 0.97857 | -0.41287 | 0.017007 | 0.0042623
9 | 0.97959 | -0.39284 | 0.02548 | 0.0063858
10 | 0.9888 | -0.21385 | 0 | 0
11 | 0.97941 | -0.39635 | 0 | 0
12 | 0.97832 | -0.41764 | 0.016951 | 0.0042483
13 | 0.99561 | -0.083351 | 0.013308 | 0.0033353
14 | 0.99597 | -0.07652 | 0 | 0
15 | 0.9887 | -0.21567 | 0.005747 | 0.0014403
16 | 0.9892 | -0.20609 | 0 | 0
17 | 0.9771 | -0.44161 | 0 | 0
18 | 0.97714 | -0.44083 | 0 | 0
19 | 0.97706 | -0.44236 | 0.00090529 | 0.00022689
20 | 0.98172 | -0.35131 | 0 | 0
21 | 0.98116 | -0.36238 | 0.047025 | 0.011785
22 | 0.98441 | -0.29885 | 0 | 0
23 | 0.98018 | -0.38151 | 0 | 0
24 | 0.97971 | -0.39066 | 0.028678 | 0.0071874
25 | 0.97845 | -0.41503 | 0 | 0
26 | 0.97762 | -0.43134 | 0 | 0
27 | 0.97881 | -0.40799 | 0.019098 | 0.0047864
28 | 0.97723 | -0.43913 | 0.003038 | 0.00076139
29 | 0.9861 | -0.26606 | 0.024275 | 0.0060839
30 | 0.97713 | -0.44097 | 0.011295 | 0.0028309
31 | 0.98664 | -0.25624 | 0 | 0
32 | 0.98724 | -0.24458 | 0 | 0
33 | 0.98611 | -0.26671 | 0.020441 | 0.0051231
34 | 0.98771 | -0.23555 | 0.019959 | 0.0050021
35 | 0.97906 | -0.40312 | 0.003696 | 0.00092631
36 | 0.97841 | -0.41581 | 0.024852 | 0.0062284
37 | 0.97807 | -0.42264 | 0.016923 | 0.0042413
38 | 1 | 0 | -0.55431 | -0.14145
39 | 0.99782 | -0.041248 | 0.023501 | 0.0058898
40 | 0.98792 | -0.23096 | 0 | 0
41 | 0.9793 | -0.39878 | 0.0287 | 0.0071929
42 | 0.99065 | -0.17822 | 0.019852 | 0.0049754
43 | 0.99121 | -0.16744 | 0 | 0
44 | 0.98991 | -0.1925 | 0.022583 | 0.0056599
45 | 0.99256 | -0.14166 | 0 | 0
46 | 0.989 | -0.21046 | 0 | 0
47 | 0.98951 | -0.20063 | 0.010763 | 0.0026974
48 | 0.99031 | -0.185 | 0 | 0
49 | 0.99108 | -0.17013 | 0.013655 | 0.0034222
50 | 0.99246 | -0.14353 | 0 | 0
51 | 0.99406 | -0.11298 | 0.023348 | 0.0058515
52 | 0.994 | -0.11397 | 0.012932 | 0.0032411
53 | 0.99781 | -0.041518 | 0.020222 | 0.005068
54 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.034849 | -0.008734 | 0.034863 | 0.0087425 | 1.3485e-05 | 8.4661e-06 | 0.052733 | 0.052733 | 0.052733 | 0.98337 | -0.31897 | 0.98379 | -0.31085 | 14.487
1 | -0.046643 | -0.011695 | 0.046679 | 0.011717 | 3.5122e-05 | 2.2239e-05 | 0.070552 | 0.070552 | 0.070552 | 0.98379 | -0.31085 | 0.9846 | -0.29506 | 19.3823
2 | -0.21093 | -0.053195 | 0.21153 | 0.053574 | 0.000597 | 0.00037889 | 0.31889 | 0.31889 | 0.31889 | 0.9846 | -0.29506 | 0.98764 | -0.23611 | 21.9021
3 | 0.16425 | 0.041478 | -0.16416 | -0.041423 | 8.7221e-05 | 5.5055e-05 | 0.24834 | 0.24834 | 0.24834 | 0.9846 | -0.29506 | 0.98403 | -0.30615 | 17.0566
4 | 0.16416 | 0.041423 | -0.16406 | -0.041359 | 9.9794e-05 | 6.3649e-05 | 0.24834 | 0.24834 | 0.24834 | 0.98403 | -0.30615 | 0.98337 | -0.31885 | 34.1131
5 | 0.13988 | 0.035297 | -0.13953 | -0.035074 | 0.00034954 | 0.00022344 | 0.21174 | 0.21174 | 0.21174 | 0.98337 | -0.31885 | 0.98069 | -0.37118 | 58.1712
6 | -0.21153 | -0.053574 | 0.21175 | 0.053718 | 0.0002264 | 0.00014368 | 0.31889 | 0.31889 | 0.31889 | 0.98764 | -0.23611 | 0.9888 | -0.21385 | 21.902
7 | 0.079992 | 0.020116 | -0.079895 | -0.020055 | 9.6066e-05 | 6.1263e-05 | 0.1214 | 0.1214 | 0.1214 | 0.98069 | -0.37118 | 0.97941 | -0.39635 | 33.3507
8 | 0.059535 | 0.014958 | -0.059473 | -0.014919 | 6.1482e-05 | 3.9095e-05 | 0.090347 | 0.090347 | 0.090347 | 0.98069 | -0.37118 | 0.97959 | -0.39284 | 24.8205
9 | 0.033972 | 0.0085195 | -0.033961 | -0.0085128 | 1.0707e-05 | 6.718e-06 | 0.051642 | 0.051642 | 0.051642 | 0.9789 | -0.40625 | 0.97857 | -0.41287 | 14.1875
10 | -0.033972 | -0.0085195 | 0.033994 | 0.0085332 | 2.1737e-05 | 1.3638e-05 | 0.051642 | 0.051642 | 0.051642 | 0.9789 | -0.40625 | 0.97959 | -0.39284 | 14.1875
11 | 0.016955 | 0.0042505 | -0.016951 | -0.0042483 | 3.8568e-06 | 2.274e-06 | 0.025782 | 0.025782 | 0.025782 | 0.97857 | -0.41287 | 0.97832 | -0.41764 | 7.0829
12 | 0.0057475 | 0.0014404 | -0.005747 | -0.0014403 | 4.9729e-07 | 9.0914e-08 | 0.0086493 | 0.0086494 | 0.0086494 | 0.9888 | -0.21385 | 0.9887 | -0.21567 | 2.3762
13 | -0.2175 | -0.055158 | 0.21758 | 0.05521 | 8.1247e-05 | 5.1584e-05 | 0.32754 | 0.32754 | 0.32754 | 0.9888 | -0.21385 | 0.9892 | -0.20609 | 22.496
14 | 0.045516 | 0.011424 | -0.045501 | -0.011415 | 1.4679e-05 | 9.2915e-06 | 0.069159 | 0.069159 | 0.069159 | 0.97941 | -0.39635 | 0.97906 | -0.40312 | 18.9997
15 | 0.03438 | 0.0086301 | -0.03436 | -0.0086181 | 1.9064e-05 | 1.1967e-05 | 0.052238 | 0.052238 | 0.052238 | 0.97941 | -0.39635 | 0.97881 | -0.40799 | 14.3511
16 | -0.013308 | -0.0033353 | 0.013312 | 0.0033377 | 4.3321e-06 | 2.3927e-06 | 0.01989 | 0.01989 | 0.01989 | 0.99561 | -0.083351 | 0.99597 | -0.07652 | 5.4642
17 | -0.50698 | -0.12924 | 0.50783 | 0.12978 | 0.00085812 | 0.00054837 | 0.75822 | 0.75821 | 0.75822 | 0.99597 | -0.07652 | 0.99781 | -0.041518 | 52.0752
18 | 0.49366 | 0.1259 | -0.4928 | -0.12534 | 0.00086746 | 0.00055429 | 0.73833 | 0.73833 | 0.73833 | 0.99597 | -0.07652 | 0.99406 | -0.11298 | 50.7092
19 | -0.21758 | -0.05521 | 0.21787 | 0.055395 | 0.00029208 | 0.00018544 | 0.32754 | 0.32754 | 0.32754 | 0.9892 | -0.20609 | 0.99065 | -0.17822 | 22.496
20 | -0.00090532 | -0.00022634 | 0.00090535 | 0.00022577 | 3.3378e-08 | -5.6543e-07 | 0.0013785 | 0.0013783 | 0.0013785 | 0.9771 | -0.44161 | 0.97714 | -0.44083 | 0.37871
21 | 0.00090532 | 0.00022634 | -0.00090529 | -0.00022689 | 3.2525e-08 | -5.5077e-07 | 0.0013785 | 0.0013787 | 0.0013787 | 0.9771 | -0.44161 | 0.97706 | -0.44236 | 0.37877
22 | 0.011295 | 0.0028309 | -0.011295 | -0.0028309 | 7.4581e-08 | 3.9312e-08 | 0.017201 | 0.017201 | 0.017201 | 0.97714 | -0.44083 | 0.97713 | -0.44097 | 4.7255
23 | -0.012201 | -0.0030567 | 0.012202 | 0.0030572 | 9.8691e-07 | 5.3611e-07 | 0.018579 | 0.018579 | 0.018579 | 0.97714 | -0.44083 | 0.97723 | -0.43913 | 5.1042
24 | 0.047049 | 0.011801 | -0.047025 | -0.011785 | 2.4813e-05 | 1.5716e-05 | 0.071317 | 0.071317 | 0.071317 | 0.98172 | -0.35131 | 0.98116 | -0.36238 | 19.5926
25 | -0.047049 | -0.011801 | 0.047167 | 0.011876 | 0.00011798 | 7.4722e-05 | 0.071317 | 0.071317 | 0.071317 | 0.98172 | -0.35131 | 0.98441 | -0.29885 | 19.5926
26 | -0.10481 | -0.026423 | 0.10497 | 0.026529 | 0.00016473 | 0.0001052 | 0.15848 | 0.15848 | 0.15848 | 0.98441 | -0.29885 | 0.9861 | -0.26606 | 43.5392
27 | 0.057642 | 0.014548 | -0.057414 | -0.014403 | 0.00022725 | 0.00014443 | 0.087166 | 0.087166 | 0.087166 | 0.98441 | -0.29885 | 0.98018 | -0.38151 | 23.9467
28 | 0.057414 | 0.014403 | -0.057389 | -0.014387 | 2.5025e-05 | 1.5905e-05 | 0.087166 | 0.087166 | 0.087166 | 0.98018 | -0.38151 | 0.97971 | -0.39066 | 23.9468
29 | 0.028711 | 0.0071998 | -0.0287 | -0.0071929 | 1.1106e-05 | 6.9118e-06 | 0.043609 | 0.043609 | 0.043609 | 0.97971 | -0.39066 | 0.9793 | -0.39878 | 11.9805
30 | 0.015257 | 0.0038287 | -0.015245 | -0.0038219 | 1.1852e-05 | 6.8488e-06 | 0.023205 | 0.023205 | 0.023205 | 0.97845 | -0.41503 | 0.97762 | -0.43134 | 6.375
31 | -0.015257 | -0.0038287 | 0.015262 | 0.0038317 | 5.1293e-06 | 2.9636e-06 | 0.023205 | 0.023205 | 0.023205 | 0.97845 | -0.41503 | 0.97881 | -0.40799 | 6.3749
32 | 0.015245 | 0.0038219 | -0.01524 | -0.0038186 | 5.6622e-06 | 3.2723e-06 | 0.023205 | 0.023205 | 0.023205 | 0.97762 | -0.43134 | 0.97723 | -0.43913 | 6.375
33 | -0.12925 | -0.032613 | 0.12947 | 0.032752 | 0.00021762 | 0.00013908 | 0.19511 | 0.19511 | 0.19511 | 0.9861 | -0.26606 | 0.98792 | -0.23096 | 53.6025
34 | -0.020451 | -0.0051292 | 0.020463 | 0.0051361 | 1.1374e-05 | 6.8718e-06 | 0.030845 | 0.030845 | 0.030845 | 0.98664 | -0.25624 | 0.98724 | -0.24458 | 8.474
35 | 0.020451 | 0.0051292 | -0.020441 | -0.0051231 | 1.0199e-05 | 6.1624e-06 | 0.030845 | 0.030845 | 0.030845 | 0.98664 | -0.25624 | 0.98611 | -0.26671 | 8.474
36 | -0.020463 | -0.0051361 | 0.020472 | 0.0051414 | 8.8192e-06 | 5.3281e-06 | 0.030845 | 0.030845 | 0.030845 | 0.98724 | -0.24458 | 0.98771 | -0.23555 | 8.4739
37 | -0.04043 | -0.010144 | 0.040479 | 0.010174 | 4.8426e-05 | 3.0546e-05 | 0.060913 | 0.060913 | 0.060913 | 0.98771 | -0.23555 | 0.989 | -0.21046 | 16.7345
38 | 0.041805 | 0.010489 | -0.04178 | -0.010473 | 2.528e-05 | 1.5969e-05 | 0.063541 | 0.063541 | 0.063541 | 0.97906 | -0.40312 | 0.97841 | -0.41581 | 17.4564
39 | 0.016928 | 0.0042445 | -0.016923 | -0.0042413 | 5.5131e-06 | 3.25e-06 | 0.025746 | 0.025746 | 0.025746 | 0.97841 | -0.41581 | 0.97807 | -0.42264 | 7.0731
40 | 0.55266 | 0.14145 | -0.55156 | -0.14075 | 0.0011014 | 0.000704 | 0.82342 | 0.82342 | 0.82342 | 1 | 0 | 0.99782 | -0.041248 | 56.5533
41 | 0.52806 | 0.13486 | -0.52806 | -0.13485 | 6.8856e-06 | 4.4006e-06 | 0.78837 | 0.78837 | 0.78837 | 0.99782 | -0.041248 | 0.99781 | -0.041518 | 54.1463
42 | -0.12947 | -0.032752 | 0.12971 | 0.032905 | 0.00023942 | 0.00015301 | 0.19511 | 0.19511 | 0.19511 | 0.98792 | -0.23096 | 0.98991 | -0.1925 | 53.6025
43 | -0.23773 | -0.060371 | 0.23812 | 0.060624 | 0.00039755 | 0.00025272 | 0.35736 | 0.35736 | 0.35736 | 0.99065 | -0.17822 | 0.99246 | -0.14353 | 24.544
44 | 0.15247 | 0.038682 | -0.15229 | -0.038565 | 0.00018352 | 0.00011697 | 0.22906 | 0.22906 | 0.22906 | 0.99121 | -0.16744 | 0.98991 | -0.1925 | 31.4642
45 | -0.15247 | -0.038682 | 0.15266 | 0.038801 | 0.00018929 | 0.00011916 | 0.22906 | 0.22906 | 0.22906 | 0.99121 | -0.16744 | 0.99256 | -0.14166 | 15.7321
46 | 0.30322 | 0.077047 | -0.3032 | -0.077029 | 2.7361e-05 | 1.7438e-05 | 0.45496 | 0.45496 | 0.45496 | 0.99256 | -0.14166 | 0.99246 | -0.14353 | 31.2472
47 | -0.45589 | -0.11585 | 0.45649 | 0.11624 | 0.0006086 | 0.00038879 | 0.68402 | 0.68402 | 0.68402 | 0.99256 | -0.14166 | 0.994 | -0.11397 | 46.9793
48 | -0.040479 | -0.010174 | 0.040498 | 0.010186 | 1.9002e-05 | 1.1986e-05 | 0.060913 | 0.060913 | 0.060913 | 0.989 | -0.21046 | 0.98951 | -0.20063 | 16.7344
49 | -0.051261 | -0.012884 | 0.051299 | 0.012908 | 3.829e-05 | 2.4285e-05 | 0.077098 | 0.077098 | 0.077098 | 0.98951 | -0.20063 | 0.99031 | -0.185 | 21.1809
50 | -0.051299 | -0.012908 | 0.051335 | 0.012931 | 3.6476e-05 | 2.3134e-05 | 0.077098 | 0.077098 | 0.077098 | 0.99031 | -0.185 | 0.99108 | -0.17013 | 21.1809
51 | -0.06499 | -0.016353 | 0.065073 | 0.016406 | 8.2723e-05 | 5.2644e-05 | 0.0976 | 0.097599 | 0.0976 | 0.99108 | -0.17013 | 0.99246 | -0.14353 | 26.8131
52 | 0.46945 | 0.11949 | -0.46943 | -0.11948 | 2.2356e-05 | 1.4283e-05 | 0.70338 | 0.70338 | 0.70338 | 0.99406 | -0.11298 | 0.994 | -0.11397 | 48.3088

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.55431 | 0.14145

## res_load
| p_mw | q_mvar
0 | 0.034849 | 0.008734
1 | 0.011781 | 0.0029526
2 | 0.024188 | 0.0060621
3 | 0.017007 | 0.0042623
4 | 0.02548 | 0.0063858
5 | 0.016951 | 0.0042483
6 | 0.013308 | 0.0033353
7 | 0.005747 | 0.0014403
8 | 0.00090529 | 0.00022689
9 | 0.047025 | 0.011785
10 | 0.028678 | 0.0071874
11 | 0.019098 | 0.0047864
12 | 0.003038 | 0.00076139
13 | 0.024275 | 0.0060839
14 | 0.011295 | 0.0028309
15 | 0.020441 | 0.0051231
16 | 0.019959 | 0.0050021
17 | 0.003696 | 0.00092631
18 | 0.024852 | 0.0062284
19 | 0.016923 | 0.0042413
20 | 0.023501 | 0.0058898
21 | 0.0287 | 0.0071929
22 | 0.019852 | 0.0049754
23 | 0.022583 | 0.0056599
24 | 0.010763 | 0.0026974
25 | 0.013655 | 0.0034222
26 | 0.023348 | 0.0058515
27 | 0.012932 | 0.0032411
28 | 0.020222 | 0.005068

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1