## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-268_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-268_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-268_0_4_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_261-268_0_4_node_8 | 0.4 | n |  | TRUE
4 | bus_LV_261-268_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_261-268_0_4_node_13 | 0.4 | n |  | TRUE
6 | bus_LV_261-268_0_4_node_31 | 0.4 | n |  | TRUE
7 | bus_LV_261-268_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_261-268_0_4_node_34 | 0.4 | n |  | TRUE
9 | bus_LV_261-268_0_4_node_35 | 0.4 | n |  | TRUE
10 | bus_LV_261-268_0_4_node_32 | 0.4 | n |  | TRUE
11 | bus_LV_261-268_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_261-268_0_4_node_39 | 0.4 | n |  | TRUE
13 | bus_LV_261-268_0_4_node_30 | 0.4 | n |  | TRUE
14 | bus_LV_261-268_0_4_node_29 | 0.4 | n |  | TRUE
15 | bus_LV_261-268_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_261-268_0_4_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_261-268_0_4_node_24 | 0.4 | n |  | TRUE
18 | bus_LV_261-268_0_4_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_261-268_0_4_node_41 | 0.4 | n |  | TRUE
20 | bus_LV_261-268_0_4_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_261-268_0_4_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_261-268_0_4_node_21 | 0.4 | n |  | TRUE
23 | bus_LV_261-268_0_4_node_33 | 0.4 | n |  | TRUE
24 | bus_LV_261-268_0_4_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_261-268_0_4_node_42 | 0.4 | n |  | TRUE
26 | bus_LV_261-268_0_4_node_27 | 0.4 | n |  | TRUE
27 | bus_LV_261-268_0_4_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_261-268_0_4_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_261-268_0_4_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_261-268_0_4_node_44 | 0.4 | n |  | TRUE
31 | bus_LV_261-268_0_4_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_261-268_0_4_node_38 | 0.4 | n |  | TRUE
33 | bus_LV_261-268_0_4_node_40 | 0.4 | n |  | TRUE
34 | bus_LV_261-268_0_4_node_22 | 0.4 | n |  | TRUE
35 | bus_LV_261-268_0_4_node_43 | 0.4 | n |  | TRUE
36 | bus_LV_261-268_0_4_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_261-268_0_4_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_261-268_0_4_node_36 | 0.4 | n |  | TRUE
39 | bus_LV_261-268_0_4_node_37 | 0.4 | n |  | TRUE
40 | bus_MV_534_0_node_100 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-268_0_4_load_0 | 0 | 0.031684 | 0.0079407 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-268_0_4_load_31 | 6 | 0.037846 | 0.0094852 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-268_0_4_load_34 | 8 | 0.027879 | 0.0069872 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-268_0_4_load_35 | 9 | 0.018451 | 0.0046242 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-268_0_4_load_32 | 10 | 0.027801 | 0.0069675 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-268_0_4_load_39 | 12 | 0.037557 | 0.0094127 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-268_0_4_load_30 | 13 | 0.010148 | 0.0025433 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-268_0_4_load_29 | 14 | 0.016425 | 0.0041164 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-268_0_4_load_24 | 17 | 0.0050207 | 0.0012583 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-268_0_4_load_41 | 19 | 0.014285 | 0.0035802 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-268_0_4_load_21 | 22 | 0.024625 | 0.0061717 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-268_0_4_load_33 | 23 | 0.042986 | 0.010773 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-268_0_4_load_42 | 25 | 0.065624 | 0.016447 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-268_0_4_load_27 | 26 | 0.01273 | 0.0031905 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-268_0_4_load_25 | 28 | 0.0085609 | 0.0021456 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-268_0_4_load_44 | 30 | 0.010474 | 0.0026249 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-268_0_4_load_18 | 31 | 0.046295 | 0.011603 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-268_0_4_load_38 | 32 | 0.0072714 | 0.0018224 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-268_0_4_load_40 | 33 | 0.0090506 | 0.0022683 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-268_0_4_load_22 | 34 | 0.031256 | 0.0078335 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-268_0_4_load_43 | 35 | 0.013037 | 0.0032675 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-268_0_4_load_26 | 36 | 0.0066184 | 0.0016587 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-268_0_4_load_23 | 37 | 0.0082552 | 0.002069 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-268_0_4_load_36 | 38 | 0.009898 | 0.0024807 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-268_0_4_load_37 | 39 | 0.009021 | 0.0022609 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 32 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-268_0_4_line_0 |  | 0 | 1 | 0.019488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-268_0_4_line_1 |  | 1 | 2 | 0.067733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-268_0_4_line_2 |  | 2 | 3 | 0.0080308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-268_0_4_line_3 |  | 3 | 13 | 0.030176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-268_0_4_line_4 |  | 3 | 14 | 0.016292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-268_0_4_line_5 |  | 3 | 7 | 0.01789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-268_0_4_line_6 |  | 4 | 5 | 0.0085649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-268_0_4_line_7 |  | 4 | 6 | 0.020689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-268_0_4_line_8 |  | 5 | 23 | 0.011444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-268_0_4_line_9 |  | 5 | 11 | 0.009946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-268_0_4_line_10 |  | 7 | 8 | 0.011617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_261-268_0_4_line_11 |  | 7 | 9 | 0.013115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_261-268_0_4_line_12 |  | 7 | 10 | 0.02255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_261-268_0_4_line_13 |  | 8 | 32 | 0.011973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_261-268_0_4_line_14 |  | 9 | 30 | 0.014886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_261-268_0_4_line_15 |  | 10 | 23 | 0.014035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-268_0_4_line_16 |  | 11 | 12 | 0.01268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-268_0_4_line_17 |  | 15 | 16 | 0.02644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-268_0_4_line_18 |  | 15 | 17 | 0.020066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-268_0_4_line_19 |  | 16 | 18 | 0.022186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_261-268_0_4_line_20 |  | 16 | 19 | 0.028511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-268_0_4_line_21 |  | 17 | 27 | 0.068852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-268_0_4_line_22 |  | 18 | 24 | 0.0247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_261-268_0_4_line_23 |  | 18 | 25 | 0.01103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-268_0_4_line_24 |  | 19 | 33 | 0.016076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-268_0_4_line_25 |  | 20 | 21 | 0.027285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-268_0_4_line_26 |  | 20 | 22 | 0.011967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-268_0_4_line_27 |  | 21 | 26 | 0.014056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-268_0_4_line_28 |  | 22 | 34 | 0.012104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-268_0_4_line_29 |  | 24 | 30 | 0.025994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_261-268_0_4_line_30 |  | 25 | 35 | 0.016794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-268_0_4_line_31 |  | 27 | 28 | 0.02856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-268_0_4_line_32 |  | 27 | 29 | 0.022179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-268_0_4_line_33 |  | 28 | 36 | 0.019827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-268_0_4_line_34 |  | 29 | 31 | 0.0044485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-268_0_4_line_35 |  | 33 | 39 | 0.011596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-268_0_4_line_36 |  | 34 | 37 | 0.028066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-268_0_4_line_37 |  | 37 | 38 | 0.019577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-268_0_4_line_38 |  | 38 | 39 | 0.010504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-268_0_4_trafo_38 | 0.63 MVA 20/0.4 kV | 40 | 32 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2684852.8535 | 1246929.6635 | 2684869.5721 | 1246939.6773
1 | 2684816.9371 | 1246984.7905 | 2684819.0679 | 1246980.5289 | 2684823.3168 | 1246973.4289 | 2684831.1409 | 1246960.9093 | 2684839.2591 | 1246947.371 | 2684841.043 | 1246948.3528 | 2684852.8535 | 1246929.6635
2 | 2684810.2549 | 1246980.3361 | 2684813.3902 | 1246982.4269 | 2684816.9371 | 1246984.7905
3 | 2684810.2549 | 1246980.3361 | 2684812.1928 | 1246977.9398 | 2684826.1963 | 1246954.7448
4 | 2684810.2549 | 1246980.3361 | 2684807.8632 | 1246981.1803 | 2684805.1663 | 1246981.1861 | 2684802.0237 | 1246979.6067 | 2684795.8533 | 1246975.2702
5 | 2684805.587 | 1246992.4338 | 2684807.6984 | 1246989.0059 | 2684808.8651 | 1246989.8232 | 2684810.6675 | 1246986.869 | 2684813.3902 | 1246982.4269 | 2684810.2549 | 1246980.3361
6 | 2684844.4197 | 1247020.6434 | 2684846.8356 | 1247017.0531 | 2684849.205 | 1247013.5399
7 | 2684849.205 | 1247013.5399 | 2684832.3533 | 1247001.5383
8 | 2684844.4197 | 1247020.6434 | 2684836.4558 | 1247014.9697 | 2684835.1569 | 1247013.9267
9 | 2684844.4197 | 1247020.6434 | 2684852.5409 | 1247026.4194
10 | 2684805.587 | 1246992.4338 | 2684799.4822 | 1247002.3179
11 | 2684805.587 | 1246992.4338 | 2684794.9628 | 1246984.7435
12 | 2684805.587 | 1246992.4338 | 2684823.5131 | 1247004.5769 | 2684824.2136 | 1247005.1394
13 | 2684793.1905 | 1247012.5047 | 2684799.4822 | 1247002.3179
14 | 2684782.6152 | 1246976.4358 | 2684791.5456 | 1246982.27 | 2684794.9628 | 1246984.7435
15 | 2684824.2136 | 1247005.1394 | 2684835.1569 | 1247013.9267
16 | 2684852.5409 | 1247026.4194 | 2684845.3837 | 1247036.8862
17 | 2684715.9003 | 1246996.355 | 2684718.7865 | 1246991.0367 | 2684724.4588 | 1246994.7983 | 2684726.7393 | 1246991.6841 | 2684732.9477 | 1246999.1672
18 | 2684715.9003 | 1246996.355 | 2684719.887 | 1246996.4898 | 2684722.8844 | 1246998.1894 | 2684730.2752 | 1247008.4326
19 | 2684746.3153 | 1246981.434 | 2684732.9477 | 1246999.1672
20 | 2684732.9477 | 1246999.1672 | 2684740.816 | 1247011.0106 | 2684748.9375 | 1247022.771
21 | 2684769.4057 | 1247065.0813 | 2684735.1659 | 1247015.2108 | 2684730.2752 | 1247008.4326
22 | 2684746.3153 | 1246981.434 | 2684761.2075 | 1246961.6989
23 | 2684746.3153 | 1246981.434 | 2684747.7285 | 1246982.455 | 2684755.3788 | 1246987.7187
24 | 2684748.9375 | 1247022.771 | 2684758.073 | 1247035.9996
25 | 2684811.3829 | 1247113.1948 | 2684808.0183 | 1247115.5151 | 2684813.1604 | 1247123.0608 | 2684821.0844 | 1247134.6828
26 | 2684811.3829 | 1247113.1948 | 2684804.5824 | 1247103.3475
27 | 2684821.0844 | 1247134.6828 | 2684815.523 | 1247147.5913
28 | 2684797.7043 | 1247093.3877 | 2684804.5824 | 1247103.3475
29 | 2684761.2075 | 1246961.6989 | 2684764.5904 | 1246963.9045 | 2684778.2161 | 1246973.5619 | 2684782.6152 | 1246976.4358
30 | 2684755.3788 | 1246987.7187 | 2684762.0539 | 1246992.3114 | 2684769.7991 | 1246996.2551
31 | 2684769.4057 | 1247065.0813 | 2684785.7156 | 1247088.5264
32 | 2684750.3272 | 1247076.4838 | 2684769.4057 | 1247065.0813
33 | 2684797.0383 | 1247104.8025 | 2684785.7156 | 1247088.5264
34 | 2684750.3272 | 1247076.4838 | 2684748.0449 | 1247080.3022
35 | 2684758.073 | 1247035.9996 | 2684764.6623 | 1247045.5412
36 | 2684781.7561 | 1247070.2938 | 2684797.7043 | 1247093.3877
37 | 2684781.7561 | 1247070.2938 | 2684770.6314 | 1247054.1848
38 | 2684770.6314 | 1247054.1848 | 2684764.6623 | 1247045.5412

## bus_geodata
| x | y | coords
0 | 2684869.5721 | 1246939.6773
1 | 2684852.8535 | 1246929.6635
2 | 2684816.9371 | 1246984.7905
3 | 2684810.2549 | 1246980.3361
4 | 2684849.205 | 1247013.5399
5 | 2684844.4197 | 1247020.6434
6 | 2684832.3533 | 1247001.5383
7 | 2684805.587 | 1246992.4338
8 | 2684799.4822 | 1247002.3179
9 | 2684794.9628 | 1246984.7435
10 | 2684824.2136 | 1247005.1394
11 | 2684852.5409 | 1247026.4194
12 | 2684845.3837 | 1247036.8862
13 | 2684826.1963 | 1246954.7448
14 | 2684795.8533 | 1246975.2702
15 | 2684715.9003 | 1246996.355
16 | 2684732.9477 | 1246999.1672
17 | 2684730.2752 | 1247008.4326
18 | 2684746.3153 | 1246981.434
19 | 2684748.9375 | 1247022.771
20 | 2684811.3829 | 1247113.1948
21 | 2684821.0844 | 1247134.6828
22 | 2684804.5824 | 1247103.3475
23 | 2684835.1569 | 1247013.9267
24 | 2684761.2074 | 1246961.6989
25 | 2684755.3788 | 1246987.7187
26 | 2684815.523 | 1247147.5913
27 | 2684769.4057 | 1247065.0813
28 | 2684785.7156 | 1247088.5264
29 | 2684750.3272 | 1247076.4838
30 | 2684782.6152 | 1246976.4358
31 | 2684748.0449 | 1247080.3022
32 | 2684793.1905 | 1247012.5047
33 | 2684758.073 | 1247035.9996
34 | 2684797.7043 | 1247093.3877
35 | 2684769.7991 | 1246996.2551
36 | 2684797.0383 | 1247104.8025
37 | 2684781.7561 | 1247070.2938
38 | 2684770.6314 | 1247054.1848
39 | 2684764.6623 | 1247045.5412
40 | 2684805.587 | 1246992.4338

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99353 | -0.12419 | 0.031684 | 0.0079407
1 | 0.99409 | -0.11329 | 0 | 0
2 | 0.99605 | -0.075513 | 0 | 0
3 | 0.99628 | -0.071043 | 0 | 0
4 | 0.99313 | -0.1319 | 0 | 0
5 | 0.99342 | -0.12617 | 0 | 0
6 | 0.99241 | -0.14575 | 0.037846 | 0.0094852
7 | 0.99723 | -0.052759 | 0 | 0
8 | 0.99856 | -0.027459 | 0.027879 | 0.0069872
9 | 0.99635 | -0.069624 | 0.018451 | 0.0046242
10 | 0.99573 | -0.081692 | 0.027801 | 0.0069675
11 | 0.99308 | -0.13277 | 0 | 0
12 | 0.99265 | -0.14119 | 0.037557 | 0.0094127
13 | 0.996 | -0.076422 | 0.010148 | 0.0025433
14 | 0.99604 | -0.075744 | 0.016425 | 0.0041164
15 | 0.9888 | -0.21451 | 0 | 0
16 | 0.99042 | -0.18322 | 0 | 0
17 | 0.98757 | -0.23833 | 0.0050207 | 0.0012583
18 | 0.99232 | -0.1467 | 0 | 0
19 | 0.98728 | -0.24376 | 0.014285 | 0.0035802
20 | 0.98012 | -0.38322 | 0 | 0
21 | 0.9798 | -0.38952 | 0 | 0
22 | 0.98027 | -0.38046 | 0.024625 | 0.0061717
23 | 0.99421 | -0.11095 | 0.042986 | 0.010773
24 | 0.99382 | -0.11786 | 0 | 0
25 | 0.99153 | -0.16207 | 0.065624 | 0.016447
26 | 0.97964 | -0.39277 | 0.01273 | 0.0031905
27 | 0.98366 | -0.31427 | 0 | 0
28 | 0.98326 | -0.32209 | 0.0085609 | 0.0021456
29 | 0.98271 | -0.33279 | 0 | 0
30 | 0.99541 | -0.087595 | 0.010474 | 0.0026249
31 | 0.98252 | -0.33651 | 0.046295 | 0.011603
32 | 1 | 0 | -0.53209 | -0.13484
33 | 0.98573 | -0.27394 | 0.0090506 | 0.0022683
34 | 0.98068 | -0.37226 | 0.031256 | 0.0078335
35 | 0.99133 | -0.16595 | 0.013037 | 0.0032675
36 | 0.98314 | -0.32445 | 0.0066184 | 0.0016587
37 | 0.98247 | -0.33742 | 0.0082552 | 0.002069
38 | 0.98386 | -0.31029 | 0.009898 | 0.0024807
39 | 0.9847 | -0.29389 | 0.009021 | 0.0022609
40 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.031684 | -0.0079407 | 0.0317 | 0.007951 | 1.6456e-05 | 1.028e-05 | 0.047453 | 0.047453 | 0.047453 | 0.99353 | -0.12419 | 0.99409 | -0.11329 | 13.0366
1 | -0.0317 | -0.007951 | 0.031758 | 0.0079867 | 5.7195e-05 | 3.5725e-05 | 0.047453 | 0.047453 | 0.047453 | 0.99409 | -0.11329 | 0.99605 | -0.075513 | 13.0366
2 | -0.031758 | -0.0079867 | 0.031764 | 0.007991 | 6.7813e-06 | 4.2355e-06 | 0.047453 | 0.047453 | 0.047453 | 0.99605 | -0.075513 | 0.99628 | -0.071043 | 13.0365
3 | 0.01015 | 0.0025446 | -0.010148 | -0.0025433 | 2.6009e-06 | 1.2718e-06 | 0.015161 | 0.015161 | 0.015161 | 0.99628 | -0.071043 | 0.996 | -0.076422 | 4.165
4 | 0.016428 | 0.0041186 | -0.016425 | -0.0041164 | 3.6785e-06 | 2.1421e-06 | 0.024537 | 0.024537 | 0.024537 | 0.99628 | -0.071043 | 0.99604 | -0.075744 | 6.741
5 | -0.058343 | -0.014654 | 0.058394 | 0.014686 | 5.0954e-05 | 3.2377e-05 | 0.087151 | 0.087151 | 0.087151 | 0.99628 | -0.071043 | 0.99723 | -0.052759 | 23.9425
6 | -0.037871 | -0.0095009 | 0.037882 | 0.0095074 | 1.0343e-05 | 6.5085e-06 | 0.056747 | 0.056747 | 0.056747 | 0.99313 | -0.1319 | 0.99342 | -0.12617 | 15.5897
7 | 0.037871 | 0.0095009 | -0.037846 | -0.0094852 | 2.4983e-05 | 1.5722e-05 | 0.056747 | 0.056747 | 0.056747 | 0.99313 | -0.1319 | 0.99241 | -0.14575 | 15.5898
8 | -0.075466 | -0.018937 | 0.075521 | 0.018972 | 5.4844e-05 | 3.4952e-05 | 0.11305 | 0.11305 | 0.11305 | 0.99342 | -0.12617 | 0.99421 | -0.11095 | 31.0567
9 | 0.037584 | 0.0094296 | -0.037572 | -0.0094222 | 1.1822e-05 | 7.4374e-06 | 0.0563 | 0.0563 | 0.0563 | 0.99342 | -0.12617 | 0.99308 | -0.13277 | 15.4669
10 | -0.50125 | -0.12701 | 0.50186 | 0.1274 | 0.00061008 | 0.00038984 | 0.74843 | 0.74843 | 0.74843 | 0.99723 | -0.052759 | 0.99856 | -0.027459 | 51.4032
11 | 0.29618 | 0.07538 | -0.29594 | -0.075227 | 0.0002406 | 0.0001533 | 0.44235 | 0.44235 | 0.44235 | 0.99723 | -0.052759 | 0.99635 | -0.069624 | 30.3814
12 | 0.14668 | 0.036948 | -0.14647 | -0.036819 | 0.00020265 | 0.00012911 | 0.21893 | 0.21893 | 0.21893 | 0.99723 | -0.052759 | 0.99573 | -0.081692 | 30.0724
13 | -0.52974 | -0.13439 | 0.53044 | 0.13484 | 0.0007005 | 0.00044769 | 0.78997 | 0.78997 | 0.78997 | 0.99856 | -0.027459 | 1 | 0 | 54.2565
14 | 0.27749 | 0.070603 | -0.27725 | -0.07045 | 0.00024011 | 0.0001529 | 0.4148 | 0.4148 | 0.4148 | 0.99635 | -0.069624 | 0.99541 | -0.087595 | 28.4889
15 | 0.11867 | 0.029851 | -0.11851 | -0.029745 | 0.0001656 | 0.0001058 | 0.17738 | 0.17738 | 0.17738 | 0.99573 | -0.081692 | 0.99421 | -0.11095 | 48.7313
16 | 0.037572 | 0.0094222 | -0.037557 | -0.0094127 | 1.5072e-05 | 9.4819e-06 | 0.0563 | 0.0563 | 0.0563 | 0.99308 | -0.13277 | 0.99265 | -0.14119 | 15.467
17 | -0.066851 | -0.016891 | 0.066951 | 0.016955 | 0.00010045 | 6.3946e-05 | 0.10065 | 0.10065 | 0.10065 | 0.9888 | -0.21451 | 0.99042 | -0.18322 | 27.6513
18 | 0.066851 | 0.016891 | -0.066775 | -0.016842 | 7.623e-05 | 4.853e-05 | 0.10065 | 0.10065 | 0.10065 | 0.9888 | -0.21451 | 0.98757 | -0.23833 | 27.6513
19 | -0.18697 | -0.047381 | 0.1873 | 0.047591 | 0.00032868 | 0.00020978 | 0.28109 | 0.28109 | 0.28109 | 0.99042 | -0.18322 | 0.99232 | -0.1467 | 38.6113
20 | 0.12002 | 0.030426 | -0.11967 | -0.030204 | 0.0003481 | 0.00022242 | 0.18044 | 0.18044 | 0.18044 | 0.99042 | -0.18322 | 0.98728 | -0.24376 | 49.5714
21 | 0.061754 | 0.015584 | -0.06153 | -0.015442 | 0.00022373 | 0.00014231 | 0.093086 | 0.093086 | 0.093086 | 0.98757 | -0.23833 | 0.98366 | -0.31427 | 25.5731
22 | -0.26602 | -0.067343 | 0.26639 | 0.067578 | 0.00036891 | 0.00023483 | 0.39914 | 0.39914 | 0.39914 | 0.99232 | -0.1467 | 0.99382 | -0.11786 | 27.4136
23 | 0.078721 | 0.019752 | -0.078664 | -0.019716 | 5.7643e-05 | 3.6749e-05 | 0.11805 | 0.11805 | 0.11805 | 0.99232 | -0.1467 | 0.99153 | -0.16207 | 32.4322
24 | 0.10538 | 0.026624 | -0.10523 | -0.026526 | 0.00015224 | 9.7227e-05 | 0.15891 | 0.15891 | 0.15891 | 0.98728 | -0.24376 | 0.98573 | -0.27394 | 43.6565
25 | 0.012736 | 0.0031937 | -0.012732 | -0.0031916 | 3.8256e-06 | 2.1047e-06 | 0.019336 | 0.019337 | 0.019337 | 0.98012 | -0.38322 | 0.9798 | -0.38952 | 5.3122
26 | -0.012736 | -0.0031937 | 0.012738 | 0.0031946 | 1.678e-06 | 9.2304e-07 | 0.019336 | 0.019336 | 0.019336 | 0.98012 | -0.38322 | 0.98027 | -0.38046 | 5.3122
27 | 0.012732 | 0.0031916 | -0.01273 | -0.0031905 | 1.9708e-06 | 1.0843e-06 | 0.019337 | 0.019337 | 0.019337 | 0.9798 | -0.38952 | 0.97964 | -0.39277 | 5.3123
28 | -0.037363 | -0.0093663 | 0.037378 | 0.0093755 | 1.4601e-05 | 9.192e-06 | 0.056717 | 0.056717 | 0.056717 | 0.98027 | -0.38046 | 0.98068 | -0.37226 | 15.5816
29 | -0.26639 | -0.067578 | 0.26678 | 0.067825 | 0.00038824 | 0.00024712 | 0.39914 | 0.39914 | 0.39914 | 0.99382 | -0.11786 | 0.99541 | -0.087595 | 27.4136
30 | 0.01304 | 0.0032688 | -0.013037 | -0.0032675 | 2.4118e-06 | 1.327e-06 | 0.01957 | 0.01957 | 0.01957 | 0.99153 | -0.16207 | 0.99133 | -0.16595 | 5.3763
31 | 0.015186 | 0.0038078 | -0.01518 | -0.0038045 | 5.6522e-06 | 3.255e-06 | 0.022973 | 0.022973 | 0.022973 | 0.98366 | -0.31427 | 0.98326 | -0.32209 | 6.3112
32 | 0.046345 | 0.011634 | -0.046304 | -0.011608 | 4.0886e-05 | 2.5886e-05 | 0.070114 | 0.070114 | 0.070114 | 0.98366 | -0.31427 | 0.98271 | -0.33279 | 19.262
33 | 0.0066191 | 0.001659 | -0.0066184 | -0.0016587 | 7.4606e-07 | 2.2603e-07 | 0.010017 | 0.010017 | 0.010017 | 0.98326 | -0.32209 | 0.98314 | -0.32445 | 2.752
34 | 0.046304 | 0.011608 | -0.046295 | -0.011603 | 8.2007e-06 | 5.1921e-06 | 0.070114 | 0.070114 | 0.070114 | 0.98271 | -0.33279 | 0.98252 | -0.33651 | 19.262
35 | 0.096182 | 0.024258 | -0.09609 | -0.024199 | 9.1737e-05 | 5.8564e-05 | 0.14525 | 0.14525 | 0.14525 | 0.98573 | -0.27394 | 0.9847 | -0.29389 | 39.9031
36 | -0.068634 | -0.017209 | 0.068748 | 0.017282 | 0.00011415 | 7.2698e-05 | 0.10414 | 0.10414 | 0.10414 | 0.98068 | -0.37226 | 0.98247 | -0.33742 | 28.6105
37 | -0.077003 | -0.019351 | 0.077103 | 0.019414 | 9.9888e-05 | 6.368e-05 | 0.11665 | 0.11665 | 0.11665 | 0.98247 | -0.33742 | 0.98386 | -0.31029 | 32.0454
38 | -0.087001 | -0.021895 | 0.087069 | 0.021939 | 6.8236e-05 | 4.3538e-05 | 0.13162 | 0.13162 | 0.13162 | 0.98386 | -0.31029 | 0.9847 | -0.29389 | 36.158

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.53936 | 0.13666

## res_load
| p_mw | q_mvar
0 | 0.031684 | 0.0079407
1 | 0.037846 | 0.0094852
2 | 0.027879 | 0.0069872
3 | 0.018451 | 0.0046242
4 | 0.027801 | 0.0069675
5 | 0.037557 | 0.0094127
6 | 0.010148 | 0.0025433
7 | 0.016425 | 0.0041164
8 | 0.0050207 | 0.0012583
9 | 0.014285 | 0.0035802
10 | 0.024625 | 0.0061717
11 | 0.042986 | 0.010773
12 | 0.065624 | 0.016447
13 | 0.01273 | 0.0031905
14 | 0.0085609 | 0.0021456
15 | 0.010474 | 0.0026249
16 | 0.046295 | 0.011603
17 | 0.0072714 | 0.0018224
18 | 0.0090506 | 0.0022683
19 | 0.031256 | 0.0078335
20 | 0.013037 | 0.0032675
21 | 0.0066184 | 0.0016587
22 | 0.0082552 | 0.002069
23 | 0.009898 | 0.0024807
24 | 0.009021 | 0.0022609

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1