## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-269_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-269_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-269_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_261-269_0_4_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_261-269_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-269_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-269_0_4_node_13 | 0.4 | n |  | TRUE
7 | bus_LV_261-269_0_4_node_14 | 0.4 | n |  | TRUE
8 | bus_LV_261-269_0_4_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_261-269_0_4_node_31 | 0.4 | n |  | TRUE
10 | bus_LV_261-269_0_4_node_38 | 0.4 | n |  | TRUE
11 | bus_LV_261-269_0_4_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_261-269_0_4_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_261-269_0_4_node_22 | 0.4 | n |  | TRUE
14 | bus_LV_261-269_0_4_node_21 | 0.4 | n |  | TRUE
15 | bus_LV_261-269_0_4_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_261-269_0_4_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_261-269_0_4_node_32 | 0.4 | n |  | TRUE
18 | bus_LV_261-269_0_4_node_25 | 0.4 | n |  | TRUE
19 | bus_LV_261-269_0_4_node_40 | 0.4 | n |  | TRUE
20 | bus_LV_261-269_0_4_node_45 | 0.4 | n |  | TRUE
21 | bus_LV_261-269_0_4_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_261-269_0_4_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_261-269_0_4_node_36 | 0.4 | n |  | TRUE
24 | bus_LV_261-269_0_4_node_41 | 0.4 | n |  | TRUE
25 | bus_LV_261-269_0_4_node_29 | 0.4 | n |  | TRUE
26 | bus_LV_261-269_0_4_node_39 | 0.4 | n |  | TRUE
27 | bus_LV_261-269_0_4_node_26 | 0.4 | n |  | TRUE
28 | bus_LV_261-269_0_4_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_261-269_0_4_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_261-269_0_4_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_261-269_0_4_node_33 | 0.4 | n |  | TRUE
32 | bus_LV_261-269_0_4_node_44 | 0.4 | n |  | TRUE
33 | bus_LV_261-269_0_4_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_261-269_0_4_node_37 | 0.4 | n |  | TRUE
35 | bus_LV_261-269_0_4_node_42 | 0.4 | n |  | TRUE
36 | bus_LV_261-269_0_4_node_48 | 0.4 | n |  | TRUE
37 | bus_LV_261-269_0_4_node_46 | 0.4 | n |  | TRUE
38 | bus_LV_261-269_0_4_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_261-269_0_4_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_261-269_0_4_node_30 | 0.4 | n |  | TRUE
41 | bus_LV_261-269_0_4_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_261-269_0_4_node_43 | 0.4 | n |  | TRUE
43 | bus_LV_261-269_0_4_node_34 | 0.4 | n |  | TRUE
44 | bus_LV_261-269_0_4_node_49 | 0.4 | n |  | TRUE
45 | bus_LV_261-269_0_4_node_47 | 0.4 | n |  | TRUE
46 | bus_MV_534_0_node_41 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-269_0_4_load_0 | 0 | 0.018416 | 0.0046155 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-269_0_4_load_1 | 1 | 0.020775 | 0.0052068 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-269_0_4_load_4 | 4 | 0.019994 | 0.0050108 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-269_0_4_load_31 | 9 | 0.012256 | 0.0030716 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-269_0_4_load_38 | 10 | 0.019133 | 0.0047951 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-269_0_4_load_22 | 13 | 0.005102 | 0.0012787 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-269_0_4_load_21 | 14 | 0.0044699 | 0.0011203 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-269_0_4_load_32 | 17 | 0.011419 | 0.0028619 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-269_0_4_load_25 | 18 | 0.0075049 | 0.0018809 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-269_0_4_load_40 | 19 | 0.011192 | 0.0028049 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-269_0_4_load_45 | 20 | 0.011283 | 0.0028278 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-269_0_4_load_36 | 23 | 0.013007 | 0.0032598 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-269_0_4_load_41 | 24 | 0.04061 | 0.010178 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-269_0_4_load_29 | 25 | 0.0098915 | 0.002479 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-269_0_4_load_39 | 26 | 0.013536 | 0.0033926 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-269_0_4_load_26 | 27 | 0.0029314 | 0.00073469 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-269_0_4_load_24 | 28 | 0.0027835 | 0.00069762 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-269_0_4_load_19 | 29 | 0.0050451 | 0.0012644 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-269_0_4_load_20 | 30 | 0.0041003 | 0.0010276 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-269_0_4_load_33 | 31 | 0.011426 | 0.0028637 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-269_0_4_load_44 | 32 | 0.017069 | 0.0042779 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-269_0_4_load_23 | 33 | 0.00775 | 0.0019423 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-269_0_4_load_37 | 34 | 0.01283 | 0.0032155 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-269_0_4_load_42 | 35 | 0.0078704 | 0.0019725 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-269_0_4_load_48 | 36 | 0.008517 | 0.0021346 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-269_0_4_load_46 | 37 | 0.0080776 | 0.0020244 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-269_0_4_load_27 | 38 | 0.016753 | 0.0041987 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-269_0_4_load_28 | 39 | 0.033815 | 0.0084749 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-269_0_4_load_30 | 40 | 0.005775 | 0.0014473 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-269_0_4_load_35 | 41 | 0.0055438 | 0.0013894 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-269_0_4_load_43 | 42 | 0.00532 | 0.0013333 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-269_0_4_load_34 | 43 | 0.010925 | 0.0027381 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-269_0_4_load_49 | 44 | 0.011533 | 0.0028903 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-269_0_4_load_47 | 45 | 0.0084402 | 0.0021153 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 31 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-269_0_4_line_0 |  | 0 | 1 | 0.019233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-269_0_4_line_1 |  | 1 | 2 | 0.023687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-269_0_4_line_2 |  | 2 | 6 | 0.008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-269_0_4_line_3 |  | 2 | 7 | 0.0080384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-269_0_4_line_4 |  | 3 | 4 | 0.019279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-269_0_4_line_5 |  | 3 | 5 | 0.0095054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-269_0_4_line_6 |  | 4 | 8 | 0.022427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-269_0_4_line_7 |  | 5 | 9 | 0.010514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_261-269_0_4_line_8 |  | 5 | 10 | 0.021637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_261-269_0_4_line_9 |  | 6 | 18 | 0.0078365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-269_0_4_line_10 |  | 7 | 19 | 0.0079951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_261-269_0_4_line_11 |  | 7 | 15 | 0.001965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_261-269_0_4_line_12 |  | 8 | 13 | 0.0091502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-269_0_4_line_13 |  | 9 | 25 | 0.012244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_261-269_0_4_line_14 |  | 10 | 26 | 0.021127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_261-269_0_4_line_15 |  | 11 | 12 | 0.018044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-269_0_4_line_16 |  | 11 | 13 | 0.022442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-269_0_4_line_17 |  | 12 | 14 | 0.01046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-269_0_4_line_18 |  | 14 | 30 | 0.0078109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-269_0_4_line_19 |  | 15 | 16 | 0.051875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-269_0_4_line_20 |  | 15 | 17 | 0.019875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_261-269_0_4_line_21 |  | 16 | 20 | 0.03464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-269_0_4_line_22 |  | 17 | 31 | 0.019098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_261-269_0_4_line_23 |  | 18 | 33 | 0.012632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-269_0_4_line_24 |  | 19 | 26 | 0.018169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_261-269_0_4_line_25 |  | 20 | 32 | 0.020326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-269_0_4_line_26 |  | 21 | 22 | 0.037927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-269_0_4_line_27 |  | 21 | 23 | 0.011783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-269_0_4_line_28 |  | 22 | 24 | 0.014513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-269_0_4_line_29 |  | 23 | 34 | 0.017218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-269_0_4_line_30 |  | 24 | 35 | 0.029014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-269_0_4_line_31 |  | 25 | 38 | 0.012123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
32 | LV_261-269_0_4_line_32 |  | 27 | 28 | 0.0060603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-269_0_4_line_33 |  | 28 | 33 | 0.01726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-269_0_4_line_34 |  | 29 | 30 | 0.016288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-269_0_4_line_35 |  | 31 | 43 | 0.010878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-269_0_4_line_36 |  | 35 | 42 | 0.0060912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-269_0_4_line_37 |  | 36 | 37 | 0.010931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-269_0_4_line_38 |  | 37 | 45 | 0.010877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-269_0_4_line_39 |  | 38 | 39 | 0.024226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-269_0_4_line_40 |  | 39 | 40 | 0.022544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-269_0_4_line_41 |  | 40 | 41 | 0.0062108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-269_0_4_line_42 |  | 41 | 42 | 0.007002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-269_0_4_line_43 |  | 43 | 44 | 0.010931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-269_0_4_line_44 |  | 44 | 45 | 0.020924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-269_0_4_trafo_33 | 0.63 MVA 20/0.4 kV | 46 | 31 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2684856.6006 | 1246818.6478 | 2684873.2345 | 1246828.3031
1 | 2684893.5492 | 1246840.48 | 2684883.9573 | 1246834.5272 | 2684873.2345 | 1246828.3031
2 | 2684893.5492 | 1246840.48 | 2684900.2936 | 1246844.813
3 | 2684893.5492 | 1246840.48 | 2684890.9111 | 1246844.8121 | 2684889.3715 | 1246847.3475
4 | 2684835.7864 | 1246804.716 | 2684846.5748 | 1246792.5391 | 2684848.5995 | 1246790.3112
5 | 2684835.7864 | 1246804.716 | 2684833.2757 | 1246808.0714 | 2684830.0648 | 1246812.3064
6 | 2684863.6832 | 1246773.7144 | 2684848.5995 | 1246790.3112
7 | 2684830.0648 | 1246812.3064 | 2684824.5244 | 1246819.9105 | 2684823.9236 | 1246820.8379
8 | 2684830.0648 | 1246812.3064 | 2684835.9974 | 1246815.8383 | 2684848.7559 | 1246823.2043
9 | 2684900.2936 | 1246844.813 | 2684906.8288 | 1246840.4884
10 | 2684889.3715 | 1246847.3475 | 2684886.2794 | 1246844.868 | 2684882.7878 | 1246842.8522
11 | 2684889.3715 | 1246847.3475 | 2684889.9565 | 1246849.2239
12 | 2684863.6832 | 1246773.7144 | 2684870.231 | 1246768.0483 | 2684870.6018 | 1246767.7261
13 | 2684817.2666 | 1246831.1136 | 2684823.9236 | 1246820.8379
14 | 2684848.7559 | 1246823.2043 | 2684867.0528 | 1246833.7677
15 | 2684897.983 | 1246767.7453 | 2684895.7251 | 1246764.5217 | 2684887.5422 | 1246753.0072
16 | 2684887.5422 | 1246753.0072 | 2684870.6018 | 1246767.7261
17 | 2684897.983 | 1246767.7453 | 2684903.6964 | 1246776.5068
18 | 2684903.6964 | 1246776.5068 | 2684907.963 | 1246783.0495
19 | 2684889.9565 | 1246849.2239 | 2684893.7757 | 1246851.0354 | 2684898.4879 | 1246853.2712 | 2684900.6764 | 1246853.4249 | 2684910.474 | 1246859.2583 | 2684935.3532 | 1246873.8364
20 | 2684889.9565 | 1246849.2239 | 2684889.519 | 1246851.2858 | 2684880.2397 | 1246866.4372
21 | 2684935.3532 | 1246873.8364 | 2684917.2739 | 1246903.3836
22 | 2684870.2651 | 1246882.7239 | 2684880.2397 | 1246866.4372
23 | 2684917.3634 | 1246833.5171 | 2684906.8288 | 1246840.4884
24 | 2684882.7878 | 1246842.8522 | 2684867.0528 | 1246833.7677
25 | 2684906.6651 | 1246920.7216 | 2684917.2739 | 1246903.3836
26 | 2684756.1384 | 1246936.3522 | 2684754.4366 | 1246939.1411 | 2684754.2517 | 1246941.5068 | 2684755.0972 | 1246944.1876 | 2684756.8994 | 1246946.5262 | 2684762.3962 | 1246951.475 | 2684777.9112 | 1246962.6606
27 | 2684777.9112 | 1246962.6606 | 2684783.9702 | 1246952.5553
28 | 2684756.1384 | 1246936.3522 | 2684763.207 | 1246923.6767
29 | 2684792.8241 | 1246937.7887 | 2684783.9702 | 1246952.5553
30 | 2684763.207 | 1246923.6767 | 2684766.4733 | 1246917.8196 | 2684777.604 | 1246898.4869
31 | 2684817.2666 | 1246831.1136 | 2684810.6751 | 1246841.2884
32 | 2684931.7569 | 1246823.9923 | 2684936.8108 | 1246820.6479
33 | 2684917.3634 | 1246833.5171 | 2684931.7569 | 1246823.9923
34 | 2684916.8601 | 1246796.6931 | 2684907.963 | 1246783.0495
35 | 2684864.5837 | 1246892.0006 | 2684870.2651 | 1246882.7239
36 | 2684777.604 | 1246898.4869 | 2684780.6432 | 1246893.2081
37 | 2684842.2659 | 1246928.4415 | 2684836.557 | 1246937.7631
38 | 2684842.2659 | 1246928.4415 | 2684847.9469 | 1246919.1654
39 | 2684810.6751 | 1246841.2884 | 2684809.4219 | 1246843.2229 | 2684798.4843 | 1246862.2202
40 | 2684787.2358 | 1246881.7575 | 2684798.4843 | 1246862.2202
41 | 2684784.1369 | 1246887.14 | 2684787.2358 | 1246881.7575
42 | 2684780.6432 | 1246893.2081 | 2684784.1369 | 1246887.14
43 | 2684858.8748 | 1246901.3222 | 2684864.5837 | 1246892.0006
44 | 2684847.9469 | 1246919.1654 | 2684858.8748 | 1246901.3222

## bus_geodata
| x | y | coords
0 | 2684856.6006 | 1246818.6478
1 | 2684873.2345 | 1246828.3031
2 | 2684893.5492 | 1246840.48
3 | 2684835.7864 | 1246804.7159
4 | 2684848.5995 | 1246790.3112
5 | 2684830.0648 | 1246812.3064
6 | 2684900.2936 | 1246844.813
7 | 2684889.3715 | 1246847.3475
8 | 2684863.6832 | 1246773.7144
9 | 2684823.9236 | 1246820.8379
10 | 2684848.7559 | 1246823.2043
11 | 2684887.5422 | 1246753.0072
12 | 2684897.983 | 1246767.7453
13 | 2684870.6018 | 1246767.7261
14 | 2684903.6964 | 1246776.5068
15 | 2684889.9565 | 1246849.2239
16 | 2684935.3532 | 1246873.8364
17 | 2684880.2397 | 1246866.4372
18 | 2684906.8288 | 1246840.4884
19 | 2684882.7878 | 1246842.8522
20 | 2684917.2739 | 1246903.3836
21 | 2684777.9112 | 1246962.6606
22 | 2684756.1384 | 1246936.3522
23 | 2684783.9702 | 1246952.5553
24 | 2684763.207 | 1246923.6767
25 | 2684817.2666 | 1246831.1136
26 | 2684867.0528 | 1246833.7677
27 | 2684936.8108 | 1246820.6479
28 | 2684931.7569 | 1246823.9923
29 | 2684916.8601 | 1246796.6931
30 | 2684907.963 | 1246783.0495
31 | 2684870.2651 | 1246882.7239
32 | 2684906.6651 | 1246920.7216
33 | 2684917.3634 | 1246833.5171
34 | 2684792.8241 | 1246937.7887
35 | 2684777.604 | 1246898.4869
36 | 2684836.557 | 1246937.7631
37 | 2684842.2659 | 1246928.4415
38 | 2684810.6751 | 1246841.2884
39 | 2684798.4843 | 1246862.2202
40 | 2684787.2358 | 1246881.7575
41 | 2684784.1369 | 1246887.14
42 | 2684780.6432 | 1246893.2081
43 | 2684864.5837 | 1246892.0006
44 | 2684858.8748 | 1246901.3222
45 | 2684847.9469 | 1246919.1654
46 | 2684889.9565 | 1246849.2239

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99415 | -0.11201 | 0.018416 | 0.0046155
1 | 0.99447 | -0.10577 | 0.020775 | 0.0052068
2 | 0.99532 | -0.089418 | 0 | 0
3 | 0.99073 | -0.17751 | 0 | 0
4 | 0.99005 | -0.19078 | 0.019994 | 0.0050108
5 | 0.99107 | -0.17098 | 0 | 0
6 | 0.99516 | -0.09237 | 0 | 0
7 | 0.99576 | -0.080913 | 0 | 0
8 | 0.98966 | -0.19825 | 0 | 0
9 | 0.99054 | -0.18117 | 0.012256 | 0.0030716
10 | 0.99241 | -0.14511 | 0.019133 | 0.0047951
11 | 0.98922 | -0.20674 | 0 | 0
12 | 0.989 | -0.21111 | 0 | 0
13 | 0.9895 | -0.20129 | 0.005102 | 0.0012787
14 | 0.98887 | -0.21365 | 0.0044699 | 0.0011203
15 | 0.99594 | -0.077385 | 0 | 0
16 | 0.9946 | -0.10327 | 0 | 0
17 | 0.99798 | -0.038492 | 0.011419 | 0.0028619
18 | 0.99502 | -0.095263 | 0.0075049 | 0.0018809
19 | 0.99516 | -0.092457 | 0.011192 | 0.0028049
20 | 0.9937 | -0.12059 | 0.011283 | 0.0028278
21 | 0.98003 | -0.38534 | 0 | 0
22 | 0.98094 | -0.36757 | 0 | 0
23 | 0.97975 | -0.39086 | 0.013007 | 0.0032598
24 | 0.98129 | -0.36078 | 0.04061 | 0.010178
25 | 0.98997 | -0.19215 | 0.0098915 | 0.002479
26 | 0.99385 | -0.11755 | 0.013536 | 0.0033926
27 | 0.99475 | -0.10031 | 0.0029314 | 0.00073469
28 | 0.99477 | -0.099995 | 0.0027835 | 0.00069762
29 | 0.98873 | -0.21639 | 0.0050451 | 0.0012644
30 | 0.9888 | -0.21493 | 0.0041003 | 0.0010276
31 | 1 | 0 | -0.39886 | -0.10092
32 | 0.99339 | -0.12671 | 0.017069 | 0.0042779
33 | 0.99486 | -0.098258 | 0.00775 | 0.0019423
34 | 0.97955 | -0.39487 | 0.01283 | 0.0032155
35 | 0.98307 | -0.32595 | 0.0078704 | 0.0019725
36 | 0.99844 | -0.029918 | 0.008517 | 0.0021346
37 | 0.99853 | -0.02829 | 0.0080776 | 0.0020244
38 | 0.98918 | -0.20742 | 0.016753 | 0.0041987
39 | 0.98639 | -0.26142 | 0.033815 | 0.0084749
40 | 0.98449 | -0.29822 | 0.005775 | 0.0014473
41 | 0.984 | -0.30774 | 0.0055438 | 0.0013894
42 | 0.98349 | -0.31778 | 0.00532 | 0.0013333
43 | 0.99953 | -0.0090093 | 0.010925 | 0.0027381
44 | 0.99917 | -0.015985 | 0.011533 | 0.0028903
45 | 0.99869 | -0.025135 | 0.0084402 | 0.0021153
46 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.018416 | -0.0046155 | 0.018422 | 0.0046188 | 5.4801e-06 | 3.2578e-06 | 0.027565 | 0.027565 | 0.027565 | 0.99415 | -0.11201 | 0.99447 | -0.10577 | 7.5728
1 | -0.039197 | -0.0098256 | 0.039228 | 0.0098449 | 3.0556e-05 | 1.9248e-05 | 0.058651 | 0.058651 | 0.058651 | 0.99447 | -0.10577 | 0.99532 | -0.089418 | 16.1129
2 | 0.020978 | 0.0052602 | -0.020975 | -0.0052584 | 2.951e-06 | 1.7847e-06 | 0.031363 | 0.031364 | 0.031364 | 0.99532 | -0.089418 | 0.99516 | -0.09237 | 8.6164
3 | -0.060206 | -0.015105 | 0.06023 | 0.015121 | 2.4424e-05 | 1.5527e-05 | 0.090014 | 0.090014 | 0.090014 | 0.99532 | -0.089418 | 0.99576 | -0.080913 | 24.7292
4 | 0.038754 | 0.0097276 | -0.038729 | -0.0097122 | 2.4498e-05 | 1.543e-05 | 0.058211 | 0.058211 | 0.058211 | 0.99073 | -0.17751 | 0.99005 | -0.19078 | 15.9921
5 | -0.038754 | -0.0097276 | 0.038766 | 0.0097352 | 1.2078e-05 | 7.6077e-06 | 0.058211 | 0.058211 | 0.058211 | 0.99073 | -0.17751 | 0.99107 | -0.17098 | 15.992
6 | 0.018736 | 0.0047014 | -0.018729 | -0.0046974 | 6.6698e-06 | 3.9804e-06 | 0.028161 | 0.028161 | 0.028161 | 0.99005 | -0.19078 | 0.98966 | -0.19825 | 7.7366
7 | 0.16468 | 0.04166 | -0.1646 | -0.041609 | 8.043e-05 | 5.1069e-05 | 0.24739 | 0.24739 | 0.24739 | 0.99107 | -0.17098 | 0.99054 | -0.18117 | 22.6547
8 | -0.20344 | -0.051396 | 0.2037 | 0.051556 | 0.00025258 | 0.00016082 | 0.3056 | 0.3056 | 0.3056 | 0.99107 | -0.17098 | 0.99241 | -0.14511 | 27.9854
9 | 0.020975 | 0.0052584 | -0.020972 | -0.0052566 | 2.8907e-06 | 1.7483e-06 | 0.031364 | 0.031364 | 0.031364 | 0.99516 | -0.09237 | 0.99502 | -0.095263 | 8.6164
10 | 0.24827 | 0.063007 | -0.24814 | -0.062919 | 0.00013777 | 8.7862e-05 | 0.37129 | 0.37129 | 0.37129 | 0.99576 | -0.080913 | 0.99516 | -0.092457 | 34.0007
11 | -0.3085 | -0.078127 | 0.30856 | 0.078161 | 5.2269e-05 | 3.3375e-05 | 0.4613 | 0.4613 | 0.4613 | 0.99576 | -0.080913 | 0.99594 | -0.077385 | 42.2438
12 | 0.018729 | 0.0046974 | -0.018726 | -0.0046958 | 2.7213e-06 | 1.6241e-06 | 0.028161 | 0.028161 | 0.028161 | 0.98966 | -0.19825 | 0.9895 | -0.20129 | 7.7367
13 | 0.15234 | 0.038538 | -0.15226 | -0.038487 | 8.0243e-05 | 5.0883e-05 | 0.22898 | 0.22898 | 0.22898 | 0.99054 | -0.18117 | 0.98997 | -0.19215 | 20.9687
14 | -0.22283 | -0.056351 | 0.22312 | 0.05654 | 0.00029512 | 0.00018805 | 0.33429 | 0.33429 | 0.33429 | 0.99241 | -0.14511 | 0.99385 | -0.11755 | 30.6124
15 | 0.013621 | 0.0034151 | -0.013618 | -0.0034135 | 2.8406e-06 | 1.5864e-06 | 0.020489 | 0.020489 | 0.020489 | 0.98922 | -0.20674 | 0.989 | -0.21111 | 5.6289
16 | -0.013621 | -0.0034151 | 0.013624 | 0.0034171 | 3.5329e-06 | 1.9729e-06 | 0.020489 | 0.020489 | 0.020489 | 0.98922 | -0.20674 | 0.9895 | -0.20129 | 5.6289
17 | 0.013618 | 0.0034135 | -0.013616 | -0.0034126 | 1.6467e-06 | 9.1967e-07 | 0.020489 | 0.020489 | 0.020489 | 0.989 | -0.21111 | 0.98887 | -0.21365 | 5.6289
18 | 0.0091463 | 0.0022923 | -0.0091458 | -0.0022921 | 5.5484e-07 | 2.549e-07 | 0.013763 | 0.013763 | 0.013763 | 0.98887 | -0.21365 | 0.9888 | -0.21493 | 3.7811
19 | 0.028415 | 0.0071449 | -0.02838 | -0.0071231 | 3.5077e-05 | 2.1775e-05 | 0.042463 | 0.042463 | 0.042463 | 0.99594 | -0.077385 | 0.9946 | -0.10327 | 11.6658
20 | -0.33697 | -0.085306 | 0.3376 | 0.085708 | 0.00063048 | 0.00040273 | 0.50376 | 0.50376 | 0.50376 | 0.99594 | -0.077385 | 0.99798 | -0.038492 | 46.1323
21 | 0.02838 | 0.0071231 | -0.028357 | -0.0071086 | 2.3423e-05 | 1.4541e-05 | 0.042463 | 0.042464 | 0.042464 | 0.9946 | -0.10327 | 0.9937 | -0.12059 | 11.6658
22 | -0.34902 | -0.08857 | 0.34967 | 0.088984 | 0.00064749 | 0.00041364 | 0.52079 | 0.52079 | 0.52079 | 0.99798 | -0.038492 | 1 | 0 | 47.6914
23 | 0.013467 | 0.0033757 | -0.013465 | -0.0033747 | 1.9215e-06 | 1.0657e-06 | 0.02014 | 0.02014 | 0.02014 | 0.99502 | -0.095263 | 0.99486 | -0.098258 | 5.5331
24 | 0.23695 | 0.060114 | -0.23666 | -0.059932 | 0.0002855 | 0.00018201 | 0.35455 | 0.35455 | 0.35455 | 0.99516 | -0.092457 | 0.99385 | -0.11755 | 32.4683
25 | 0.017074 | 0.0042809 | -0.017069 | -0.0042779 | 4.9829e-06 | 2.9259e-06 | 0.025568 | 0.025568 | 0.025568 | 0.9937 | -0.12059 | 0.99339 | -0.12671 | 7.0242
26 | -0.025846 | -0.0064808 | 0.025868 | 0.0064944 | 2.1903e-05 | 1.354e-05 | 0.039244 | 0.039244 | 0.039244 | 0.98003 | -0.38534 | 0.98094 | -0.36757 | 10.7812
27 | 0.025846 | 0.0064808 | -0.025839 | -0.0064766 | 6.8047e-06 | 4.2066e-06 | 0.039244 | 0.039244 | 0.039244 | 0.98003 | -0.38534 | 0.97975 | -0.39086 | 10.7813
28 | -0.025868 | -0.0064944 | 0.025876 | 0.0064995 | 8.3817e-06 | 5.181e-06 | 0.039244 | 0.039243 | 0.039244 | 0.98094 | -0.36757 | 0.98129 | -0.36078 | 10.7812
29 | 0.012832 | 0.0032168 | -0.01283 | -0.0032155 | 2.4525e-06 | 1.3528e-06 | 0.01949 | 0.01949 | 0.01949 | 0.97975 | -0.39086 | 0.97955 | -0.39487 | 5.3543
30 | -0.066486 | -0.016677 | 0.066596 | 0.016748 | 0.0001106 | 7.0419e-05 | 0.10082 | 0.10082 | 0.10082 | 0.98129 | -0.36078 | 0.98307 | -0.32595 | 27.6988
31 | 0.14237 | 0.036008 | -0.14227 | -0.035941 | 0.00010421 | 6.6382e-05 | 0.21411 | 0.21411 | 0.21411 | 0.98997 | -0.19215 | 0.98918 | -0.20742 | 29.4108
32 | -0.0029314 | -0.00073469 | 0.0029315 | 0.00073463 | 4.3698e-08 | -5.0709e-08 | 0.004385 | 0.004385 | 0.004385 | 0.99475 | -0.10031 | 0.99477 | -0.099995 | 1.2047
33 | -0.005715 | -0.0014323 | 0.0057155 | 0.0014323 | 4.73e-07 | 7.8626e-08 | 0.0085487 | 0.0085486 | 0.0085487 | 0.99477 | -0.099995 | 0.99486 | -0.098258 | 2.3485
34 | -0.0050451 | -0.0012644 | 0.0050455 | 0.0012644 | 3.5213e-07 | 1.6449e-08 | 0.0075928 | 0.0075927 | 0.0075928 | 0.98873 | -0.21639 | 0.9888 | -0.21493 | 2.0859
35 | 0.047539 | 0.011932 | -0.047519 | -0.011919 | 2.0417e-05 | 1.2924e-05 | 0.070745 | 0.070745 | 0.070745 | 1 | 0 | 0.99953 | -0.0090093 | 19.4355
36 | -0.074467 | -0.01872 | 0.074496 | 0.018739 | 2.9031e-05 | 1.8503e-05 | 0.11274 | 0.11274 | 0.11274 | 0.98307 | -0.32595 | 0.98349 | -0.31778 | 30.9716
37 | -0.008517 | -0.0021346 | 0.0085177 | 0.0021348 | 6.6043e-07 | 2.797e-07 | 0.012693 | 0.012693 | 0.012693 | 0.99844 | -0.029918 | 0.99853 | -0.02829 | 3.4871
38 | -0.016595 | -0.0041593 | 0.016598 | 0.0041607 | 2.4947e-06 | 1.4543e-06 | 0.02473 | 0.02473 | 0.02473 | 0.99853 | -0.02829 | 0.99869 | -0.025135 | 6.7941
39 | 0.12551 | 0.031743 | -0.12519 | -0.031535 | 0.0003242 | 0.00020718 | 0.18891 | 0.18891 | 0.18891 | 0.98918 | -0.20742 | 0.98639 | -0.26142 | 51.8982
40 | 0.091373 | 0.023061 | -0.091212 | -0.022958 | 0.00016076 | 0.0001026 | 0.1379 | 0.1379 | 0.1379 | 0.98639 | -0.26142 | 0.98449 | -0.29822 | 37.884
41 | 0.085437 | 0.021511 | -0.085398 | -0.021486 | 3.8859e-05 | 2.4791e-05 | 0.12917 | 0.12917 | 0.12917 | 0.98449 | -0.29822 | 0.984 | -0.30774 | 35.486
42 | 0.079854 | 0.020096 | -0.079816 | -0.020072 | 3.8308e-05 | 2.4428e-05 | 0.12079 | 0.12079 | 0.12079 | 0.984 | -0.30774 | 0.98349 | -0.31778 | 33.1829
43 | 0.036594 | 0.0091807 | -0.036581 | -0.0091731 | 1.2167e-05 | 7.6435e-06 | 0.054481 | 0.054481 | 0.054481 | 0.99953 | -0.0090093 | 0.99917 | -0.015985 | 14.9673
44 | 0.025049 | 0.0062828 | -0.025038 | -0.006276 | 1.092e-05 | 6.7149e-06 | 0.037306 | 0.037306 | 0.037306 | 0.99917 | -0.015985 | 0.99869 | -0.025135 | 10.2489

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.41028 | 0.10378

## res_load
| p_mw | q_mvar
0 | 0.018416 | 0.0046155
1 | 0.020775 | 0.0052068
2 | 0.019994 | 0.0050108
3 | 0.012256 | 0.0030716
4 | 0.019133 | 0.0047951
5 | 0.005102 | 0.0012787
6 | 0.0044699 | 0.0011203
7 | 0.011419 | 0.0028619
8 | 0.0075049 | 0.0018809
9 | 0.011192 | 0.0028049
10 | 0.011283 | 0.0028278
11 | 0.013007 | 0.0032598
12 | 0.04061 | 0.010178
13 | 0.0098915 | 0.002479
14 | 0.013536 | 0.0033926
15 | 0.0029314 | 0.00073469
16 | 0.0027835 | 0.00069762
17 | 0.0050451 | 0.0012644
18 | 0.0041003 | 0.0010276
19 | 0.011426 | 0.0028637
20 | 0.017069 | 0.0042779
21 | 0.00775 | 0.0019423
22 | 0.01283 | 0.0032155
23 | 0.0078704 | 0.0019725
24 | 0.008517 | 0.0021346
25 | 0.0080776 | 0.0020244
26 | 0.016753 | 0.0041987
27 | 0.033815 | 0.0084749
28 | 0.005775 | 0.0014473
29 | 0.0055438 | 0.0013894
30 | 0.00532 | 0.0013333
31 | 0.010925 | 0.0027381
32 | 0.011533 | 0.0028903
33 | 0.0084402 | 0.0021153

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1