## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-276_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-276_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-276_0_4_node_93 | 0.4 | n |  | TRUE
3 | bus_LV_261-276_0_4_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_261-276_0_4_node_31 | 0.4 | n |  | TRUE
5 | bus_LV_261-276_0_4_node_12 | 0.4 | n |  | TRUE
6 | bus_LV_261-276_0_4_node_95 | 0.4 | n |  | TRUE
7 | bus_LV_261-276_0_4_node_14 | 0.4 | n |  | TRUE
8 | bus_LV_261-276_0_4_node_65 | 0.4 | n |  | TRUE
9 | bus_LV_261-276_0_4_node_15 | 0.4 | n |  | TRUE
10 | bus_LV_261-276_0_4_node_32 | 0.4 | n |  | TRUE
11 | bus_LV_261-276_0_4_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_261-276_0_4_node_80 | 0.4 | n |  | TRUE
13 | bus_LV_261-276_0_4_node_99 | 0.4 | n |  | TRUE
14 | bus_LV_261-276_0_4_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_261-276_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_261-276_0_4_node_6 | 0.4 | n |  | TRUE
17 | bus_LV_261-276_0_4_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_261-276_0_4_node_66 | 0.4 | n |  | TRUE
19 | bus_LV_261-276_0_4_node_63 | 0.4 | n |  | TRUE
20 | bus_LV_261-276_0_4_node_7 | 0.4 | n |  | TRUE
21 | bus_LV_261-276_0_4_node_9 | 0.4 | n |  | TRUE
22 | bus_LV_261-276_0_4_node_46 | 0.4 | n |  | TRUE
23 | bus_LV_261-276_0_4_node_85 | 0.4 | n |  | TRUE
24 | bus_LV_261-276_0_4_node_50 | 0.4 | n |  | TRUE
25 | bus_LV_261-276_0_4_node_96 | 0.4 | n |  | TRUE
26 | bus_LV_261-276_0_4_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_261-276_0_4_node_102 | 0.4 | n |  | TRUE
28 | bus_LV_261-276_0_4_node_64 | 0.4 | n |  | TRUE
29 | bus_LV_261-276_0_4_node_49 | 0.4 | n |  | TRUE
30 | bus_LV_261-276_0_4_node_70 | 0.4 | n |  | TRUE
31 | bus_LV_261-276_0_4_node_91 | 0.4 | n |  | TRUE
32 | bus_LV_261-276_0_4_node_68 | 0.4 | n |  | TRUE
33 | bus_LV_261-276_0_4_node_30 | 0.4 | n |  | TRUE
34 | bus_LV_261-276_0_4_node_97 | 0.4 | n |  | TRUE
35 | bus_LV_261-276_0_4_node_98 | 0.4 | n |  | TRUE
36 | bus_LV_261-276_0_4_node_79 | 0.4 | n |  | TRUE
37 | bus_LV_261-276_0_4_node_73 | 0.4 | n |  | TRUE
38 | bus_LV_261-276_0_4_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_261-276_0_4_node_27 | 0.4 | n |  | TRUE
40 | bus_LV_261-276_0_4_node_28 | 0.4 | n |  | TRUE
41 | bus_LV_261-276_0_4_node_47 | 0.4 | n |  | TRUE
42 | bus_LV_261-276_0_4_node_48 | 0.4 | n |  | TRUE
43 | bus_LV_261-276_0_4_node_81 | 0.4 | n |  | TRUE
44 | bus_LV_261-276_0_4_node_69 | 0.4 | n |  | TRUE
45 | bus_LV_261-276_0_4_node_67 | 0.4 | n |  | TRUE
46 | bus_LV_261-276_0_4_node_74 | 0.4 | n |  | TRUE
47 | bus_LV_261-276_0_4_node_89 | 0.4 | n |  | TRUE
48 | bus_LV_261-276_0_4_node_90 | 0.4 | n |  | TRUE
49 | bus_LV_261-276_0_4_node_92 | 0.4 | n |  | TRUE
50 | bus_LV_261-276_0_4_node_100 | 0.4 | n |  | TRUE
51 | bus_MV_534_0_node_56 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-276_0_4_load_0 | 0 | 0.0026556 | 0.00066555 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-276_0_4_load_1 | 1 | 0.0034171 | 0.00085641 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-276_0_4_load_93 | 2 | 0.0062068 | 0.0015556 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-276_0_4_load_5 | 3 | 0.0038242 | 0.00095843 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-276_0_4_load_31 | 4 | 0.0016072 | 0.00040279 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-276_0_4_load_95 | 6 | 0.0046968 | 0.0011771 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-276_0_4_load_65 | 8 | 0.0073991 | 0.0018544 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-276_0_4_load_80 | 12 | 0.0018179 | 0.0004556 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-276_0_4_load_99 | 13 | 0.0022422 | 0.00056196 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-276_0_4_load_10 | 15 | 0.01216 | 0.0030477 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-276_0_4_load_6 | 16 | 0.010965 | 0.002748 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-276_0_4_load_66 | 18 | 0.0075628 | 0.0018954 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-276_0_4_load_63 | 19 | 0.018966 | 0.0047533 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-276_0_4_load_7 | 20 | 0.0090539 | 0.0022691 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-276_0_4_load_9 | 21 | 0.0051277 | 0.0012851 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-276_0_4_load_46 | 22 | 0.0044058 | 0.0011042 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-276_0_4_load_85 | 23 | 0.010052 | 0.0025194 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-276_0_4_load_50 | 24 | 0.0029183 | 0.00073139 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-276_0_4_load_96 | 25 | 0.00315 | 0.00078946 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-276_0_4_load_102 | 27 | 0.0087039 | 0.0021814 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-276_0_4_load_49 | 29 | 0.00999 | 0.0025037 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-276_0_4_load_91 | 31 | 0.0088861 | 0.0022271 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-276_0_4_load_30 | 33 | 0.0079746 | 0.0019986 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-276_0_4_load_97 | 34 | 0.0030757 | 0.00077085 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-276_0_4_load_98 | 35 | 0.0049629 | 0.0012438 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-276_0_4_load_79 | 36 | 0.0091119 | 0.0022836 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-276_0_4_load_29 | 38 | 0.0086831 | 0.0021762 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-276_0_4_load_27 | 39 | 0.0077842 | 0.0019509 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-276_0_4_load_28 | 40 | 0.0059408 | 0.0014889 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-276_0_4_load_47 | 41 | 0.02232 | 0.005594 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-276_0_4_load_48 | 42 | 0.018866 | 0.0047283 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-276_0_4_load_81 | 43 | 0.0053561 | 0.0013424 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-276_0_4_load_67 | 45 | 0.0036846 | 0.00092346 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-276_0_4_load_74 | 46 | 0.0050032 | 0.0012539 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-276_0_4_load_89 | 47 | 0.054725 | 0.013715 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-276_0_4_load_90 | 48 | 0.01456 | 0.003649 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-276_0_4_load_92 | 49 | 0.0087487 | 0.0021926 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-276_0_4_load_100 | 50 | 0.0056392 | 0.0014133 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 41 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-276_0_4_line_0 |  | 0 | 1 | 0.015138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-276_0_4_line_1 |  | 0 | 2 | 0.01213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-276_0_4_line_2 |  | 1 | 3 | 0.084566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-276_0_4_line_3 |  | 1 | 4 | 0.046729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-276_0_4_line_4 |  | 4 | 38 | 0.018501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-276_0_4_line_5 |  | 5 | 6 | 0.022297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_261-276_0_4_line_6 |  | 5 | 7 | 0.013525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-276_0_4_line_7 |  | 5 | 8 | 0.0044216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_261-276_0_4_line_8 |  | 6 | 35 | 0.01285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_261-276_0_4_line_9 |  | 7 | 12 | 0.050442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-276_0_4_line_10 |  | 7 | 13 | 0.013193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-276_0_4_line_11 |  | 8 | 17 | 0.014271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_261-276_0_4_line_12 |  | 9 | 10 | 0.03633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-276_0_4_line_13 |  | 9 | 11 | 0.063034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-276_0_4_line_14 |  | 10 | 33 | 0.02012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-276_0_4_line_15 |  | 11 | 25 | 0.033349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_261-276_0_4_line_16 |  | 11 | 14 | 0.087878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_261-276_0_4_line_17 |  | 12 | 36 | 0.004093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-276_0_4_line_18 |  | 14 | 15 | 0.007226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_261-276_0_4_line_19 |  | 14 | 16 | 0.0362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-276_0_4_line_20 |  | 15 | 23 | 0.023583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-276_0_4_line_21 |  | 15 | 24 | 0.021317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_261-276_0_4_line_22 |  | 16 | 20 | 0.024284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-276_0_4_line_23 |  | 17 | 18 | 0.016315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_261-276_0_4_line_24 |  | 17 | 19 | 0.034463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-276_0_4_line_25 |  | 18 | 37 | 0.02249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_261-276_0_4_line_26 |  | 20 | 21 | 0.00075565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-276_0_4_line_27 |  | 21 | 22 | 0.020826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-276_0_4_line_28 |  | 24 | 29 | 0.016207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_261-276_0_4_line_29 |  | 25 | 34 | 0.00972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_261-276_0_4_line_30 |  | 26 | 27 | 0.041231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-276_0_4_line_31 |  | 26 | 28 | 0.11954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-276_0_4_line_32 |  | 28 | 36 | 0.12867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-276_0_4_line_33 |  | 29 | 41 | 0.010787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_261-276_0_4_line_34 |  | 30 | 31 | 0.035001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-276_0_4_line_35 |  | 30 | 32 | 0.023101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-276_0_4_line_36 |  | 31 | 47 | 0.0097724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-276_0_4_line_37 |  | 32 | 45 | 0.033488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_261-276_0_4_line_38 |  | 33 | 40 | 0.020156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-276_0_4_line_39 |  | 34 | 35 | 0.023042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_261-276_0_4_line_40 |  | 37 | 43 | 0.012278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-276_0_4_line_41 |  | 37 | 44 | 0.002868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_261-276_0_4_line_42 |  | 38 | 39 | 0.042485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-276_0_4_line_43 |  | 39 | 40 | 0.02304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-276_0_4_line_44 |  | 41 | 42 | 0.0056928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-276_0_4_line_45 |  | 44 | 46 | 0.018423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-276_0_4_line_46 |  | 44 | 45 | 0.022394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_261-276_0_4_line_47 |  | 47 | 48 | 0.0076975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-276_0_4_line_48 |  | 48 | 49 | 0.0048717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-276_0_4_line_49 |  | 49 | 50 | 0.023538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-276_0_4_trafo_47 | 0.63 MVA 20/0.4 kV | 51 | 41 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2684864.1979 | 1247572.3233 | 2684854.1261 | 1247579.9181 | 2684852.702 | 1247582.0013
1 | 2684852.702 | 1247582.0013 | 2684842.2023 | 1247588.0749
2 | 2684864.1979 | 1247572.3233 | 2684940.2215 | 1247609.3613
3 | 2684835.1335 | 1247535.7326 | 2684864.1979 | 1247572.3233
4 | 2684835.1335 | 1247535.7326 | 2684844.3389 | 1247527.5393 | 2684849.5458 | 1247524.2153
5 | 2684889.8819 | 1247356.4978 | 2684891.4169 | 1247364.2922 | 2684893.3438 | 1247371.1026 | 2684895.9647 | 1247377.4448 | 2684896.2004 | 1247377.784
6 | 2684889.8819 | 1247356.4978 | 2684890.994 | 1247356.3803 | 2684895.3745 | 1247355.8982 | 2684896.1916 | 1247355.8098 | 2684901.2984 | 1247355.2492 | 2684903.326 | 1247355.0225
7 | 2684889.8819 | 1247356.4978 | 2684889.1866 | 1247352.1312
8 | 2684896.2004 | 1247377.784 | 2684901.7006 | 1247385.6997 | 2684903.4903 | 1247388.3662
9 | 2684903.326 | 1247355.0225 | 2684906.8873 | 1247355.307 | 2684942.375 | 1247385.9237
10 | 2684903.326 | 1247355.0225 | 2684903.4754 | 1247359.8838 | 2684904.0366 | 1247365.0067 | 2684904.9962 | 1247368.0342
11 | 2684887.2084 | 1247338.0014 | 2684887.8305 | 1247343.6145 | 2684889.1866 | 1247352.1312
12 | 2684946.493 | 1247484.8478 | 2684952.3042 | 1247476.7695 | 2684954.094 | 1247472.581 | 2684956.2835 | 1247466.3299 | 2684957.1541 | 1247459.3483 | 2684957.2588 | 1247455.7361 | 2684957.1114 | 1247454.4219 | 2684956.742 | 1247451.2142
13 | 2684940.1838 | 1247443.349 | 2684935.6026 | 1247446.2411 | 2684936.4474 | 1247450.5452 | 2684933.318 | 1247453.8584 | 2684932.1819 | 1247457.2335 | 2684933.5352 | 1247457.6755 | 2684958.063 | 1247461.8076 | 2684959.2699 | 1247462.9813 | 2684963.45 | 1247458.5602 | 2684961.4606 | 1247456.1188 | 2684957.1114 | 1247454.4219 | 2684956.742 | 1247451.2142
14 | 2684946.493 | 1247484.8478 | 2684943.4931 | 1247488.085 | 2684938.931 | 1247491.7558 | 2684930.3047 | 1247496.5135
15 | 2684940.1838 | 1247443.349 | 2684930.1669 | 1247427.5938 | 2684921.9947 | 1247415.4004
16 | 2684889.9308 | 1247497.5696 | 2684917.0563 | 1247489.6187 | 2684925.6884 | 1247486.0396 | 2684931.4973 | 1247482.3423 | 2684935.5574 | 1247478.3864 | 2684938.8569 | 1247474.264 | 2684942.4396 | 1247467.2545 | 2684943.5116 | 1247463.6116 | 2684943.9023 | 1247457.9575 | 2684943.4737 | 1247453.6037 | 2684942.818 | 1247449.8137 | 2684941.3105 | 1247445.3777 | 2684940.1838 | 1247443.349
17 | 2684945.4741 | 1247388.5974 | 2684942.375 | 1247385.9237
18 | 2684889.9308 | 1247497.5696 | 2684887.9683 | 1247490.6141
19 | 2684889.9308 | 1247497.5696 | 2684881.4966 | 1247499.984 | 2684861.8998 | 1247505.9857 | 2684855.507 | 1247508.6666
20 | 2684887.9683 | 1247490.6141 | 2684899.5488 | 1247487.3886 | 2684896.0978 | 1247476.3536
21 | 2684887.9683 | 1247490.6141 | 2684875.8095 | 1247494.1316 | 2684873.3544 | 1247485.8268
22 | 2684834.6991 | 1247521.0368 | 2684842.6937 | 1247515.3067 | 2684852.0285 | 1247510.1253 | 2684855.507 | 1247508.6666
23 | 2684887.2084 | 1247338.0014 | 2684873.7959 | 1247328.7116
24 | 2684887.2084 | 1247338.0014 | 2684886.3295 | 1247326.0578 | 2684884.511 | 1247304.8271 | 2684884.5279 | 1247303.6485
25 | 2684855.3079 | 1247315.9063 | 2684873.7959 | 1247328.7116
26 | 2684834.0849 | 1247521.477 | 2684834.0849 | 1247521.477 | 2684834.6991 | 1247521.0368
27 | 2684820.12 | 1247536.8845 | 2684826.2307 | 1247529.2927 | 2684834.0849 | 1247521.477
28 | 2684873.3544 | 1247485.8268 | 2684868.7597 | 1247470.2843
29 | 2684921.9947 | 1247415.4004 | 2684917.2321 | 1247408.2943 | 2684916.5657 | 1247407.338
30 | 2684965.0435 | 1247361.1109 | 2684969.8939 | 1247356.3101 | 2684982.7792 | 1247344.8196 | 2684992.0051 | 1247338.8363 | 2684997.5961 | 1247336.1144
31 | 2684997.5961 | 1247336.1144 | 2685039.8689 | 1247401.7912 | 2685059.4115 | 1247431.7047 | 2685063.1777 | 1247436.1287
32 | 2685063.1777 | 1247436.1287 | 2685061.1502 | 1247435.8216 | 2685051.831 | 1247433.5752 | 2685014.8779 | 1247423.082 | 2684986.9267 | 1247415.3646 | 2684973.1273 | 1247408.9621 | 2684955.7599 | 1247397.4715 | 2684945.4741 | 1247388.5974
33 | 2684865.7015 | 1247459.9394 | 2684865.7015 | 1247459.9394 | 2684868.7597 | 1247470.2843
34 | 2684840.5191 | 1247380.1756 | 2684831.0988 | 1247387.0904 | 2684825.8763 | 1247393.0979 | 2684814.022 | 1247402.8574
35 | 2684840.5191 | 1247380.1756 | 2684835.5149 | 1247374.0995 | 2684833.8326 | 1247370.2504 | 2684831.2037 | 1247364.9867 | 2684827.9297 | 1247360.9925
36 | 2684806.4774 | 1247409.0687 | 2684814.022 | 1247402.8574
37 | 2684827.9297 | 1247360.9925 | 2684827.8371 | 1247351.6286 | 2684829.1306 | 1247340.9504 | 2684838.0319 | 1247330.978
38 | 2684930.3047 | 1247496.5135 | 2684930.3047 | 1247496.5135 | 2684911.4547 | 1247502.0477 | 2684910.9661 | 1247502.1949
39 | 2684916.5657 | 1247407.338 | 2684907.2845 | 1247394.0191 | 2684903.4903 | 1247388.3662
40 | 2684855.3079 | 1247315.9063 | 2684847.2071 | 1247325.1331
41 | 2684852.9444 | 1247314.2713 | 2684855.3079 | 1247315.9063
42 | 2684849.5458 | 1247524.2153 | 2684856.8944 | 1247519.5241 | 2684865.7437 | 1247516.0704 | 2684870.716 | 1247514.3403 | 2684888.9062 | 1247508.842
43 | 2684888.9062 | 1247508.842 | 2684889.9627 | 1247508.5226 | 2684910.9661 | 1247502.1949
44 | 2684865.7015 | 1247459.9394 | 2684871.2179 | 1247458.5329
45 | 2684852.9444 | 1247314.2713 | 2684837.7584 | 1247303.8415
46 | 2684852.9444 | 1247314.2713 | 2684838.0319 | 1247330.978
47 | 2684806.4774 | 1247409.0687 | 2684800.5347 | 1247413.9611
48 | 2684800.5347 | 1247413.9611 | 2684796.7737 | 1247417.0575
49 | 2684778.1179 | 1247431.3878 | 2684787.7494 | 1247424.4871 | 2684796.7737 | 1247417.0575

## bus_geodata
| x | y | coords
0 | 2684852.702 | 1247582.0013
1 | 2684864.1979 | 1247572.3233
2 | 2684842.2023 | 1247588.0749
3 | 2684940.2215 | 1247609.3613
4 | 2684835.1335 | 1247535.7326
5 | 2684889.8819 | 1247356.4978
6 | 2684896.2004 | 1247377.784
7 | 2684903.326 | 1247355.0225
8 | 2684889.1866 | 1247352.1312
9 | 2684956.742 | 1247451.2142
10 | 2684946.493 | 1247484.8478
11 | 2684940.1838 | 1247443.349
12 | 2684942.375 | 1247385.9237
13 | 2684904.9962 | 1247368.0342
14 | 2684889.9308 | 1247497.5696
15 | 2684887.9683 | 1247490.6141
16 | 2684855.507 | 1247508.6666
17 | 2684887.2084 | 1247338.0014
18 | 2684873.7959 | 1247328.7116
19 | 2684884.5279 | 1247303.6485
20 | 2684834.6991 | 1247521.0368
21 | 2684834.0849 | 1247521.477
22 | 2684820.12 | 1247536.8845
23 | 2684896.0978 | 1247476.3536
24 | 2684873.3544 | 1247485.8268
25 | 2684921.9947 | 1247415.4004
26 | 2684997.5961 | 1247336.1144
27 | 2684965.0435 | 1247361.1109
28 | 2685063.1777 | 1247436.1287
29 | 2684868.7597 | 1247470.2843
30 | 2684840.5191 | 1247380.1756
31 | 2684814.022 | 1247402.8574
32 | 2684827.9297 | 1247360.9924
33 | 2684930.3047 | 1247496.5135
34 | 2684916.5657 | 1247407.338
35 | 2684903.4903 | 1247388.3662
36 | 2684945.4741 | 1247388.5974
37 | 2684855.3079 | 1247315.9063
38 | 2684849.5458 | 1247524.2153
39 | 2684888.9062 | 1247508.842
40 | 2684910.9661 | 1247502.1949
41 | 2684865.7015 | 1247459.9394
42 | 2684871.2179 | 1247458.5329
43 | 2684847.2071 | 1247325.1331
44 | 2684852.9444 | 1247314.2713
45 | 2684838.0319 | 1247330.978
46 | 2684837.7584 | 1247303.8415
47 | 2684806.4774 | 1247409.0687
48 | 2684800.5347 | 1247413.9611
49 | 2684796.7737 | 1247417.0575
50 | 2684778.1179 | 1247431.3878
51 | 2684883.0855 | 1247455.5071

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98014 | -0.38184 | 0.0026556 | 0.00066555
1 | 0.98026 | -0.37941 | 0.0034171 | 0.00085641
2 | 0.98007 | -0.38321 | 0.0062068 | 0.0015556
3 | 0.97996 | -0.38528 | 0.0038242 | 0.00095843
4 | 0.98096 | -0.36577 | 0.0016072 | 0.00040279
5 | 0.9837 | -0.31161 | 0 | 0
6 | 0.98482 | -0.28989 | 0.0046968 | 0.0011771
7 | 0.98343 | -0.31694 | 0 | 0
8 | 0.98351 | -0.31534 | 0.0073991 | 0.0018544
9 | 0.98628 | -0.26198 | 0 | 0
10 | 0.98466 | -0.29334 | 0 | 0
11 | 0.98908 | -0.2078 | 0 | 0
12 | 0.98252 | -0.33482 | 0.0018179 | 0.0004556
13 | 0.9834 | -0.31748 | 0.0022422 | 0.00056196
14 | 0.99523 | -0.090353 | 0 | 0
15 | 0.9958 | -0.079509 | 0.01216 | 0.0030477
16 | 0.99425 | -0.1092 | 0.010965 | 0.002748
17 | 0.98292 | -0.32676 | 0 | 0
18 | 0.98235 | -0.33797 | 0.0075628 | 0.0018954
19 | 0.98232 | -0.33856 | 0.018966 | 0.0047533
20 | 0.99384 | -0.11716 | 0.0090539 | 0.0022691
21 | 0.99384 | -0.11729 | 0.0051277 | 0.0012851
22 | 0.99375 | -0.11891 | 0.0044058 | 0.0011042
23 | 0.99558 | -0.083677 | 0.010052 | 0.0025194
24 | 0.99763 | -0.044824 | 0.0029183 | 0.00073139
25 | 0.98724 | -0.24318 | 0.00315 | 0.00078946
26 | 0.98045 | -0.37525 | 0 | 0
27 | 0.98012 | -0.38176 | 0.0087039 | 0.0021814
28 | 0.98141 | -0.3564 | 0 | 0
29 | 0.99903 | -0.018264 | 0.00999 | 0.0025037
30 | 0.97789 | -0.42481 | 0 | 0
31 | 0.97487 | -0.48404 | 0.0088861 | 0.0022271
32 | 0.97988 | -0.38591 | 0 | 0
33 | 0.98377 | -0.31076 | 0.0079746 | 0.0019986
34 | 0.98671 | -0.25334 | 0.0030757 | 0.00077085
35 | 0.98549 | -0.27703 | 0.0049629 | 0.0012438
36 | 0.98245 | -0.33613 | 0.0091119 | 0.0022836
37 | 0.9816 | -0.35242 | 0 | 0
38 | 0.98126 | -0.35983 | 0.0086831 | 0.0021762
39 | 0.9823 | -0.33955 | 0.0077842 | 0.0019509
40 | 0.98302 | -0.32533 | 0.0059408 | 0.0014889
41 | 1 | 0 | -0.31629 | -0.080668
42 | 0.9999 | -0.0018721 | 0.018866 | 0.0047283
43 | 0.98154 | -0.35361 | 0.0053561 | 0.0013424
44 | 0.98151 | -0.35417 | 0 | 0
45 | 0.98084 | -0.36718 | 0.0036846 | 0.00092346
46 | 0.98143 | -0.35584 | 0.0050032 | 0.0012539
47 | 0.97411 | -0.49905 | 0.054725 | 0.013715
48 | 0.97391 | -0.50314 | 0.01456 | 0.003649
49 | 0.97384 | -0.50443 | 0.0087487 | 0.0021926
50 | 0.97372 | -0.50687 | 0.0056392 | 0.0014133
51 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0088628 | -0.0022212 | 0.0088638 | 0.0022217 | 1.0277e-06 | 4.6693e-07 | 0.013455 | 0.013455 | 0.013455 | 0.98014 | -0.38184 | 0.98026 | -0.37941 | 3.6965
1 | 0.0062072 | 0.0015557 | -0.0062068 | -0.0015556 | 4.0395e-07 | 1.0566e-07 | 0.0094236 | 0.0094237 | 0.0094237 | 0.98014 | -0.38184 | 0.98007 | -0.38321 | 2.5889
2 | 0.0038253 | 0.00095805 | -0.0038242 | -0.00095843 | 1.0692e-06 | -3.8144e-07 | 0.0058064 | 0.0058068 | 0.0058068 | 0.98026 | -0.37941 | 0.97996 | -0.38528 | 1.5953
3 | -0.016106 | -0.0040362 | 0.016117 | 0.0040423 | 1.0474e-05 | 6.1141e-06 | 0.024449 | 0.024449 | 0.024449 | 0.98026 | -0.37941 | 0.98096 | -0.36577 | 6.7167
4 | -0.017724 | -0.0044451 | 0.017729 | 0.004448 | 5.0152e-06 | 2.9761e-06 | 0.026886 | 0.026886 | 0.026886 | 0.98096 | -0.36577 | 0.98126 | -0.35983 | 7.3864
5 | -0.16335 | -0.041296 | 0.16352 | 0.041404 | 0.00017035 | 0.00010817 | 0.24722 | 0.24722 | 0.24722 | 0.9837 | -0.31161 | 0.98482 | -0.28989 | 22.6394
6 | 0.021918 | 0.0055051 | -0.021913 | -0.0055017 | 5.5767e-06 | 3.3975e-06 | 0.033159 | 0.033159 | 0.033159 | 0.9837 | -0.31161 | 0.98343 | -0.31694 | 9.1098
7 | 0.14143 | 0.035791 | -0.14141 | -0.035775 | 2.5326e-05 | 1.604e-05 | 0.21406 | 0.21406 | 0.21406 | 0.9837 | -0.31161 | 0.98351 | -0.31534 | 19.6029
8 | -0.16822 | -0.042581 | 0.16832 | 0.042647 | 0.00010389 | 6.6001e-05 | 0.25432 | 0.25432 | 0.25432 | 0.98482 | -0.28989 | 0.98549 | -0.27703 | 23.2893
9 | 0.019671 | 0.0049399 | -0.019654 | -0.0049298 | 1.6761e-05 | 1.0087e-05 | 0.029767 | 0.029767 | 0.029767 | 0.98343 | -0.31694 | 0.98252 | -0.33482 | 8.1777
10 | 0.0022423 | 0.00056183 | -0.0022422 | -0.00056196 | 5.6949e-08 | -1.3094e-07 | 0.0033927 | 0.0033928 | 0.0033928 | 0.98343 | -0.31694 | 0.9834 | -0.31748 | 0.93209
11 | 0.13401 | 0.03392 | -0.13393 | -0.033874 | 7.3419e-05 | 4.6445e-05 | 0.20287 | 0.20287 | 0.20287 | 0.98351 | -0.31534 | 0.98292 | -0.32676 | 18.5777
12 | 0.048301 | 0.012182 | -0.048228 | -0.012136 | 7.2402e-05 | 4.5875e-05 | 0.072899 | 0.0729 | 0.0729 | 0.98628 | -0.26198 | 0.98466 | -0.29334 | 20.0274
13 | -0.048301 | -0.012182 | 0.048426 | 0.012262 | 0.00012562 | 7.9589e-05 | 0.072899 | 0.072899 | 0.072899 | 0.98628 | -0.26198 | 0.98908 | -0.2078 | 20.0273
14 | 0.048228 | 0.012136 | -0.048188 | -0.012111 | 4.0098e-05 | 2.5407e-05 | 0.0729 | 0.0729 | 0.0729 | 0.98466 | -0.29334 | 0.98377 | -0.31076 | 20.0274
15 | 0.1801 | 0.045827 | -0.17979 | -0.045632 | 0.00030659 | 0.00019494 | 0.2712 | 0.2712 | 0.2712 | 0.98908 | -0.2078 | 0.98724 | -0.24318 | 24.835
16 | -0.22853 | -0.058088 | 0.22983 | 0.058917 | 0.0013006 | 0.00082899 | 0.3441 | 0.3441 | 0.3441 | 0.98908 | -0.2078 | 0.99523 | -0.090353 | 31.5107
17 | 0.017836 | 0.0044742 | -0.017835 | -0.0044735 | 1.1201e-06 | 6.6501e-07 | 0.027014 | 0.027014 | 0.027014 | 0.98252 | -0.33482 | 0.98245 | -0.33613 | 7.4214
18 | -0.25941 | -0.066344 | 0.25955 | 0.066431 | 0.00013621 | 8.6895e-05 | 0.38833 | 0.38833 | 0.38833 | 0.99523 | -0.090353 | 0.9958 | -0.079509 | 35.5618
19 | 0.029586 | 0.0074272 | -0.02956 | -0.0074106 | 2.6569e-05 | 1.6534e-05 | 0.04424 | 0.04424 | 0.04424 | 0.99523 | -0.090353 | 0.99425 | -0.1092 | 12.1539
20 | 0.010054 | 0.0025203 | -0.010052 | -0.0025194 | 1.9963e-06 | 9.709e-07 | 0.015024 | 0.015024 | 0.015024 | 0.9958 | -0.079509 | 0.99558 | -0.083677 | 4.1276
21 | -0.28176 | -0.071999 | 0.28224 | 0.072301 | 0.00047348 | 0.00030219 | 0.42153 | 0.42153 | 0.42153 | 0.9958 | -0.079509 | 0.99763 | -0.044824 | 38.6016
22 | 0.018595 | 0.0046626 | -0.018588 | -0.0046584 | 7.0533e-06 | 4.1993e-06 | 0.02783 | 0.02783 | 0.02783 | 0.99425 | -0.1092 | 0.99384 | -0.11716 | 7.6457
23 | 0.11496 | 0.029114 | -0.1149 | -0.029075 | 6.1845e-05 | 3.8961e-05 | 0.17414 | 0.17414 | 0.17414 | 0.98292 | -0.32676 | 0.98235 | -0.33797 | 15.9469
24 | 0.018977 | 0.0047597 | -0.018966 | -0.0047533 | 1.0667e-05 | 6.3904e-06 | 0.02873 | 0.02873 | 0.02873 | 0.98292 | -0.32676 | 0.98232 | -0.33856 | 7.8928
25 | 0.10733 | 0.02718 | -0.10726 | -0.027133 | 7.4401e-05 | 4.6763e-05 | 0.16268 | 0.16268 | 0.16268 | 0.98235 | -0.33797 | 0.9816 | -0.35242 | 14.8978
26 | 0.0095339 | 0.0023893 | -0.0095339 | -0.0023893 | 5.774e-08 | 2.7162e-08 | 0.014274 | 0.014274 | 0.014274 | 0.99384 | -0.11716 | 0.99384 | -0.11729 | 3.9216
27 | 0.0044061 | 0.0011041 | -0.0044058 | -0.0011042 | 3.3989e-07 | -5.231e-08 | 0.006597 | 0.0065971 | 0.0065971 | 0.99384 | -0.11729 | 0.99375 | -0.11891 | 1.8124
28 | -0.28516 | -0.073033 | 0.28552 | 0.073267 | 0.00036745 | 0.00023453 | 0.42588 | 0.42588 | 0.42588 | 0.99763 | -0.044824 | 0.99903 | -0.018264 | 39.0002
29 | 0.17664 | 0.044842 | -0.17656 | -0.044787 | 8.626e-05 | 5.4834e-05 | 0.26645 | 0.26645 | 0.26645 | 0.98724 | -0.24318 | 0.98671 | -0.25334 | 24.4002
30 | 0.0087066 | 0.0021826 | -0.0087039 | -0.0021814 | 2.6998e-06 | 1.2081e-06 | 0.013214 | 0.013214 | 0.013214 | 0.98045 | -0.37525 | 0.98012 | -0.38176 | 3.6303
31 | -0.0087066 | -0.0021826 | 0.0087145 | 0.0021861 | 7.8275e-06 | 3.5005e-06 | 0.013214 | 0.013214 | 0.013214 | 0.98045 | -0.37525 | 0.98141 | -0.3564 | 3.6303
32 | -0.0087145 | -0.0021861 | 0.0087229 | 0.0021899 | 8.4242e-06 | 3.7639e-06 | 0.013214 | 0.013213 | 0.013214 | 0.98141 | -0.3564 | 0.98245 | -0.33613 | 3.6301
33 | -0.29551 | -0.075771 | 0.29578 | 0.075938 | 0.00026196 | 0.00016723 | 0.44076 | 0.44076 | 0.44076 | 0.99903 | -0.018264 | 1 | 0 | 40.3628
34 | 0.092888 | 0.023407 | -0.092626 | -0.02324 | 0.00026239 | 0.00016749 | 0.14139 | 0.14139 | 0.14139 | 0.97789 | -0.42481 | 0.97487 | -0.48404 | 38.8434
35 | -0.092888 | -0.023407 | 0.093061 | 0.023518 | 0.00017318 | 0.00011054 | 0.14139 | 0.14139 | 0.14139 | 0.97789 | -0.42481 | 0.97988 | -0.38591 | 38.8434
36 | 0.083739 | 0.021013 | -0.08368 | -0.020974 | 5.9879e-05 | 3.8201e-05 | 0.12783 | 0.12783 | 0.12783 | 0.97487 | -0.48404 | 0.97411 | -0.49905 | 35.1172
37 | -0.093061 | -0.023518 | 0.093145 | 0.02357 | 8.3682e-05 | 5.229e-05 | 0.14139 | 0.14139 | 0.14139 | 0.97988 | -0.38591 | 0.98084 | -0.36718 | 12.9478
38 | 0.040214 | 0.010112 | -0.040186 | -0.010094 | 2.7976e-05 | 1.7649e-05 | 0.060838 | 0.060838 | 0.060838 | 0.98377 | -0.31076 | 0.98302 | -0.32533 | 16.7137
39 | 0.17348 | 0.044017 | -0.17328 | -0.043891 | 0.00019743 | 0.00012547 | 0.26181 | 0.26181 | 0.26181 | 0.98671 | -0.25334 | 0.98549 | -0.27703 | 23.9755
40 | 0.0053564 | 0.0013424 | -0.0053561 | -0.0013424 | 3.0358e-07 | 3.9088e-08 | 0.0081198 | 0.0081199 | 0.0081199 | 0.9816 | -0.35242 | 0.98154 | -0.35361 | 2.2307
41 | 0.1019 | 0.025791 | -0.10189 | -0.025785 | 8.5646e-06 | 5.3726e-06 | 0.15456 | 0.15456 | 0.15456 | 0.9816 | -0.35242 | 0.98151 | -0.35417 | 14.1542
42 | -0.026412 | -0.0066242 | 0.026438 | 0.00664 | 2.556e-05 | 1.5821e-05 | 0.040054 | 0.040054 | 0.040054 | 0.98126 | -0.35983 | 0.9823 | -0.33955 | 11.0038
43 | -0.034222 | -0.0085909 | 0.034245 | 0.0086055 | 2.3223e-05 | 1.4571e-05 | 0.051845 | 0.051845 | 0.051845 | 0.9823 | -0.33955 | 0.98302 | -0.32533 | 14.2432
44 | 0.018868 | 0.0047293 | -0.018866 | -0.0047283 | 1.6828e-06 | 1.0023e-06 | 0.028076 | 0.028076 | 0.028076 | 1 | 0 | 0.9999 | -0.0018721 | 7.7132
45 | 0.0050036 | 0.0012539 | -0.0050032 | -0.0012539 | 3.9753e-07 | 2.1601e-08 | 0.0075856 | 0.0075857 | 0.0075857 | 0.98151 | -0.35417 | 0.98143 | -0.35584 | 2.084
46 | 0.09689 | 0.024531 | -0.09683 | -0.024493 | 6.0472e-05 | 3.7854e-05 | 0.14698 | 0.14698 | 0.14698 | 0.98151 | -0.35417 | 0.98084 | -0.36718 | 13.4596
47 | 0.028955 | 0.0072591 | -0.028949 | -0.0072556 | 5.6473e-06 | 3.5185e-06 | 0.044231 | 0.044231 | 0.044231 | 0.97411 | -0.49905 | 0.97391 | -0.50314 | 12.1515
48 | 0.014389 | 0.0036066 | -0.014389 | -0.0036061 | 8.8306e-07 | 5.0454e-07 | 0.021986 | 0.021986 | 0.021986 | 0.97391 | -0.50314 | 0.97384 | -0.50443 | 6.04
49 | 0.0056399 | 0.0014134 | -0.0056392 | -0.0014133 | 6.555e-07 | 1.2671e-07 | 0.0086176 | 0.0086177 | 0.0086177 | 0.97384 | -0.50443 | 0.97372 | -0.50687 | 2.3675

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.33861 | 0.086262

## res_load
| p_mw | q_mvar
0 | 0.0026556 | 0.00066555
1 | 0.0034171 | 0.00085641
2 | 0.0062068 | 0.0015556
3 | 0.0038242 | 0.00095843
4 | 0.0016072 | 0.00040279
5 | 0.0046968 | 0.0011771
6 | 0.0073991 | 0.0018544
7 | 0.0018179 | 0.0004556
8 | 0.0022422 | 0.00056196
9 | 0.01216 | 0.0030477
10 | 0.010965 | 0.002748
11 | 0.0075628 | 0.0018954
12 | 0.018966 | 0.0047533
13 | 0.0090539 | 0.0022691
14 | 0.0051277 | 0.0012851
15 | 0.0044058 | 0.0011042
16 | 0.010052 | 0.0025194
17 | 0.0029183 | 0.00073139
18 | 0.00315 | 0.00078946
19 | 0.0087039 | 0.0021814
20 | 0.00999 | 0.0025037
21 | 0.0088861 | 0.0022271
22 | 0.0079746 | 0.0019986
23 | 0.0030757 | 0.00077085
24 | 0.0049629 | 0.0012438
25 | 0.0091119 | 0.0022836
26 | 0.0086831 | 0.0021762
27 | 0.0077842 | 0.0019509
28 | 0.0059408 | 0.0014889
29 | 0.02232 | 0.005594
30 | 0.018866 | 0.0047283
31 | 0.0053561 | 0.0013424
32 | 0.0036846 | 0.00092346
33 | 0.0050032 | 0.0012539
34 | 0.054725 | 0.013715
35 | 0.01456 | 0.003649
36 | 0.0087487 | 0.0021926
37 | 0.0056392 | 0.0014133

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1