## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-276_1_2_node_17 | 0.4 | n |  | TRUE
1 | bus_LV_261-276_1_2_node_24 | 0.4 | n |  | TRUE
2 | bus_LV_261-276_1_2_node_37 | 0.4 | n |  | TRUE
3 | bus_LV_261-276_1_2_node_22 | 0.4 | n |  | TRUE
4 | bus_LV_261-276_1_2_node_23 | 0.4 | n |  | TRUE
5 | bus_LV_261-276_1_2_node_25 | 0.4 | n |  | TRUE
6 | bus_LV_261-276_1_2_node_26 | 0.4 | n |  | TRUE
7 | bus_LV_261-276_1_2_node_44 | 0.4 | n |  | TRUE
8 | bus_LV_261-276_1_2_node_33 | 0.4 | n |  | TRUE
9 | bus_LV_261-276_1_2_node_34 | 0.4 | n |  | TRUE
10 | bus_LV_261-276_1_2_node_35 | 0.4 | n |  | TRUE
11 | bus_LV_261-276_1_2_node_41 | 0.4 | n |  | TRUE
12 | bus_LV_261-276_1_2_node_38 | 0.4 | n |  | TRUE
13 | bus_LV_261-276_1_2_node_36 | 0.4 | n |  | TRUE
14 | bus_LV_261-276_1_2_node_39 | 0.4 | n |  | TRUE
15 | bus_LV_261-276_1_2_node_40 | 0.4 | n |  | TRUE
16 | bus_LV_261-276_1_2_node_45 | 0.4 | n |  | TRUE
17 | bus_LV_261-276_1_2_node_58 | 0.4 | n |  | TRUE
18 | bus_LV_261-276_1_2_node_51 | 0.4 | n |  | TRUE
19 | bus_LV_261-276_1_2_node_52 | 0.4 | n |  | TRUE
20 | bus_LV_261-276_1_2_node_53 | 0.4 | n |  | TRUE
21 | bus_LV_261-276_1_2_node_54 | 0.4 | n |  | TRUE
22 | bus_LV_261-276_1_2_node_55 | 0.4 | n |  | TRUE
23 | bus_LV_261-276_1_2_node_56 | 0.4 | n |  | TRUE
24 | bus_LV_261-276_1_2_node_78 | 0.4 | n |  | TRUE
25 | bus_LV_261-276_1_2_node_62 | 0.4 | n |  | TRUE
26 | bus_LV_261-276_1_2_node_76 | 0.4 | n |  | TRUE
27 | bus_LV_261-276_1_2_node_57 | 0.4 | n |  | TRUE
28 | bus_LV_261-276_1_2_node_59 | 0.4 | n |  | TRUE
29 | bus_LV_261-276_1_2_node_60 | 0.4 | n |  | TRUE
30 | bus_LV_261-276_1_2_node_61 | 0.4 | n |  | TRUE
31 | bus_LV_261-276_1_2_node_88 | 0.4 | n |  | TRUE
32 | bus_LV_261-276_1_2_node_71 | 0.4 | n |  | TRUE
33 | bus_LV_261-276_1_2_node_84 | 0.4 | n |  | TRUE
34 | bus_LV_261-276_1_2_node_86 | 0.4 | n |  | TRUE
35 | bus_LV_261-276_1_2_node_75 | 0.4 | n |  | TRUE
36 | bus_LV_261-276_1_2_node_77 | 0.4 | n |  | TRUE
37 | bus_LV_261-276_1_2_node_82 | 0.4 | n |  | TRUE
38 | bus_LV_261-276_1_2_node_83 | 0.4 | n |  | TRUE
39 | bus_LV_261-276_1_2_node_94 | 0.4 | n |  | TRUE
40 | bus_LV_261-276_1_2_node_87 | 0.4 | n |  | TRUE
41 | bus_LV_261-276_1_2_node_101 | 0.4 | n |  | TRUE
42 | bus_MV_534_0_node_101 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-276_1_2_load_37 | 2 | 0.0048152 | 0.0012068 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-276_1_2_load_22 | 3 | 0.0050643 | 0.0012692 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-276_1_2_load_23 | 4 | 0.0060918 | 0.0015267 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-276_1_2_load_25 | 5 | 0.0065594 | 0.0016439 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-276_1_2_load_26 | 6 | 0.003608 | 0.00090424 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-276_1_2_load_44 | 7 | 0.0017201 | 0.00043109 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-276_1_2_load_33 | 8 | 0.0088791 | 0.0022253 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-276_1_2_load_34 | 9 | 0.011498 | 0.0028816 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-276_1_2_load_41 | 11 | 0.0043831 | 0.0010985 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-276_1_2_load_38 | 12 | 0.0089453 | 0.0022419 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-276_1_2_load_36 | 13 | 0.0040737 | 0.001021 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-276_1_2_load_39 | 14 | 0.0045622 | 0.0011434 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-276_1_2_load_40 | 15 | 0.0033025 | 0.00082769 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-276_1_2_load_58 | 17 | 0.005628 | 0.0014105 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-276_1_2_load_51 | 18 | 0.0036592 | 0.00091709 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-276_1_2_load_52 | 19 | 0.0040257 | 0.0010089 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-276_1_2_load_54 | 21 | 0.0043969 | 0.001102 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-276_1_2_load_55 | 22 | 0.0056151 | 0.0014073 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-276_1_2_load_56 | 23 | 0.0058572 | 0.001468 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-276_1_2_load_78 | 24 | 0.0012714 | 0.00031863 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-276_1_2_load_62 | 25 | 0.0056401 | 0.0014135 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-276_1_2_load_76 | 26 | 0.0030018 | 0.00075233 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-276_1_2_load_57 | 27 | 0.0043141 | 0.0010812 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-276_1_2_load_60 | 29 | 0.0014913 | 0.00037375 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-276_1_2_load_86 | 34 | 0.012159 | 0.0030474 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-276_1_2_load_75 | 35 | 0.0034256 | 0.00085852 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-276_1_2_load_77 | 36 | 0.0046583 | 0.0011675 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-276_1_2_load_82 | 37 | 0.015219 | 0.0038143 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-276_1_2_load_94 | 39 | 0.0047524 | 0.0011911 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-276_1_2_load_101 | 41 | 0.0047326 | 0.0011861 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 24 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-276_1_2_line_0 |  | 0 | 1 | 0.006256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-276_1_2_line_1 |  | 0 | 2 | 0.022862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-276_1_2_line_2 |  | 1 | 6 | 0.04249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-276_1_2_line_3 |  | 1 | 3 | 0.023466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-276_1_2_line_4 |  | 2 | 13 | 0.020666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-276_1_2_line_5 |  | 3 | 4 | 0.0014376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-276_1_2_line_6 |  | 4 | 5 | 0.036938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-276_1_2_line_7 |  | 5 | 7 | 0.0050936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-276_1_2_line_8 |  | 6 | 8 | 0.01972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-276_1_2_line_9 |  | 7 | 16 | 0.01266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-276_1_2_line_10 |  | 8 | 9 | 0.013518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-276_1_2_line_11 |  | 9 | 10 | 0.049526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-276_1_2_line_12 |  | 10 | 11 | 0.016662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-276_1_2_line_13 |  | 10 | 12 | 0.01965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-276_1_2_line_14 |  | 12 | 14 | 0.014966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-276_1_2_line_15 |  | 14 | 15 | 0.011162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-276_1_2_line_16 |  | 16 | 17 | 0.013181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-276_1_2_line_17 |  | 17 | 27 | 0.028519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-276_1_2_line_18 |  | 18 | 19 | 1.0137e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_261-276_1_2_line_19 |  | 18 | 20 | 0.015265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_261-276_1_2_line_20 |  | 19 | 21 | 0.014611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_261-276_1_2_line_21 |  | 20 | 22 | 0.023346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-276_1_2_line_22 |  | 20 | 23 | 0.0053612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-276_1_2_line_23 |  | 21 | 24 | 0.0075085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_261-276_1_2_line_24 |  | 22 | 25 | 0.016538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-276_1_2_line_25 |  | 23 | 26 | 0.022952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-276_1_2_line_26 |  | 25 | 30 | 0.018155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-276_1_2_line_27 |  | 26 | 35 | 0.02514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-276_1_2_line_28 |  | 27 | 28 | 0.0046826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-276_1_2_line_29 |  | 28 | 29 | 0.029833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-276_1_2_line_30 |  | 28 | 30 | 0.021371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-276_1_2_line_31 |  | 30 | 31 | 0.043965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-276_1_2_line_32 |  | 31 | 41 | 0.003114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-276_1_2_line_33 |  | 31 | 40 | 0.040204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-276_1_2_line_34 |  | 32 | 33 | 0.024969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-276_1_2_line_35 |  | 32 | 34 | 0.039469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-276_1_2_line_36 |  | 33 | 39 | 0.021437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-276_1_2_line_37 |  | 33 | 38 | 0.031462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-276_1_2_line_38 |  | 34 | 40 | 0.011133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-276_1_2_line_39 |  | 35 | 36 | 0.00208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-276_1_2_line_40 |  | 37 | 38 | 0.019278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-276_1_2_trafo_78 | 0.63 MVA 20/0.4 kV | 42 | 24 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2684802.1257 | 1247563.1953 | 2684796.8875 | 1247559.7512
1 | 2684802.1257 | 1247563.1953 | 2684800.6141 | 1247566.4205 | 2684797.2699 | 1247575.257 | 2684793.4027 | 1247584.3187
2 | 2684796.8875 | 1247559.7512 | 2684791.2979 | 1247561.3391 | 2684779.7011 | 1247560.9619 | 2684755.4815 | 1247567.4622
3 | 2684796.8875 | 1247559.7512 | 2684790.1956 | 1247551.2714 | 2684784.3115 | 1247540.0576
4 | 2684785.3037 | 1247603.3314 | 2684790.7752 | 1247590.4754 | 2684793.4027 | 1247584.3187
5 | 2684783.6436 | 1247538.7847 | 2684784.3115 | 1247540.0576
6 | 2684783.6436 | 1247538.7847 | 2684772.1365 | 1247516.8544 | 2684765.5606 | 1247506.6112
7 | 2684765.5606 | 1247506.6112 | 2684762.8088 | 1247502.3248
8 | 2684755.4815 | 1247567.4622 | 2684736.4356 | 1247572.574
9 | 2684755.9695 | 1247491.6714 | 2684762.8088 | 1247502.3248
10 | 2684723.3799 | 1247576.078 | 2684736.4356 | 1247572.574
11 | 2684675.5829 | 1247589.0507 | 2684721.7626 | 1247576.5121 | 2684723.3799 | 1247576.078
12 | 2684675.5829 | 1247589.0507 | 2684659.5771 | 1247593.6799
13 | 2684675.5829 | 1247589.0507 | 2684670.5262 | 1247570.062
14 | 2684670.5262 | 1247570.062 | 2684668.4284 | 1247562.1842 | 2684665.0154 | 1247556.2867
15 | 2684654.2961 | 1247553.1758 | 2684665.0154 | 1247556.2867
16 | 2684755.9695 | 1247491.6714 | 2684747.8015 | 1247481.3258
17 | 2684730.1292 | 1247458.9423 | 2684747.8015 | 1247481.3258
18 | 2684676.0699 | 1247483.3413 | 2684676.0693 | 1247483.3405
19 | 2684667.0875 | 1247470.9976 | 2684676.0693 | 1247483.3405
20 | 2684676.0699 | 1247483.3413 | 2684684.6669 | 1247495.1554
21 | 2684667.0875 | 1247470.9976 | 2684686.2617 | 1247457.6792
22 | 2684667.0875 | 1247470.9976 | 2684662.7052 | 1247474.0861
23 | 2684690.7796 | 1247490.795 | 2684684.6669 | 1247495.1554
24 | 2684686.2617 | 1247457.6792 | 2684699.8448 | 1247448.2443
25 | 2684643.9438 | 1247487.3083 | 2684662.7052 | 1247474.0861
26 | 2684714.7556 | 1247437.8872 | 2684699.8448 | 1247448.2443
27 | 2684623.3941 | 1247501.7909 | 2684643.9438 | 1247487.3083
28 | 2684727.2275 | 1247455.2671 | 2684730.1292 | 1247458.9423
29 | 2684727.2275 | 1247455.2671 | 2684738.898 | 1247447.328 | 2684731.9836 | 1247437.4886 | 2684729.8368 | 1247434.4334
30 | 2684714.7556 | 1247437.8872 | 2684727.2275 | 1247455.2671
31 | 2684714.7556 | 1247437.8872 | 2684739.0706 | 1247421.5225 | 2684751.0877 | 1247413.1324
32 | 2684751.0877 | 1247413.1324 | 2684749.1205 | 1247410.7136
33 | 2684729.5008 | 1247400.3478 | 2684727.153 | 1247404.4729 | 2684739.0706 | 1247421.5225 | 2684751.0877 | 1247413.1324
34 | 2684692.927 | 1247365.3773 | 2684680.1113 | 1247379.9718 | 2684676.217 | 1247383.9636
35 | 2684692.927 | 1247365.3773 | 2684721.454 | 1247392.6538
36 | 2684676.217 | 1247383.9636 | 2684684.3001 | 1247392.9079 | 2684689.5599 | 1247400.6757
37 | 2684645.1758 | 1247379.4171 | 2684659.8612 | 1247379.8715 | 2684676.217 | 1247383.9636
38 | 2684729.5008 | 1247400.3478 | 2684721.454 | 1247392.6538
39 | 2684623.3941 | 1247501.7909 | 2684621.6939 | 1247502.9891
40 | 2684645.1758 | 1247379.4171 | 2684647.1866 | 1247398.5898

## bus_geodata
| x | y | coords
0 | 2684802.1257 | 1247563.1953
1 | 2684796.8875 | 1247559.7512
2 | 2684793.4027 | 1247584.3187
3 | 2684784.3115 | 1247540.0576
4 | 2684783.6436 | 1247538.7847
5 | 2684765.5606 | 1247506.6112
6 | 2684755.4815 | 1247567.4622
7 | 2684762.8088 | 1247502.3248
8 | 2684736.4356 | 1247572.574
9 | 2684723.3799 | 1247576.078
10 | 2684675.5829 | 1247589.0507
11 | 2684659.5771 | 1247593.6799
12 | 2684670.5262 | 1247570.062
13 | 2684785.3037 | 1247603.3314
14 | 2684665.0154 | 1247556.2867
15 | 2684654.2961 | 1247553.1758
16 | 2684755.9695 | 1247491.6714
17 | 2684747.8015 | 1247481.3258
18 | 2684676.0693 | 1247483.3405
19 | 2684676.0699 | 1247483.3413
20 | 2684667.0875 | 1247470.9976
21 | 2684684.6669 | 1247495.1554
22 | 2684686.2617 | 1247457.6792
23 | 2684662.7052 | 1247474.0861
24 | 2684690.7796 | 1247490.795
25 | 2684699.8448 | 1247448.2443
26 | 2684643.9438 | 1247487.3083
27 | 2684730.1292 | 1247458.9423
28 | 2684727.2275 | 1247455.2671
29 | 2684729.8368 | 1247434.4334
30 | 2684714.7556 | 1247437.8872
31 | 2684751.0876 | 1247413.1324
32 | 2684692.927 | 1247365.3774
33 | 2684676.217 | 1247383.9636
34 | 2684721.454 | 1247392.6538
35 | 2684623.3941 | 1247501.7909
36 | 2684621.6939 | 1247502.9891
37 | 2684647.1866 | 1247398.5898
38 | 2684645.1758 | 1247379.4171
39 | 2684689.5599 | 1247400.6757
40 | 2684729.5008 | 1247400.3478
41 | 2684749.1205 | 1247410.7136
42 | 2684667.0875 | 1247470.9976

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98069 | -0.37108 | 0 | 0
1 | 0.98075 | -0.37008 | 0 | 0
2 | 0.98051 | -0.37477 | 0.0048152 | 0.0012068
3 | 0.98192 | -0.34711 | 0.0050643 | 0.0012692
4 | 0.982 | -0.34557 | 0.0060918 | 0.0015267
5 | 0.98423 | -0.30212 | 0.0065594 | 0.0016439
6 | 0.97896 | -0.40493 | 0.003608 | 0.00090424
7 | 0.98457 | -0.29554 | 0.0017201 | 0.00043109
8 | 0.9782 | -0.41985 | 0.0088791 | 0.0022253
9 | 0.97779 | -0.4279 | 0.011498 | 0.0028816
10 | 0.97682 | -0.44706 | 0 | 0
11 | 0.97675 | -0.44839 | 0.0043831 | 0.0010985
12 | 0.97651 | -0.4531 | 0.0089453 | 0.0022419
13 | 0.98043 | -0.37629 | 0.0040737 | 0.001021
14 | 0.9764 | -0.45525 | 0.0045622 | 0.0011434
15 | 0.97637 | -0.45592 | 0.0033025 | 0.00082769
16 | 0.98544 | -0.27883 | 0 | 0
17 | 0.98633 | -0.26145 | 0.005628 | 0.0014105
18 | 0.99838 | -0.03074 | 0.0036592 | 0.00091709
19 | 0.99838 | -0.030738 | 0.0040257 | 0.0010089
20 | 0.99732 | -0.050783 | 0 | 0
21 | 0.99944 | -0.010613 | 0.0043969 | 0.001102
22 | 0.99445 | -0.10538 | 0.0056151 | 0.0014073
23 | 0.99724 | -0.052375 | 0.0058572 | 0.001468
24 | 1 | 0 | -0.16587 | -0.041982
25 | 0.99251 | -0.14261 | 0.0056401 | 0.0014135
26 | 0.99701 | -0.056836 | 0.0030018 | 0.00075233
27 | 0.98842 | -0.2211 | 0.0043141 | 0.0010812
28 | 0.98878 | -0.21413 | 0 | 0
29 | 0.98874 | -0.21492 | 0.0014913 | 0.00037375
30 | 0.99046 | -0.18182 | 0 | 0
31 | 0.98898 | -0.21066 | 0 | 0
32 | 0.98673 | -0.25421 | 0 | 0
33 | 0.98628 | -0.26314 | 0 | 0
34 | 0.98746 | -0.24011 | 0.012159 | 0.0030474
35 | 0.99682 | -0.060401 | 0.0034256 | 0.00085852
36 | 0.99681 | -0.060571 | 0.0046583 | 0.0011675
37 | 0.98556 | -0.27699 | 0.015219 | 0.0038143
38 | 0.98583 | -0.27173 | 0 | 0
39 | 0.98618 | -0.26497 | 0.0047524 | 0.0011911
40 | 0.98779 | -0.23372 | 0 | 0
41 | 0.98896 | -0.21093 | 0.0047326 | 0.0011861
42 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0088908 | -0.0022284 | 0.0088912 | 0.0022286 | 4.2693e-07 | 1.9429e-07 | 0.01349 | 0.01349 | 0.01349 | 0.98069 | -0.37108 | 0.98075 | -0.37008 | 3.7061
1 | 0.0088908 | 0.0022284 | -0.0088892 | -0.0022277 | 1.5602e-06 | 7.1013e-07 | 0.01349 | 0.01349 | 0.01349 | 0.98069 | -0.37108 | 0.98051 | -0.37477 | 3.7061
2 | 0.045321 | 0.011412 | -0.045246 | -0.011364 | 7.5382e-05 | 4.7709e-05 | 0.068782 | 0.068782 | 0.068782 | 0.98075 | -0.37008 | 0.97896 | -0.40493 | 18.8961
3 | -0.054212 | -0.01364 | 0.054272 | 0.013678 | 5.9562e-05 | 3.7823e-05 | 0.082272 | 0.082272 | 0.082272 | 0.98075 | -0.37008 | 0.98192 | -0.34711 | 22.6021
4 | 0.004074 | 0.0010209 | -0.0040737 | -0.001021 | 2.9623e-07 | -7.1043e-08 | 0.0061826 | 0.0061827 | 0.0061827 | 0.98051 | -0.37477 | 0.98043 | -0.37629 | 1.6985
5 | -0.059336 | -0.014948 | 0.05934 | 0.01495 | 4.3613e-06 | 2.7731e-06 | 0.089946 | 0.089946 | 0.089946 | 0.98192 | -0.34711 | 0.982 | -0.34557 | 24.7104
6 | -0.065432 | -0.016477 | 0.065568 | 0.016564 | 0.00013625 | 8.673e-05 | 0.099177 | 0.099177 | 0.099177 | 0.982 | -0.34557 | 0.98423 | -0.30212 | 27.2464
7 | -0.072128 | -0.018208 | 0.072151 | 0.018222 | 2.2733e-05 | 1.4484e-05 | 0.10909 | 0.10909 | 0.10909 | 0.98423 | -0.30212 | 0.98457 | -0.29554 | 29.9707
8 | 0.041638 | 0.01046 | -0.041608 | -0.010441 | 2.9629e-05 | 1.8715e-05 | 0.063298 | 0.063298 | 0.063298 | 0.97896 | -0.40493 | 0.9782 | -0.41985 | 17.3895
9 | -0.073871 | -0.018653 | 0.07393 | 0.018691 | 5.9226e-05 | 3.7743e-05 | 0.11169 | 0.11169 | 0.11169 | 0.98457 | -0.29554 | 0.98544 | -0.27883 | 30.6849
10 | 0.032729 | 0.0082159 | -0.032716 | -0.008208 | 1.2567e-05 | 7.8734e-06 | 0.049791 | 0.049791 | 0.049791 | 0.9782 | -0.41985 | 0.97779 | -0.4279 | 13.6789
11 | 0.021219 | 0.0053264 | -0.021199 | -0.0053146 | 1.9369e-05 | 1.1776e-05 | 0.032294 | 0.032294 | 0.032294 | 0.97779 | -0.4279 | 0.97682 | -0.44706 | 8.872
12 | 0.0043834 | 0.0010985 | -0.0043831 | -0.0010985 | 2.7858e-07 | -3.0267e-08 | 0.0066773 | 0.0066773 | 0.0066773 | 0.97682 | -0.44706 | 0.97675 | -0.44839 | 1.8344
13 | 0.016816 | 0.0042161 | -0.016811 | -0.0042133 | 4.8356e-06 | 2.8489e-06 | 0.025617 | 0.025617 | 0.025617 | 0.97682 | -0.44706 | 0.97651 | -0.4531 | 7.0376
14 | 0.0078657 | 0.0019714 | -0.0078649 | -0.001971 | 8.0627e-07 | 3.288e-07 | 0.011986 | 0.011986 | 0.011986 | 0.97651 | -0.4531 | 0.9764 | -0.45525 | 3.2928
15 | 0.0033026 | 0.00082762 | -0.0033025 | -0.00082769 | 1.0603e-07 | -7.1738e-08 | 0.0050331 | 0.0050331 | 0.0050331 | 0.9764 | -0.45525 | 0.97637 | -0.45592 | 1.3827
16 | -0.07393 | -0.018691 | 0.073992 | 0.01873 | 6.1666e-05 | 3.9298e-05 | 0.11169 | 0.11169 | 0.11169 | 0.98544 | -0.27883 | 0.98633 | -0.26145 | 30.6849
17 | -0.07962 | -0.020141 | 0.079774 | 0.020239 | 0.00015447 | 9.8498e-05 | 0.12018 | 0.12018 | 0.12018 | 0.98633 | -0.26145 | 0.98842 | -0.2211 | 33.0174
18 | -0.15556 | -0.039718 | 0.15556 | 0.039718 | 1.024e-08 | 6.5534e-09 | 0.23211 | 0.23211 | 0.23211 | 0.99838 | -0.03074 | 0.99838 | -0.030738 | 31.8835
19 | 0.1519 | 0.038801 | -0.15175 | -0.038707 | 0.00014704 | 9.3708e-05 | 0.22666 | 0.22666 | 0.22666 | 0.99838 | -0.03074 | 0.99732 | -0.050783 | 31.1344
20 | -0.15959 | -0.040727 | 0.15974 | 0.040826 | 0.00015533 | 9.9026e-05 | 0.23811 | 0.23811 | 0.23811 | 0.99838 | -0.030738 | 0.99944 | -0.010613 | 32.7077
21 | 0.13481 | 0.034459 | -0.13445 | -0.034232 | 0.00035501 | 0.0002269 | 0.20137 | 0.20137 | 0.20137 | 0.99732 | -0.050783 | 0.99445 | -0.10538 | 55.3218
22 | 0.016948 | 0.0042488 | -0.016947 | -0.0042481 | 1.2856e-06 | 7.5281e-07 | 0.025287 | 0.025287 | 0.025287 | 0.99732 | -0.050783 | 0.99724 | -0.052375 | 6.947
23 | -0.16414 | -0.041928 | 0.16422 | 0.041982 | 8.4271e-05 | 5.3736e-05 | 0.24466 | 0.24466 | 0.24466 | 0.99944 | -0.010613 | 1 | 0 | 33.6069
24 | 0.12884 | 0.032824 | -0.12861 | -0.032677 | 0.00023094 | 0.00014759 | 0.19297 | 0.19297 | 0.19297 | 0.99445 | -0.10538 | 0.99251 | -0.14261 | 53.0136
25 | 0.01109 | 0.0027801 | -0.011087 | -0.0027789 | 2.3568e-06 | 1.2089e-06 | 0.016547 | 0.016547 | 0.016547 | 0.99724 | -0.052375 | 0.99701 | -0.056836 | 4.546
26 | 0.12297 | 0.031263 | -0.12273 | -0.031115 | 0.00023179 | 0.00014811 | 0.18451 | 0.18451 | 0.18451 | 0.99251 | -0.14261 | 0.99046 | -0.18182 | 50.6906
27 | 0.0080853 | 0.0020266 | -0.0080839 | -0.002026 | 1.3728e-06 | 5.5083e-07 | 0.012067 | 0.012067 | 0.012067 | 0.99701 | -0.056836 | 0.99682 | -0.060401 | 3.3152
28 | -0.084088 | -0.021321 | 0.084116 | 0.021338 | 2.8179e-05 | 1.7974e-05 | 0.12668 | 0.12668 | 0.12668 | 0.98842 | -0.2211 | 0.98878 | -0.21413 | 34.8016
29 | 0.0014913 | 0.0003734 | -0.0014913 | -0.00037375 | 5.6346e-08 | -3.4658e-07 | 0.0022442 | 0.0022443 | 0.0022443 | 0.98878 | -0.21413 | 0.98874 | -0.21492 | 0.61657
30 | -0.085608 | -0.021712 | 0.085741 | 0.021797 | 0.0001332 | 8.4974e-05 | 0.12892 | 0.12892 | 0.12892 | 0.98878 | -0.21413 | 0.99046 | -0.18182 | 35.4181
31 | 0.036993 | 0.0093183 | -0.036942 | -0.0092863 | 5.0953e-05 | 3.2045e-05 | 0.055592 | 0.055592 | 0.055592 | 0.99046 | -0.18182 | 0.98898 | -0.21066 | 15.2726
32 | 0.0047326 | 0.0011861 | -0.0047326 | -0.0011861 | 5.9211e-08 | -2.0623e-09 | 0.0071207 | 0.0071207 | 0.0071207 | 0.98898 | -0.21066 | 0.98896 | -0.21093 | 1.9562
33 | 0.032209 | 0.0081002 | -0.032174 | -0.008078 | 3.5423e-05 | 2.2155e-05 | 0.048472 | 0.048472 | 0.048472 | 0.98898 | -0.21066 | 0.98779 | -0.23372 | 13.3164
34 | 0.019991 | 0.0050163 | -0.019982 | -0.0050112 | 8.5109e-06 | 5.1282e-06 | 0.030149 | 0.030149 | 0.030149 | 0.98673 | -0.25421 | 0.98628 | -0.26314 | 8.2827
35 | -0.019991 | -0.0050163 | 0.020004 | 0.0050244 | 1.3453e-05 | 8.1055e-06 | 0.030149 | 0.030149 | 0.030149 | 0.98673 | -0.25421 | 0.98746 | -0.24011 | 8.2826
36 | 0.0047529 | 0.0011911 | -0.0047524 | -0.0011911 | 4.1335e-07 | -8.9973e-09 | 0.0071707 | 0.0071708 | 0.0071708 | 0.98628 | -0.26314 | 0.98618 | -0.26497 | 1.97
37 | 0.015229 | 0.0038201 | -0.015223 | -0.0038165 | 6.2295e-06 | 3.5855e-06 | 0.022978 | 0.022978 | 0.022978 | 0.98628 | -0.26314 | 0.98583 | -0.27173 | 6.3127
38 | -0.032164 | -0.0080719 | 0.032174 | 0.008078 | 9.8091e-06 | 6.1354e-06 | 0.048472 | 0.048472 | 0.048472 | 0.98746 | -0.24011 | 0.98779 | -0.23372 | 13.3164
39 | 0.0046584 | 0.0011675 | -0.0046583 | -0.0011675 | 3.7718e-08 | -2.9757e-09 | 0.0069538 | 0.0069538 | 0.0069538 | 0.99682 | -0.060401 | 0.99681 | -0.060571 | 1.9104
40 | -0.015219 | -0.0038143 | 0.015223 | 0.0038165 | 3.8171e-06 | 2.1972e-06 | 0.022978 | 0.022978 | 0.022978 | 0.98556 | -0.27699 | 0.98583 | -0.27173 | 6.3128

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.16714 | 0.042301

## res_load
| p_mw | q_mvar
0 | 0.0048152 | 0.0012068
1 | 0.0050643 | 0.0012692
2 | 0.0060918 | 0.0015267
3 | 0.0065594 | 0.0016439
4 | 0.003608 | 0.00090424
5 | 0.0017201 | 0.00043109
6 | 0.0088791 | 0.0022253
7 | 0.011498 | 0.0028816
8 | 0.0043831 | 0.0010985
9 | 0.0089453 | 0.0022419
10 | 0.0040737 | 0.001021
11 | 0.0045622 | 0.0011434
12 | 0.0033025 | 0.00082769
13 | 0.005628 | 0.0014105
14 | 0.0036592 | 0.00091709
15 | 0.0040257 | 0.0010089
16 | 0.0043969 | 0.001102
17 | 0.0056151 | 0.0014073
18 | 0.0058572 | 0.001468
19 | 0.0012714 | 0.00031863
20 | 0.0056401 | 0.0014135
21 | 0.0030018 | 0.00075233
22 | 0.0043141 | 0.0010812
23 | 0.0014913 | 0.00037375
24 | 0.012159 | 0.0030474
25 | 0.0034256 | 0.00085852
26 | 0.0046583 | 0.0011675
27 | 0.015219 | 0.0038143
28 | 0.0047524 | 0.0011911
29 | 0.0047326 | 0.0011861

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1