## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-290_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-290_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-290_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-290_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-290_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-290_0_4_node_11 | 0.4 | n |  | TRUE
6 | bus_LV_261-290_0_4_node_25 | 0.4 | n |  | TRUE
7 | bus_LV_261-290_0_4_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_261-290_0_4_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_261-290_0_4_node_23 | 0.4 | n |  | TRUE
10 | bus_LV_261-290_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_261-290_0_4_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_261-290_0_4_node_28 | 0.4 | n |  | TRUE
13 | bus_LV_261-290_0_4_node_31 | 0.4 | n |  | TRUE
14 | bus_LV_261-290_0_4_node_29 | 0.4 | n |  | TRUE
15 | bus_LV_261-290_0_4_node_36 | 0.4 | n |  | TRUE
16 | bus_LV_261-290_0_4_node_32 | 0.4 | n |  | TRUE
17 | bus_LV_261-290_0_4_node_24 | 0.4 | n |  | TRUE
18 | bus_LV_261-290_0_4_node_37 | 0.4 | n |  | TRUE
19 | bus_LV_261-290_0_4_node_5 | 0.4 | n |  | TRUE
20 | bus_LV_261-290_0_4_node_7 | 0.4 | n |  | TRUE
21 | bus_LV_261-290_0_4_node_9 | 0.4 | n |  | TRUE
22 | bus_LV_261-290_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_261-290_0_4_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_261-290_0_4_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_261-290_0_4_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_261-290_0_4_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_261-290_0_4_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_261-290_0_4_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_261-290_0_4_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_261-290_0_4_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_261-290_0_4_node_35 | 0.4 | n |  | TRUE
32 | bus_LV_261-290_0_4_node_38 | 0.4 | n |  | TRUE
33 | bus_LV_261-290_0_4_node_33 | 0.4 | n |  | TRUE
34 | bus_LV_261-290_0_4_node_39 | 0.4 | n |  | TRUE
35 | bus_MV_550_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-290_0_4_load_0 | 0 | 0.013037 | 0.0032674 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-290_0_4_load_1 | 1 | 0.012824 | 0.003214 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-290_0_4_load_2 | 2 | 0.01441 | 0.0036114 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-290_0_4_load_11 | 5 | 0.0090901 | 0.0022782 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-290_0_4_load_25 | 6 | 0.0086973 | 0.0021798 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-290_0_4_load_12 | 8 | 0.014067 | 0.0035254 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-290_0_4_load_23 | 9 | 0.010067 | 0.0025231 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-290_0_4_load_6 | 10 | 0.010708 | 0.0026836 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-290_0_4_load_10 | 11 | 0.0092506 | 0.0023184 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-290_0_4_load_36 | 15 | 0.037507 | 0.0094001 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-290_0_4_load_32 | 16 | 0.006974 | 0.0017478 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-290_0_4_load_37 | 18 | 0.00089445 | 0.00022417 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-290_0_4_load_5 | 19 | 0.017942 | 0.0044967 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-290_0_4_load_9 | 21 | 0.019818 | 0.0049668 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-290_0_4_load_13 | 22 | 0.010587 | 0.0026534 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-290_0_4_load_21 | 23 | 0.0095547 | 0.0023946 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-290_0_4_load_14 | 24 | 0.015048 | 0.0037713 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-290_0_4_load_15 | 25 | 0.0073662 | 0.0018461 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-290_0_4_load_20 | 26 | 0.01088 | 0.0027269 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-290_0_4_load_18 | 27 | 0.0069565 | 0.0017435 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-290_0_4_load_16 | 28 | 0.0085971 | 0.0021546 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-290_0_4_load_17 | 29 | 0.010374 | 0.0025999 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-290_0_4_load_22 | 30 | 0.046082 | 0.011549 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-290_0_4_load_35 | 31 | 0.065314 | 0.016369 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-290_0_4_load_38 | 32 | 0.042264 | 0.010592 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-290_0_4_load_33 | 33 | 0.0072205 | 0.0018096 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-290_0_4_load_39 | 34 | 0.054382 | 0.01363 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 21 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-290_0_4_line_0 |  | 0 | 1 | 0.019648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-290_0_4_line_1 |  | 0 | 2 | 0.0082905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-290_0_4_line_2 |  | 1 | 3 | 0.031597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-290_0_4_line_3 |  | 2 | 4 | 0.0069149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-290_0_4_line_4 |  | 3 | 5 | 0.020227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-290_0_4_line_5 |  | 4 | 6 | 0.010448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-290_0_4_line_6 |  | 5 | 11 | 0.02292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-290_0_4_line_7 |  | 7 | 8 | 0.015068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-290_0_4_line_8 |  | 7 | 9 | 0.034556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_261-290_0_4_line_9 |  | 7 | 10 | 0.027777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_261-290_0_4_line_10 |  | 8 | 11 | 0.033639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-290_0_4_line_11 |  | 9 | 23 | 0.025149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_261-290_0_4_line_12 |  | 10 | 19 | 0.0089388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_261-290_0_4_line_13 |  | 12 | 13 | 0.011221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-290_0_4_line_14 |  | 12 | 14 | 0.03153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-290_0_4_line_15 |  | 12 | 15 | 0.012147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-290_0_4_line_16 |  | 13 | 18 | 0.02824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-290_0_4_line_17 |  | 14 | 16 | 0.029915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-290_0_4_line_18 |  | 14 | 17 | 0.008632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-290_0_4_line_19 |  | 16 | 33 | 0.010802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-290_0_4_line_20 |  | 17 | 31 | 0.023051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_261-290_0_4_line_21 |  | 17 | 30 | 0.017038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_261-290_0_4_line_22 |  | 19 | 20 | 0.0066818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_261-290_0_4_line_23 |  | 20 | 21 | 0.020906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_261-290_0_4_line_24 |  | 21 | 22 | 0.016883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-290_0_4_line_25 |  | 22 | 24 | 0.0046085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-290_0_4_line_26 |  | 23 | 30 | 0.02262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_261-290_0_4_line_27 |  | 24 | 25 | 0.016953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-290_0_4_line_28 |  | 25 | 26 | 0.0036611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-290_0_4_line_29 |  | 26 | 27 | 0.017747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-290_0_4_line_30 |  | 27 | 28 | 0.00050151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-290_0_4_line_31 |  | 28 | 29 | 0.0012481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-290_0_4_line_32 |  | 31 | 32 | 0.0027311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-290_0_4_line_33 |  | 32 | 34 | 0.013367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-290_0_4_trafo_9 | 0.63 MVA 20/0.4 kV | 35 | 21 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2684334.757 | 1248114.7156 | 2684352.877 | 1248107.118
1 | 2684334.757 | 1248114.7156 | 2684329.3431 | 1248116.9856 | 2684327.7388 | 1248118.7974
2 | 2684382.9359 | 1248097.4779 | 2684358.839 | 1248104.6182 | 2684352.877 | 1248107.118
3 | 2684326.0874 | 1248125.5123 | 2684327.7388 | 1248118.7974
4 | 2684382.9359 | 1248097.4779 | 2684382.3069 | 1248077.2605
5 | 2684326.0874 | 1248125.5123 | 2684316.9225 | 1248130.528
6 | 2684378.5437 | 1248054.7774 | 2684382.0395 | 1248068.6661 | 2684382.3069 | 1248077.2605
7 | 2684349.7688 | 1248017.0243 | 2684360.3302 | 1248027.7721
8 | 2684349.7688 | 1248017.0243 | 2684323.4683 | 1247994.6106
9 | 2684349.7688 | 1248017.0243 | 2684322.5411 | 1248022.5226
10 | 2684378.5437 | 1248054.7774 | 2684375.6774 | 1248043.3902 | 2684360.3302 | 1248027.7721
11 | 2684323.4683 | 1247994.6106 | 2684304.327 | 1247978.298
12 | 2684313.7792 | 1248024.292 | 2684322.5411 | 1248022.5226
13 | 2684246.7159 | 1247924.6799 | 2684254.2256 | 1247933.0372
14 | 2684254.2256 | 1247933.0372 | 2684253.2632 | 1247933.257 | 2684253.476 | 1247934.2274 | 2684254.7188 | 1247939.7825 | 2684255.4004 | 1247942.8389 | 2684270.7305 | 1247939.2986 | 2684271.8547 | 1247944.1626
15 | 2684254.2256 | 1247933.0372 | 2684266.068 | 1247930.3341
16 | 2684246.7159 | 1247924.6799 | 2684244.2974 | 1247923.7226 | 2684238.2811 | 1247917.11 | 2684233.2773 | 1247909.3999 | 2684229.9971 | 1247902.6468
17 | 2684271.8547 | 1247944.1626 | 2684280.3554 | 1247942.3154 | 2684292.7033 | 1247937.6207 | 2684299.9283 | 1247934.1733
18 | 2684274.2443 | 1247952.4582 | 2684271.8547 | 1247944.1626
19 | 2684309.647 | 1247929.4611 | 2684308.4981 | 1247930.0841 | 2684299.9283 | 1247934.1733
20 | 2684274.2443 | 1247952.4582 | 2684268.2239 | 1247962.0687 | 2684264.6337 | 1247970.2126 | 2684262.8151 | 1247972.3548
21 | 2684274.2443 | 1247952.4582 | 2684287.1293 | 1247963.6052
22 | 2684307.2296 | 1248025.6146 | 2684313.7792 | 1248024.292
23 | 2684307.2296 | 1248025.6146 | 2684304.9419 | 1248026.0824 | 2684295.75 | 1248029.2763 | 2684287.8683 | 1248033.2784
24 | 2684287.8683 | 1248033.2784 | 2684287.8683 | 1248033.2784 | 2684275.9929 | 1248040.8708 | 2684273.9934 | 1248042.8135
25 | 2684273.9934 | 1248042.8135 | 2684270.688 | 1248046.025
26 | 2684287.1293 | 1247963.6052 | 2684289.9649 | 1247966.0584 | 2684304.327 | 1247978.298
27 | 2684260.0888 | 1248059.1877 | 2684267.0935 | 1248049.5174 | 2684270.688 | 1248046.025
28 | 2684260.0888 | 1248059.1877 | 2684257.9411 | 1248062.1527
29 | 2684247.5301 | 1248076.5255 | 2684257.9411 | 1248062.1527
30 | 2684247.2359 | 1248076.9316 | 2684247.5301 | 1248076.5255
31 | 2684246.5037 | 1248077.9424 | 2684247.2359 | 1248076.9316
32 | 2684261.0476 | 1247974.4369 | 2684262.8151 | 1247972.3548
33 | 2684252.3969 | 1247984.6272 | 2684261.0476 | 1247974.4369

## bus_geodata
| x | y | coords
0 | 2684334.757 | 1248114.7156
1 | 2684352.877 | 1248107.118
2 | 2684327.7388 | 1248118.7974
3 | 2684382.9359 | 1248097.4779
4 | 2684326.0874 | 1248125.5123
5 | 2684382.3069 | 1248077.2605
6 | 2684316.9225 | 1248130.528
7 | 2684349.7688 | 1248017.0243
8 | 2684360.3302 | 1248027.7721
9 | 2684323.4683 | 1247994.6106
10 | 2684322.5411 | 1248022.5226
11 | 2684378.5437 | 1248054.7774
12 | 2684254.2256 | 1247933.0372
13 | 2684246.7159 | 1247924.6799
14 | 2684271.8547 | 1247944.1626
15 | 2684266.068 | 1247930.3341
16 | 2684299.9283 | 1247934.1733
17 | 2684274.2443 | 1247952.4582
18 | 2684229.9971 | 1247902.6468
19 | 2684313.7792 | 1248024.292
20 | 2684307.2296 | 1248025.6146
21 | 2684287.8683 | 1248033.2784
22 | 2684273.9934 | 1248042.8135
23 | 2684304.327 | 1247978.298
24 | 2684270.688 | 1248046.025
25 | 2684260.0888 | 1248059.1877
26 | 2684257.9411 | 1248062.1527
27 | 2684247.5301 | 1248076.5254
28 | 2684247.2359 | 1248076.9316
29 | 2684246.5037 | 1248077.9424
30 | 2684287.1293 | 1247963.6052
31 | 2684262.8151 | 1247972.3548
32 | 2684261.0476 | 1247974.4369
33 | 2684309.647 | 1247929.4611
34 | 2684252.3969 | 1247984.6272
35 | 2684307.2296 | 1248025.6146

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98516 | -0.28514 | 0.013037 | 0.0032674
1 | 0.98581 | -0.2724 | 0.012824 | 0.003214
2 | 0.98498 | -0.28858 | 0.01441 | 0.0036114
3 | 0.98723 | -0.24469 | 0 | 0
4 | 0.98493 | -0.28966 | 0 | 0
5 | 0.98815 | -0.22699 | 0.0090901 | 0.0022782
6 | 0.98484 | -0.2913 | 0.0086973 | 0.0021798
7 | 0.99258 | -0.14131 | 0 | 0
8 | 0.99145 | -0.16303 | 0.014067 | 0.0035254
9 | 0.9896 | -0.19859 | 0.010067 | 0.0025231
10 | 0.99567 | -0.082252 | 0.010708 | 0.0026836
11 | 0.98937 | -0.20326 | 0.0092506 | 0.0023184
12 | 0.98247 | -0.33704 | 0 | 0
13 | 0.98246 | -0.33723 | 0 | 0
14 | 0.98359 | -0.3152 | 0 | 0
15 | 0.98205 | -0.34527 | 0.037507 | 0.0094001
16 | 0.9832 | -0.32286 | 0.006974 | 0.0017478
17 | 0.98401 | -0.30703 | 0 | 0
18 | 0.98244 | -0.33768 | 0.00089445 | 0.00022417
19 | 0.99669 | -0.062766 | 0.017942 | 0.0044967
20 | 0.99749 | -0.047525 | 0 | 0
21 | 1 | 0 | -0.46735 | -0.11889
22 | 0.99893 | -0.020564 | 0.010587 | 0.0026534
23 | 0.98751 | -0.23899 | 0.0095547 | 0.0023946
24 | 0.99868 | -0.025333 | 0.015048 | 0.0037713
25 | 0.998 | -0.038429 | 0.0073662 | 0.0018461
26 | 0.99788 | -0.040787 | 0.01088 | 0.0027269
27 | 0.99746 | -0.048845 | 0.0069565 | 0.0017435
28 | 0.99745 | -0.049011 | 0.0085971 | 0.0021546
29 | 0.99744 | -0.049238 | 0.010374 | 0.0025999
30 | 0.9857 | -0.27418 | 0.046082 | 0.011549
31 | 0.98228 | -0.34069 | 0.065314 | 0.016369
32 | 0.98204 | -0.34546 | 0.042264 | 0.010592
33 | 0.98313 | -0.32426 | 0.0072205 | 0.0018096
34 | 0.98137 | -0.3586 | 0.054382 | 0.01363
35 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.036149 | -0.0090614 | 0.036171 | 0.0090752 | 2.1967e-05 | 1.3808e-05 | 0.054601 | 0.054601 | 0.054601 | 0.98516 | -0.28514 | 0.98581 | -0.2724 | 15.0004
1 | 0.023112 | 0.005794 | -0.023108 | -0.0057917 | 3.7888e-06 | 2.3193e-06 | 0.03491 | 0.03491 | 0.03491 | 0.98516 | -0.28514 | 0.98498 | -0.28858 | 9.5906
2 | -0.048995 | -0.012289 | 0.04906 | 0.01233 | 6.4812e-05 | 4.1076e-05 | 0.073958 | 0.073958 | 0.073958 | 0.98581 | -0.2724 | 0.98723 | -0.24469 | 20.3182
3 | 0.0086984 | 0.0021803 | -0.008698 | -0.0021801 | 4.4778e-07 | 1.9857e-07 | 0.013141 | 0.013141 | 0.013141 | 0.98498 | -0.28858 | 0.98493 | -0.28966 | 3.6101
4 | -0.04906 | -0.01233 | 0.049101 | 0.012357 | 4.149e-05 | 2.6294e-05 | 0.073958 | 0.073958 | 0.073958 | 0.98723 | -0.24469 | 0.98815 | -0.22699 | 20.3182
5 | 0.008698 | 0.0021801 | -0.0086973 | -0.0021798 | 6.7655e-07 | 3.0004e-07 | 0.013141 | 0.013141 | 0.013141 | 0.98493 | -0.28966 | 0.98484 | -0.2913 | 3.6101
6 | -0.058191 | -0.014635 | 0.058257 | 0.014677 | 6.6027e-05 | 4.1964e-05 | 0.087647 | 0.087646 | 0.087647 | 0.98815 | -0.22699 | 0.98937 | -0.20326 | 24.0787
7 | 0.08179 | 0.020658 | -0.081705 | -0.020603 | 8.5032e-05 | 5.4226e-05 | 0.12267 | 0.12267 | 0.12267 | 0.99258 | -0.14131 | 0.99145 | -0.16303 | 33.7008
8 | 0.28274 | 0.07182 | -0.28196 | -0.071324 | 0.00077729 | 0.00049613 | 0.42421 | 0.42421 | 0.42421 | 0.99258 | -0.14131 | 0.9896 | -0.19859 | 38.8467
9 | -0.36453 | -0.092478 | 0.36557 | 0.093141 | 0.0010384 | 0.00066352 | 0.54688 | 0.54688 | 0.54688 | 0.99258 | -0.14131 | 0.99567 | -0.082252 | 50.0803
10 | 0.067638 | 0.017078 | -0.067508 | -0.016995 | 0.00013011 | 8.2838e-05 | 0.10156 | 0.10156 | 0.10156 | 0.99145 | -0.16303 | 0.98937 | -0.20326 | 27.9009
11 | 0.27189 | 0.068801 | -0.27137 | -0.068465 | 0.00052605 | 0.00033571 | 0.40907 | 0.40907 | 0.40907 | 0.9896 | -0.19859 | 0.98751 | -0.23899 | 37.4605
12 | -0.37627 | -0.095825 | 0.37663 | 0.096051 | 0.00035401 | 0.00022622 | 0.56288 | 0.56288 | 0.56288 | 0.99567 | -0.082252 | 0.99669 | -0.062766 | 51.5456
13 | 0.00089448 | 0.00022369 | -0.00089447 | -0.00022383 | 7.7212e-09 | -1.3715e-07 | 0.0013546 | 0.0013546 | 0.0013546 | 0.98247 | -0.33704 | 0.98246 | -0.33723 | 0.37215
14 | -0.038416 | -0.009633 | 0.038456 | 0.0096583 | 4.003e-05 | 2.5219e-05 | 0.058185 | 0.058185 | 0.058185 | 0.98247 | -0.33704 | 0.98359 | -0.3152 | 15.985
15 | 0.037522 | 0.0094094 | -0.037507 | -0.0094001 | 1.4712e-05 | 9.2618e-06 | 0.056831 | 0.056831 | 0.056831 | 0.98247 | -0.33704 | 0.98205 | -0.34527 | 15.6129
16 | 0.00089447 | 0.00022383 | -0.00089445 | -0.00022417 | 1.9435e-08 | -3.4516e-07 | 0.0013546 | 0.0013547 | 0.0013547 | 0.98246 | -0.33723 | 0.98244 | -0.33768 | 0.37218
17 | 0.0142 | 0.0035606 | -0.014195 | -0.0035576 | 5.1774e-06 | 2.934e-06 | 0.021483 | 0.021483 | 0.021483 | 0.98359 | -0.3152 | 0.9832 | -0.32286 | 5.902
18 | -0.052656 | -0.013219 | 0.052677 | 0.013232 | 2.0545e-05 | 1.3039e-05 | 0.079668 | 0.079668 | 0.079668 | 0.98359 | -0.3152 | 0.98401 | -0.30703 | 21.8869
19 | 0.0072209 | 0.0018098 | -0.0072205 | -0.0018096 | 4.8381e-07 | 1.7265e-07 | 0.010929 | 0.010929 | 0.010929 | 0.9832 | -0.32286 | 0.98313 | -0.32426 | 3.0024
20 | 0.16228 | 0.040793 | -0.16202 | -0.040627 | 0.00026036 | 0.00016604 | 0.24544 | 0.24544 | 0.24544 | 0.98401 | -0.30703 | 0.98228 | -0.34069 | 33.714
21 | -0.21495 | -0.054025 | 0.21529 | 0.05424 | 0.00033764 | 0.00021566 | 0.32511 | 0.32511 | 0.32511 | 0.98401 | -0.30703 | 0.9857 | -0.27418 | 44.6574
22 | -0.39457 | -0.10055 | 0.39486 | 0.10073 | 0.00029041 | 0.0001856 | 0.58966 | 0.58966 | 0.58966 | 0.99669 | -0.062766 | 0.99749 | -0.047525 | 53.9986
23 | -0.39486 | -0.10073 | 0.39577 | 0.10131 | 0.00090862 | 0.0005807 | 0.58966 | 0.58966 | 0.58966 | 0.99749 | -0.047525 | 1 | 0 | 53.9986
24 | 0.069933 | 0.017574 | -0.069864 | -0.017531 | 6.8579e-05 | 4.3669e-05 | 0.10408 | 0.10408 | 0.10408 | 1 | 0 | 0.99893 | -0.020564 | 28.5927
25 | 0.059277 | 0.014877 | -0.059263 | -0.014869 | 1.3477e-05 | 8.5647e-06 | 0.088307 | 0.088307 | 0.088307 | 0.99893 | -0.020564 | 0.99868 | -0.025333 | 24.2601
26 | 0.26181 | 0.06607 | -0.26137 | -0.065789 | 0.00044042 | 0.000281 | 0.39467 | 0.39467 | 0.39467 | 0.98751 | -0.23899 | 0.9857 | -0.27418 | 36.1421
27 | 0.044216 | 0.011097 | -0.044188 | -0.01108 | 2.7597e-05 | 1.744e-05 | 0.065886 | 0.065886 | 0.065886 | 0.99868 | -0.025333 | 0.998 | -0.038429 | 18.1006
28 | 0.036822 | 0.0092337 | -0.036818 | -0.0092311 | 4.1385e-06 | 2.6008e-06 | 0.054903 | 0.054903 | 0.054903 | 0.998 | -0.038429 | 0.99788 | -0.040787 | 15.0833
29 | 0.025938 | 0.0065043 | -0.025928 | -0.0064981 | 9.9566e-06 | 6.1405e-06 | 0.038679 | 0.038679 | 0.038679 | 0.99788 | -0.040787 | 0.99746 | -0.048845 | 10.6261
30 | 0.018971 | 0.0047547 | -0.018971 | -0.0047546 | 1.5063e-07 | 8.9858e-08 | 0.028301 | 0.028301 | 0.028301 | 0.99746 | -0.048845 | 0.99745 | -0.049011 | 7.775
31 | 0.010374 | 0.0026 | -0.010374 | -0.0025999 | 1.121e-07 | 5.5452e-08 | 0.015476 | 0.015476 | 0.015476 | 0.99745 | -0.049011 | 0.99744 | -0.049238 | 4.2516
32 | 0.096702 | 0.024258 | -0.09668 | -0.024243 | 2.198e-05 | 1.4033e-05 | 0.1465 | 0.1465 | 0.1465 | 0.98228 | -0.34069 | 0.98204 | -0.34546 | 40.2466
33 | 0.054417 | 0.013651 | -0.054382 | -0.01363 | 3.4083e-05 | 2.1644e-05 | 0.082458 | 0.082458 | 0.082458 | 0.98204 | -0.34546 | 0.98137 | -0.3586 | 22.6534

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.48717 | 0.12386

## res_load
| p_mw | q_mvar
0 | 0.013037 | 0.0032674
1 | 0.012824 | 0.003214
2 | 0.01441 | 0.0036114
3 | 0.0090901 | 0.0022782
4 | 0.0086973 | 0.0021798
5 | 0.014067 | 0.0035254
6 | 0.010067 | 0.0025231
7 | 0.010708 | 0.0026836
8 | 0.0092506 | 0.0023184
9 | 0.037507 | 0.0094001
10 | 0.006974 | 0.0017478
11 | 0.00089445 | 0.00022417
12 | 0.017942 | 0.0044967
13 | 0.019818 | 0.0049668
14 | 0.010587 | 0.0026534
15 | 0.0095547 | 0.0023946
16 | 0.015048 | 0.0037713
17 | 0.0073662 | 0.0018461
18 | 0.01088 | 0.0027269
19 | 0.0069565 | 0.0017435
20 | 0.0085971 | 0.0021546
21 | 0.010374 | 0.0025999
22 | 0.046082 | 0.011549
23 | 0.065314 | 0.016369
24 | 0.042264 | 0.010592
25 | 0.0072205 | 0.0018096
26 | 0.054382 | 0.01363

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1