## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-304_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-304_0_3_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_261-304_0_3_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_261-304_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-304_0_3_node_22 | 0.4 | n |  | TRUE
5 | bus_LV_261-304_0_3_node_21 | 0.4 | n |  | TRUE
6 | bus_LV_261-304_0_3_node_28 | 0.4 | n |  | TRUE
7 | bus_LV_261-304_0_3_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_261-304_0_3_node_15 | 0.4 | n |  | TRUE
9 | bus_LV_261-304_0_3_node_25 | 0.4 | n |  | TRUE
10 | bus_LV_261-304_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_261-304_0_3_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_261-304_0_3_node_16 | 0.4 | n |  | TRUE
13 | bus_LV_261-304_0_3_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_261-304_0_3_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_261-304_0_3_node_33 | 0.4 | n |  | TRUE
16 | bus_LV_261-304_0_3_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_261-304_0_3_node_32 | 0.4 | n |  | TRUE
18 | bus_LV_261-304_0_3_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_261-304_0_3_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_261-304_0_3_node_23 | 0.4 | n |  | TRUE
21 | bus_LV_261-304_0_3_node_31 | 0.4 | n |  | TRUE
22 | bus_LV_261-304_0_3_node_24 | 0.4 | n |  | TRUE
23 | bus_LV_261-304_0_3_node_29 | 0.4 | n |  | TRUE
24 | bus_LV_261-304_0_3_node_27 | 0.4 | n |  | TRUE
25 | bus_LV_261-304_0_3_node_26 | 0.4 | n |  | TRUE
26 | bus_LV_261-304_0_3_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_261-304_0_3_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_261-304_0_3_node_30 | 0.4 | n |  | TRUE
29 | bus_MV_528_0_node_12 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-304_0_3_load_0 | 0 | 0.012328 | 0.0030897 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-304_0_3_load_21 | 5 | 0.012721 | 0.0031881 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-304_0_3_load_28 | 6 | 0.021288 | 0.0053353 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-304_0_3_load_25 | 9 | 0.010913 | 0.0027351 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-304_0_3_load_18 | 13 | 0.021486 | 0.0053848 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-304_0_3_load_33 | 15 | 0.043551 | 0.010915 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-304_0_3_load_32 | 17 | 0.037947 | 0.0095104 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-304_0_3_load_23 | 20 | 0.047328 | 0.011861 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-304_0_3_load_31 | 21 | 0.01921 | 0.0048145 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-304_0_3_load_24 | 22 | 0.082779 | 0.020746 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-304_0_3_load_29 | 23 | 0.044737 | 0.011212 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-304_0_3_load_27 | 24 | 0.020966 | 0.0052547 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-304_0_3_load_26 | 25 | 0.0015315 | 0.00038384 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-304_0_3_load_19 | 26 | 0.020955 | 0.0052519 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-304_0_3_load_20 | 27 | 0.020968 | 0.005255 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-304_0_3_load_30 | 28 | 0.0011875 | 0.00029761 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 26 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-304_0_3_line_0 |  | 0 | 1 | 0.0082617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-304_0_3_line_1 |  | 1 | 2 | 0.10222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-304_0_3_line_2 |  | 2 | 6 | 0.018833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-304_0_3_line_3 |  | 2 | 3 | 0.087132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-304_0_3_line_4 |  | 3 | 4 | 0.060997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-304_0_3_line_5 |  | 3 | 5 | 0.011311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-304_0_3_line_6 |  | 4 | 23 | 0.0026126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-304_0_3_line_7 |  | 6 | 24 | 0.020143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-304_0_3_line_8 |  | 7 | 8 | 0.072059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-304_0_3_line_9 |  | 7 | 9 | 0.013161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-304_0_3_line_10 |  | 8 | 19 | 0.089747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-304_0_3_line_11 |  | 8 | 21 | 0.01749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-304_0_3_line_12 |  | 9 | 25 | 0.0031792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-304_0_3_line_13 |  | 10 | 11 | 0.040288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-304_0_3_line_14 |  | 10 | 12 | 0.020588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_261-304_0_3_line_15 |  | 10 | 13 | 0.016491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_261-304_0_3_line_16 |  | 11 | 17 | 0.035417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-304_0_3_line_17 |  | 12 | 22 | 0.029268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_261-304_0_3_line_18 |  | 13 | 26 | 0.020239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_261-304_0_3_line_19 |  | 14 | 15 | 0.044911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-304_0_3_line_20 |  | 14 | 16 | 0.27565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-304_0_3_line_21 |  | 16 | 17 | 0.023961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-304_0_3_line_22 |  | 18 | 19 | 0.08809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-304_0_3_line_23 |  | 18 | 20 | 0.027961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-304_0_3_line_24 |  | 19 | 22 | 0.028388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-304_0_3_line_25 |  | 23 | 28 | 0.032463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-304_0_3_line_26 |  | 24 | 27 | 0.019991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-304_0_3_line_27 |  | 26 | 27 | 0.019991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-304_0_3_trafo_19 | 0.63 MVA 20/0.4 kV | 29 | 26 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2683173.4122 | 1251729.5774 | 2683176.1851 | 1251725.0797 | 2683177.6899 | 1251722.5099
1 | 2683173.4122 | 1251729.5774 | 2683215.9612 | 1251755.8722 | 2683200.6163 | 1251782.1764 | 2683195.4833 | 1251787.5751 | 2683192.1749 | 1251794.1892 | 2683193.0827 | 1251801.0292
2 | 2683193.0827 | 1251801.0292 | 2683188.7746 | 1251808.4187 | 2683183.6029 | 1251817.303
3 | 2683117.4241 | 1251757.8131 | 2683142.2723 | 1251771.7943 | 2683151.4895 | 1251777.0943 | 2683170.9796 | 1251788.3095 | 2683193.0827 | 1251801.0292
4 | 2683064.4727 | 1251727.2589 | 2683117.4241 | 1251757.8131
5 | 2683117.4241 | 1251757.8131 | 2683116.8202 | 1251746.5184
6 | 2683064.4727 | 1251727.2589 | 2683062.2054 | 1251725.9607
7 | 2683183.6029 | 1251817.303 | 2683173.4694 | 1251834.7108
8 | 2682950.8876 | 1251792.539 | 2682957.486 | 1251793.521 | 2682964.9204 | 1251794.6259 | 2682965.5693 | 1251797.337 | 2682967.016 | 1251799.6701 | 2682973.951 | 1251804.0928 | 2682972.6364 | 1251812.8031 | 2682971.0569 | 1251823.1776 | 2682984.527 | 1251825.012 | 2682994.2922 | 1251830.5307
9 | 2682950.8876 | 1251792.539 | 2682948.8815 | 1251805.546
10 | 2683072.9365 | 1251873.9762 | 2683057.0936 | 1251864.2802 | 2683019.9469 | 1251842.9771 | 2683005.2033 | 1251836.6881 | 2682994.2922 | 1251830.5307
11 | 2682994.2922 | 1251830.5307 | 2682985.2376 | 1251845.4947
12 | 2682948.8815 | 1251805.546 | 2682948.4302 | 1251808.4721 | 2682948.3968 | 1251808.6881
13 | 2683134.8802 | 1251901.0095 | 2683136.1901 | 1251901.7952 | 2683169.4766 | 1251921.6549
14 | 2683122.2582 | 1251903.8346 | 2683131.7351 | 1251908.9047 | 2683134.5914 | 1251904.3747 | 2683133.3489 | 1251903.6345 | 2683134.8802 | 1251901.0095
15 | 2683134.8802 | 1251901.0095 | 2683135.9477 | 1251899.1676 | 2683143.1732 | 1251886.7551
16 | 2683169.4766 | 1251921.6549 | 2683200.2172 | 1251939.2448
17 | 2683122.2582 | 1251903.8346 | 2683097.2132 | 1251888.6902
18 | 2683143.1732 | 1251886.7551 | 2683153.3553 | 1251869.2639
19 | 2683311.7061 | 1251882.1342 | 2683306.2001 | 1251893.6543 | 2683278.1409 | 1251877.8147
20 | 2683221.0141 | 1251951.1449 | 2683219.0307 | 1251954.7865 | 2683225.6699 | 1251958.7493 | 2683229.6444 | 1252040.0661 | 2683237.4986 | 1252039.7428 | 2683235.1868 | 1252034.5286 | 2683233.6955 | 1252017.6617 | 2683231.4277 | 1251976.0209 | 2683232.808 | 1251958.9052 | 2683235.208 | 1251952.4786 | 2683278.1409 | 1251877.8147
21 | 2683221.0141 | 1251951.1449 | 2683200.2172 | 1251939.2448
22 | 2683028.3191 | 1251949.9967 | 2683072.9365 | 1251873.9762
23 | 2683028.3191 | 1251949.9967 | 2683052.2371 | 1251964.4801
24 | 2683072.9365 | 1251873.9762 | 2683077.3968 | 1251876.7074 | 2683097.2132 | 1251888.6902
25 | 2683034.034 | 1251709.8304 | 2683062.2054 | 1251725.9607
26 | 2683163.4123 | 1251851.9874 | 2683173.4694 | 1251834.7108
27 | 2683163.4123 | 1251851.9874 | 2683153.3553 | 1251869.2639

## bus_geodata
| x | y | coords
0 | 2683177.6899 | 1251722.5099
1 | 2683173.4122 | 1251729.5774
2 | 2683193.0827 | 1251801.0292
3 | 2683117.4241 | 1251757.8131
4 | 2683064.4727 | 1251727.2589
5 | 2683116.8202 | 1251746.5184
6 | 2683183.6029 | 1251817.303
7 | 2682950.8876 | 1251792.539
8 | 2682994.2922 | 1251830.5307
9 | 2682948.8815 | 1251805.546
10 | 2683134.8802 | 1251901.0095
11 | 2683169.4766 | 1251921.6549
12 | 2683122.2582 | 1251903.8346
13 | 2683143.1732 | 1251886.7551
14 | 2683278.1409 | 1251877.8147
15 | 2683311.7061 | 1251882.1342
16 | 2683221.0141 | 1251951.1449
17 | 2683200.2172 | 1251939.2448
18 | 2683028.3191 | 1251949.9967
19 | 2683072.9365 | 1251873.9762
20 | 2683052.2371 | 1251964.4801
21 | 2682985.2376 | 1251845.4947
22 | 2683097.2132 | 1251888.6902
23 | 2683062.2054 | 1251725.9607
24 | 2683173.4694 | 1251834.7108
25 | 2682948.3968 | 1251808.6881
26 | 2683153.3553 | 1251869.2639
27 | 2683163.4123 | 1251851.9874
28 | 2683034.034 | 1251709.8304
29 | 2683134.8802 | 1251901.0095

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99129 | -0.16711 | 0.012328 | 0.0030897
1 | 0.99138 | -0.1653 | 0 | 0
2 | 0.99253 | -0.14298 | 0 | 0
3 | 0.98783 | -0.23382 | 0 | 0
4 | 0.98525 | -0.28399 | 0 | 0
5 | 0.9877 | -0.23639 | 0.012721 | 0.0031881
6 | 0.99376 | -0.11935 | 0.021288 | 0.0053353
7 | 0.9865 | -0.2597 | 0 | 0
8 | 0.98732 | -0.24365 | 0 | 0
9 | 0.98635 | -0.26263 | 0.010913 | 0.0027351
10 | 0.99569 | -0.082018 | 0 | 0
11 | 0.99266 | -0.13993 | 0 | 0
12 | 0.99417 | -0.11134 | 0 | 0
13 | 0.99754 | -0.046815 | 0.021486 | 0.0053848
14 | 0.97786 | -0.42609 | 0 | 0
15 | 0.97605 | -0.46181 | 0.043551 | 0.010915
16 | 0.98902 | -0.20971 | 0 | 0
17 | 0.98999 | -0.19113 | 0.037947 | 0.0095104
18 | 0.98609 | -0.26742 | 0 | 0
19 | 0.98993 | -0.19298 | 0 | 0
20 | 0.98487 | -0.29117 | 0.047328 | 0.011861
21 | 0.98701 | -0.24966 | 0.01921 | 0.0048145
22 | 0.99199 | -0.15318 | 0.082779 | 0.020746
23 | 0.98514 | -0.28615 | 0.044737 | 0.011212
24 | 0.99547 | -0.086609 | 0.020966 | 0.0052547
25 | 0.98634 | -0.26272 | 0.0015315 | 0.00038384
26 | 1 | 0 | -0.40477 | -0.10264
27 | 0.99754 | -0.046876 | 0.020968 | 0.005255
28 | 0.98511 | -0.28684 | 0.0011875 | 0.00029761
29 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.012328 | -0.0030897 | 0.012329 | 0.0030903 | 1.061e-06 | 5.725e-07 | 0.018505 | 0.018505 | 0.018505 | 0.99129 | -0.16711 | 0.99138 | -0.1653 | 5.0839
1 | -0.012329 | -0.0030903 | 0.012342 | 0.0030973 | 1.3126e-05 | 7.0812e-06 | 0.018505 | 0.018505 | 0.018505 | 0.99138 | -0.1653 | 0.99253 | -0.14298 | 5.0839
2 | -0.07136 | -0.018031 | 0.071441 | 0.018083 | 8.0913e-05 | 5.1541e-05 | 0.10704 | 0.10704 | 0.10704 | 0.99253 | -0.14298 | 0.99376 | -0.11935 | 29.4054
3 | 0.059018 | 0.014934 | -0.058762 | -0.014771 | 0.00025609 | 0.00016278 | 0.088531 | 0.088531 | 0.088531 | 0.99253 | -0.14298 | 0.98783 | -0.23382 | 24.3217
4 | 0.046039 | 0.011582 | -0.045929 | -0.011512 | 0.00011006 | 6.9662e-05 | 0.069367 | 0.069367 | 0.069367 | 0.98783 | -0.23382 | 0.98525 | -0.28399 | 19.0568
5 | 0.012722 | 0.003189 | -0.012721 | -0.0031881 | 1.5578e-06 | 8.5224e-07 | 0.019165 | 0.019165 | 0.019165 | 0.98783 | -0.23382 | 0.9877 | -0.23639 | 5.265
6 | 0.045929 | 0.011512 | -0.045925 | -0.011509 | 4.7142e-06 | 2.9838e-06 | 0.069367 | 0.069367 | 0.069367 | 0.98525 | -0.28399 | 0.98514 | -0.28615 | 19.0568
7 | -0.092729 | -0.023418 | 0.092875 | 0.023511 | 0.00014575 | 9.3021e-05 | 0.13891 | 0.13891 | 0.13891 | 0.99376 | -0.11935 | 0.99547 | -0.086609 | 38.1624
8 | -0.012446 | -0.0031198 | 0.012456 | 0.003125 | 9.5242e-06 | 5.1747e-06 | 0.018774 | 0.018774 | 0.018774 | 0.9865 | -0.2597 | 0.98732 | -0.24365 | 5.1577
9 | 0.012446 | 0.0031198 | -0.012445 | -0.0031189 | 1.7395e-06 | 9.4529e-07 | 0.018774 | 0.018774 | 0.018774 | 0.9865 | -0.2597 | 0.98635 | -0.26263 | 5.1577
10 | -0.031671 | -0.0079428 | 0.031748 | 0.0079907 | 7.6686e-05 | 4.7928e-05 | 0.047735 | 0.047734 | 0.047735 | 0.98732 | -0.24365 | 0.98993 | -0.19298 | 13.1139
11 | 0.019216 | 0.0048178 | -0.01921 | -0.0048145 | 5.5011e-06 | 3.2971e-06 | 0.028961 | 0.028961 | 0.028961 | 0.98732 | -0.24365 | 0.98701 | -0.24966 | 7.9563
12 | 0.0015316 | 0.00038381 | -0.0015315 | -0.00038384 | 6.3647e-09 | -3.6504e-08 | 0.0023105 | 0.0023105 | 0.0023105 | 0.98635 | -0.26263 | 0.98634 | -0.26272 | 0.63476
13 | 0.0825 | 0.021061 | -0.08227 | -0.020915 | 0.00023017 | 0.00014679 | 0.12343 | 0.12343 | 0.12343 | 0.99569 | -0.082018 | 0.99266 | -0.13993 | 33.9092
14 | 0.16278 | 0.041189 | -0.16255 | -0.041043 | 0.00022872 | 0.00014584 | 0.24341 | 0.24341 | 0.24341 | 0.99569 | -0.082018 | 0.99417 | -0.11134 | 33.4353
15 | -0.24528 | -0.06225 | 0.2457 | 0.062516 | 0.00041611 | 0.00026588 | 0.36684 | 0.36684 | 0.36684 | 0.99569 | -0.082018 | 0.99754 | -0.046815 | 50.3898
16 | 0.08227 | 0.020915 | -0.082068 | -0.020785 | 0.00020234 | 0.00012904 | 0.12343 | 0.12343 | 0.12343 | 0.99266 | -0.13993 | 0.98999 | -0.19113 | 33.9092
17 | 0.16255 | 0.041043 | -0.16223 | -0.040836 | 0.00032514 | 0.00020733 | 0.24341 | 0.24341 | 0.24341 | 0.99417 | -0.11134 | 0.99199 | -0.15318 | 33.4354
18 | -0.26718 | -0.067901 | 0.26779 | 0.068287 | 0.0006038 | 0.0003859 | 0.39889 | 0.39889 | 0.39889 | 0.99754 | -0.046815 | 1 | 0 | 54.7923
19 | 0.043626 | 0.010962 | -0.043551 | -0.010915 | 7.4244e-05 | 4.6954e-05 | 0.066395 | 0.066395 | 0.066395 | 0.97786 | -0.42609 | 0.97605 | -0.46181 | 18.2405
20 | -0.043626 | -0.010962 | 0.044081 | 0.01125 | 0.00045568 | 0.00028813 | 0.066395 | 0.066394 | 0.066395 | 0.97786 | -0.42609 | 0.98902 | -0.20971 | 18.2404
21 | -0.044081 | -0.01125 | 0.044121 | 0.011275 | 3.9609e-05 | 2.5042e-05 | 0.066394 | 0.066394 | 0.066394 | 0.98902 | -0.20971 | 0.98999 | -0.19113 | 18.2401
22 | -0.047381 | -0.011895 | 0.04755 | 0.012002 | 0.0001689 | 0.00010697 | 0.071506 | 0.071505 | 0.071506 | 0.98609 | -0.26742 | 0.98993 | -0.19298 | 19.6444
23 | 0.047381 | 0.011895 | -0.047328 | -0.011861 | 5.3613e-05 | 3.3956e-05 | 0.071506 | 0.071506 | 0.071506 | 0.98609 | -0.26742 | 0.98487 | -0.29117 | 19.6445
24 | -0.079298 | -0.019993 | 0.079449 | 0.02009 | 0.00015136 | 9.6502e-05 | 0.11924 | 0.11924 | 0.11924 | 0.98993 | -0.19298 | 0.99199 | -0.15318 | 32.7581
25 | 0.0011875 | 0.00029722 | -0.0011875 | -0.00029761 | 3.9162e-08 | -3.8825e-07 | 0.0017935 | 0.0017937 | 0.0017937 | 0.98514 | -0.28615 | 0.98511 | -0.28684 | 0.49277
26 | -0.11384 | -0.028766 | 0.11406 | 0.028904 | 0.00021729 | 0.0001388 | 0.17025 | 0.17025 | 0.17025 | 0.99547 | -0.086609 | 0.99754 | -0.046876 | 46.7724
27 | 0.13533 | 0.034354 | -0.13503 | -0.034159 | 0.00030446 | 0.00019459 | 0.20153 | 0.20153 | 0.20153 | 1 | 0 | 0.99754 | -0.046876 | 55.365

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.42572 | 0.10789

## res_load
| p_mw | q_mvar
0 | 0.012328 | 0.0030897
1 | 0.012721 | 0.0031881
2 | 0.021288 | 0.0053353
3 | 0.010913 | 0.0027351
4 | 0.021486 | 0.0053848
5 | 0.043551 | 0.010915
6 | 0.037947 | 0.0095104
7 | 0.047328 | 0.011861
8 | 0.01921 | 0.0048145
9 | 0.082779 | 0.020746
10 | 0.044737 | 0.011212
11 | 0.020966 | 0.0052547
12 | 0.0015315 | 0.00038384
13 | 0.020955 | 0.0052519
14 | 0.020968 | 0.005255
15 | 0.0011875 | 0.00029761

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1