## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-332_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-332_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-332_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_261-332_0_4_node_13 | 0.4 | n |  | TRUE
4 | bus_LV_261-332_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_261-332_0_4_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_261-332_0_4_node_27 | 0.4 | n |  | TRUE
7 | bus_LV_261-332_0_4_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_261-332_0_4_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_261-332_0_4_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_261-332_0_4_node_29 | 0.4 | n |  | TRUE
11 | bus_LV_261-332_0_4_node_17 | 0.4 | n |  | TRUE
12 | bus_LV_261-332_0_4_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_261-332_0_4_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_261-332_0_4_node_35 | 0.4 | n |  | TRUE
15 | bus_LV_261-332_0_4_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_261-332_0_4_node_34 | 0.4 | n |  | TRUE
17 | bus_LV_261-332_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_261-332_0_4_node_24 | 0.4 | n |  | TRUE
19 | bus_LV_261-332_0_4_node_21 | 0.4 | n |  | TRUE
20 | bus_LV_261-332_0_4_node_33 | 0.4 | n |  | TRUE
21 | bus_LV_261-332_0_4_node_28 | 0.4 | n |  | TRUE
22 | bus_LV_261-332_0_4_node_26 | 0.4 | n |  | TRUE
23 | bus_LV_261-332_0_4_node_25 | 0.4 | n |  | TRUE
24 | bus_LV_261-332_0_4_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_261-332_0_4_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_261-332_0_4_node_30 | 0.4 | n |  | TRUE
27 | bus_LV_261-332_0_4_node_32 | 0.4 | n |  | TRUE
28 | bus_LV_261-332_0_4_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_261-332_0_4_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_261-332_0_4_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_261-332_0_4_node_36 | 0.4 | n |  | TRUE
32 | bus_LV_261-332_0_4_node_31 | 0.4 | n |  | TRUE
33 | bus_MV_535_0_node_58 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-332_0_4_load_0 | 0 | 0.095933 | 0.024043 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-332_0_4_load_1 | 1 | 0.053625 | 0.01344 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-332_0_4_load_27 | 6 | 0.0094948 | 0.0023796 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-332_0_4_load_20 | 9 | 0.0079583 | 0.0019945 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-332_0_4_load_29 | 10 | 0.02879 | 0.0072154 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-332_0_4_load_17 | 11 | 0.0064584 | 0.0016186 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-332_0_4_load_14 | 12 | 0.038954 | 0.0097627 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-332_0_4_load_35 | 14 | 0.0088309 | 0.0022132 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-332_0_4_load_16 | 15 | 0.020618 | 0.0051673 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-332_0_4_load_34 | 16 | 0.0080047 | 0.0020062 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-332_0_4_load_24 | 18 | 0.0066428 | 0.0016648 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-332_0_4_load_21 | 19 | 0.0086582 | 0.00217 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-332_0_4_load_33 | 20 | 0.012642 | 0.0031685 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-332_0_4_load_28 | 21 | 0.0097445 | 0.0024422 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-332_0_4_load_26 | 22 | 0.0094906 | 0.0023786 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-332_0_4_load_25 | 23 | 0.0094744 | 0.0023745 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-332_0_4_load_19 | 24 | 0.036017 | 0.0090268 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-332_0_4_load_18 | 25 | 0.0062308 | 0.0015616 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-332_0_4_load_30 | 26 | 0.01371 | 0.003436 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-332_0_4_load_32 | 27 | 0.0087328 | 0.0021886 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-332_0_4_load_15 | 28 | 0.019769 | 0.0049546 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-332_0_4_load_23 | 29 | 0.020539 | 0.0051477 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-332_0_4_load_22 | 30 | 0.0080655 | 0.0020214 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-332_0_4_load_36 | 31 | 0.020798 | 0.0052126 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-332_0_4_load_31 | 32 | 0.0064516 | 0.0016169 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 31 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-332_0_4_line_0 |  | 0 | 1 | 0.033046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-332_0_4_line_1 |  | 1 | 2 | 0.015595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_261-332_0_4_line_2 |  | 2 | 3 | 0.028032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_261-332_0_4_line_3 |  | 3 | 20 | 0.0066149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_261-332_0_4_line_4 |  | 3 | 8 | 0.002868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-332_0_4_line_5 |  | 4 | 5 | 0.0095137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-332_0_4_line_6 |  | 4 | 6 | 0.046924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-332_0_4_line_7 |  | 5 | 11 | 0.02654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-332_0_4_line_8 |  | 5 | 12 | 0.012005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-332_0_4_line_9 |  | 6 | 23 | 0.015697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-332_0_4_line_10 |  | 7 | 8 | 0.036456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-332_0_4_line_11 |  | 7 | 9 | 0.051934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-332_0_4_line_12 |  | 7 | 10 | 0.017571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-332_0_4_line_13 |  | 9 | 25 | 0.016655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-332_0_4_line_14 |  | 10 | 26 | 0.018196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-332_0_4_line_15 |  | 11 | 27 | 0.026903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-332_0_4_line_16 |  | 12 | 28 | 0.01437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_261-332_0_4_line_17 |  | 13 | 14 | 0.0067462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_261-332_0_4_line_18 |  | 13 | 15 | 0.014681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_261-332_0_4_line_19 |  | 13 | 16 | 0.016764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_261-332_0_4_line_20 |  | 14 | 31 | 0.00051048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_261-332_0_4_line_21 |  | 15 | 28 | 0.010688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_261-332_0_4_line_22 |  | 16 | 20 | 0.012387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_261-332_0_4_line_23 |  | 17 | 18 | 0.0063742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-332_0_4_line_24 |  | 17 | 19 | 0.0074974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-332_0_4_line_25 |  | 18 | 32 | 0.014971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-332_0_4_line_26 |  | 19 | 30 | 0.010245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-332_0_4_line_27 |  | 21 | 22 | 0.015714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-332_0_4_line_28 |  | 22 | 23 | 0.015707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-332_0_4_line_29 |  | 24 | 25 | 0.036272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-332_0_4_line_30 |  | 27 | 32 | 0.012799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-332_0_4_line_31 |  | 29 | 30 | 0.014352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-332_0_4_trafo_36 | 0.63 MVA 20/0.4 kV | 33 | 31 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2681871.8357 | 1247234.1823 | 2681892.9377 | 1247245.5654 | 2681899.591 | 1247251.7291
1 | 2681911.0315 | 1247262.3276 | 2681899.591 | 1247251.7291
2 | 2681911.0315 | 1247262.3276 | 2681918.3397 | 1247262.0617 | 2681922.4811 | 1247254.8136 | 2681926.0884 | 1247248.5032 | 2681928.6123 | 1247244.0682
3 | 2681928.6123 | 1247244.0682 | 2681922.7664 | 1247240.9725
4 | 2681928.6123 | 1247244.0682 | 2681931.3103 | 1247245.0617
5 | 2681842.7218 | 1247198.9493 | 2681846.4712 | 1247200.9469 | 2681851.1747 | 1247203.3135
6 | 2681842.7218 | 1247198.9493 | 2681873.3101 | 1247163.3653
7 | 2681851.1747 | 1247203.3135 | 2681868.3615 | 1247183.0895
8 | 2681851.1747 | 1247203.3135 | 2681861.047 | 1247208.2757 | 2681861.8914 | 1247208.7231
9 | 2681873.3101 | 1247163.3653 | 2681883.5422 | 1247151.4621
10 | 2681931.3103 | 1247245.0617 | 2681933.4962 | 1247245.9481 | 2681935.985 | 1247246.7831 | 2681939.8051 | 1247246.936 | 2681950.927 | 1247246.734 | 2681965.1659 | 1247244.5514 | 2681967.2486 | 1247244.1576
11 | 2681967.2486 | 1247244.1576 | 2681950.5172 | 1247230.4831 | 2681957.9113 | 1247218.5432 | 2681958.2789 | 1247217.0916 | 2681958.1409 | 1247215.5997 | 2681957.5026 | 1247214.2343 | 2681955.1018 | 1247212.4999 | 2681952.5108 | 1247210.8629 | 2681947.6383 | 1247207.8054
12 | 2681967.2486 | 1247244.1576 | 2681970.2799 | 1247243.4546 | 2681975.6378 | 1247241.6495 | 2681981.305 | 1247237.1468 | 2681982.3256 | 1247235.9577
13 | 2681933.5309 | 1247198.9531 | 2681947.6383 | 1247207.8054
14 | 2681994.1765 | 1247222.1499 | 2681982.3256 | 1247235.9577
15 | 2681887.1417 | 1247173.1183 | 2681882.5861 | 1247169.2333 | 2681882.0176 | 1247168.8251 | 2681881.3321 | 1247168.6933 | 2681880.5967 | 1247168.8833 | 2681880.0158 | 1247169.3757 | 2681868.3615 | 1247183.0895
16 | 2681861.8914 | 1247208.7231 | 2681874.5884 | 1247215.4516
17 | 2681897.0043 | 1247227.3305 | 2681897.5169 | 1247226.3146 | 2681900.0364 | 1247221.3041
18 | 2681897.0043 | 1247227.3305 | 2681884.0327 | 1247220.4564
19 | 2681897.0043 | 1247227.3305 | 2681911.8196 | 1247235.1758
20 | 2681900.0364 | 1247221.3041 | 2681900.2657 | 1247220.848
21 | 2681884.0327 | 1247220.4564 | 2681874.5884 | 1247215.4516
22 | 2681922.7664 | 1247240.9725 | 2681911.8196 | 1247235.1758
23 | 2681913.1215 | 1247195.274 | 2681908.2715 | 1247191.1378
24 | 2681913.1215 | 1247195.274 | 2681914.2413 | 1247196.2346 | 2681919.3291 | 1247199.4563
25 | 2681908.2715 | 1247191.1378 | 2681896.8805 | 1247181.4236
26 | 2681927.9852 | 1247204.9373 | 2681919.3291 | 1247199.4563
27 | 2681904.0243 | 1247127.6348 | 2681893.7808 | 1247139.5513
28 | 2681893.7808 | 1247139.5513 | 2681883.5422 | 1247151.4621
29 | 2681933.5309 | 1247198.9531 | 2681925.169 | 1247193.7059 | 2681919.745 | 1247190.4508 | 2681904.4885 | 1247177.4038
30 | 2681887.1417 | 1247173.1183 | 2681896.8805 | 1247181.4236
31 | 2681927.9852 | 1247204.9373 | 2681940.1105 | 1247212.6152

## bus_geodata
| x | y | coords
0 | 2681871.8357 | 1247234.1823
1 | 2681899.591 | 1247251.7291
2 | 2681911.0315 | 1247262.3276
3 | 2681928.6123 | 1247244.0682
4 | 2681842.7218 | 1247198.9493
5 | 2681851.1747 | 1247203.3135
6 | 2681873.3101 | 1247163.3653
7 | 2681967.2486 | 1247244.1576
8 | 2681931.3103 | 1247245.0617
9 | 2681947.6383 | 1247207.8054
10 | 2681982.3256 | 1247235.9577
11 | 2681868.3615 | 1247183.0895
12 | 2681861.8914 | 1247208.7231
13 | 2681897.0043 | 1247227.3305
14 | 2681900.0364 | 1247221.3041
15 | 2681884.0327 | 1247220.4564
16 | 2681911.8197 | 1247235.1758
17 | 2681913.1215 | 1247195.274
18 | 2681908.2715 | 1247191.1378
19 | 2681919.3291 | 1247199.4563
20 | 2681922.7664 | 1247240.9725
21 | 2681904.0243 | 1247127.6348
22 | 2681893.7808 | 1247139.5513
23 | 2681883.5422 | 1247151.4621
24 | 2681904.4885 | 1247177.4038
25 | 2681933.5309 | 1247198.9531
26 | 2681994.1765 | 1247222.1499
27 | 2681887.1417 | 1247173.1183
28 | 2681874.5884 | 1247215.4516
29 | 2681940.1105 | 1247212.6152
30 | 2681927.9852 | 1247204.9373
31 | 2681900.2657 | 1247220.848
32 | 2681896.8805 | 1247181.4236
33 | 2681897.0043 | 1247227.3305

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99225 | -0.14908 | 0.095933 | 0.024043
1 | 0.99514 | -0.093119 | 0.053625 | 0.01344
2 | 0.99621 | -0.072615 | 0 | 0
3 | 0.99717 | -0.054225 | 0 | 0
4 | 0.99585 | -0.079652 | 0 | 0
5 | 0.99618 | -0.073266 | 0 | 0
6 | 0.99421 | -0.11121 | 0.0094948 | 0.0023796
7 | 0.99383 | -0.11834 | 0 | 0
8 | 0.99692 | -0.058887 | 0 | 0
9 | 0.99144 | -0.16447 | 0.0079583 | 0.0019945
10 | 0.99315 | -0.13153 | 0.02879 | 0.0072154
11 | 0.99459 | -0.10387 | 0.0064584 | 0.0016186
12 | 0.99732 | -0.051413 | 0.038954 | 0.0097627
13 | 0.99926 | -0.014134 | 0 | 0
14 | 0.99995 | -0.0010118 | 0.0088309 | 0.0022132
15 | 0.99865 | -0.025871 | 0.020618 | 0.0051673
16 | 0.99825 | -0.033388 | 0.0080047 | 0.0020062
17 | 0.99173 | -0.15917 | 0 | 0
18 | 0.99194 | -0.15496 | 0.0066428 | 0.0016648
19 | 0.99147 | -0.16412 | 0.0086582 | 0.00217
20 | 0.99753 | -0.047205 | 0.012642 | 0.0031685
21 | 0.99338 | -0.1272 | 0.0097445 | 0.0024422
22 | 0.99352 | -0.1245 | 0.0094906 | 0.0023786
23 | 0.9938 | -0.11916 | 0.0094744 | 0.0023745
24 | 0.9896 | -0.20018 | 0.036017 | 0.0090268
25 | 0.9908 | -0.17695 | 0.0062308 | 0.0015616
26 | 0.99292 | -0.13594 | 0.01371 | 0.003436
27 | 0.99313 | -0.13192 | 0.0087328 | 0.0021886
28 | 0.99825 | -0.033462 | 0.019769 | 0.0049546
29 | 0.99093 | -0.17455 | 0.020539 | 0.0051477
30 | 0.9912 | -0.16932 | 0.0080655 | 0.0020214
31 | 1 | 0 | -0.45905 | -0.11562
32 | 0.99254 | -0.14332 | 0.0064516 | 0.0016169
33 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.095933 | -0.024043 | 0.096189 | 0.024207 | 0.00025648 | 0.00016372 | 0.14386 | 0.14386 | 0.14386 | 0.99225 | -0.14908 | 0.99514 | -0.093119 | 39.5232
1 | -0.14981 | -0.037646 | 0.14996 | 0.03774 | 0.00014678 | 9.3536e-05 | 0.22405 | 0.22405 | 0.22405 | 0.99514 | -0.093119 | 0.99621 | -0.072615 | 30.776
2 | -0.14996 | -0.03774 | 0.15009 | 0.037823 | 0.00013192 | 8.2969e-05 | 0.22405 | 0.22405 | 0.22405 | 0.99621 | -0.072615 | 0.99717 | -0.054225 | 15.388
3 | -0.24329 | -0.061369 | 0.24337 | 0.061421 | 8.1801e-05 | 5.2007e-05 | 0.36319 | 0.36319 | 0.36319 | 0.99717 | -0.054225 | 0.99753 | -0.047205 | 24.9442
4 | 0.093197 | 0.023546 | -0.093176 | -0.023533 | 2.0821e-05 | 1.3288e-05 | 0.13914 | 0.13914 | 0.13914 | 0.99717 | -0.054225 | 0.99692 | -0.058887 | 38.2251
5 | -0.038279 | -0.0096214 | 0.038291 | 0.0096288 | 1.1676e-05 | 7.3486e-06 | 0.057207 | 0.057207 | 0.057207 | 0.99585 | -0.079652 | 0.99618 | -0.073266 | 15.7162
6 | 0.038279 | 0.0096214 | -0.038221 | -0.0095852 | 5.7587e-05 | 3.6246e-05 | 0.057207 | 0.057207 | 0.057207 | 0.99585 | -0.079652 | 0.99421 | -0.11121 | 15.7163
7 | 0.065805 | 0.01659 | -0.065708 | -0.016529 | 9.6228e-05 | 6.1241e-05 | 0.098329 | 0.098329 | 0.098329 | 0.99618 | -0.073266 | 0.99459 | -0.10387 | 27.0134
8 | -0.1041 | -0.026219 | 0.1042 | 0.026289 | 0.0001089 | 6.9542e-05 | 0.15554 | 0.15554 | 0.15554 | 0.99618 | -0.073266 | 0.99732 | -0.051413 | 42.7295
9 | 0.028727 | 0.0072056 | -0.028716 | -0.0071988 | 1.0882e-05 | 6.7609e-06 | 0.042997 | 0.042997 | 0.042997 | 0.99421 | -0.11121 | 0.9938 | -0.11916 | 11.8123
10 | -0.092912 | -0.023364 | 0.093176 | 0.023533 | 0.00026467 | 0.00016891 | 0.13914 | 0.13914 | 0.13914 | 0.99383 | -0.11834 | 0.99692 | -0.058887 | 38.2252
11 | 0.050383 | 0.012694 | -0.050272 | -0.012624 | 0.0001109 | 7.0302e-05 | 0.075459 | 0.075459 | 0.075459 | 0.99383 | -0.11834 | 0.99144 | -0.16447 | 20.7306
12 | 0.042529 | 0.01067 | -0.042502 | -0.010653 | 2.672e-05 | 1.6873e-05 | 0.06368 | 0.06368 | 0.06368 | 0.99383 | -0.11834 | 0.99315 | -0.13153 | 17.4946
13 | 0.042313 | 0.010629 | -0.042288 | -0.010613 | 2.5196e-05 | 1.5911e-05 | 0.063515 | 0.063515 | 0.063515 | 0.99144 | -0.16447 | 0.9908 | -0.17695 | 17.4492
14 | 0.013713 | 0.0034376 | -0.01371 | -0.003436 | 2.8804e-06 | 1.608e-06 | 0.020546 | 0.020546 | 0.020546 | 0.99315 | -0.13153 | 0.99292 | -0.13594 | 5.6444
15 | 0.05925 | 0.01491 | -0.059171 | -0.01486 | 7.9314e-05 | 5.0413e-05 | 0.088666 | 0.088666 | 0.088666 | 0.99459 | -0.10387 | 0.99313 | -0.13192 | 24.3589
16 | -0.14316 | -0.036051 | 0.14328 | 0.03613 | 0.00012299 | 7.8339e-05 | 0.21366 | 0.21366 | 0.21366 | 0.99732 | -0.051413 | 0.99825 | -0.033462 | 29.3482
17 | -0.44826 | -0.11321 | 0.44854 | 0.11339 | 0.00028207 | 0.00018017 | 0.66782 | 0.66782 | 0.66782 | 0.99926 | -0.014134 | 0.99995 | -0.0010118 | 45.8669
18 | 0.18383 | 0.046354 | -0.18373 | -0.046289 | 0.00010321 | 6.5285e-05 | 0.27384 | 0.27384 | 0.27384 | 0.99926 | -0.014134 | 0.99865 | -0.025871 | 18.808
19 | 0.26443 | 0.066859 | -0.26419 | -0.066704 | 0.00024395 | 0.00015525 | 0.39398 | 0.39398 | 0.39398 | 0.99926 | -0.014134 | 0.99825 | -0.033388 | 27.0589
20 | -0.45738 | -0.11561 | 0.4574 | 0.11562 | 2.2192e-05 | 1.4176e-05 | 0.68096 | 0.68096 | 0.68096 | 0.99995 | -0.0010118 | 1 | 0 | 46.7694
21 | 0.16311 | 0.041122 | -0.16305 | -0.041084 | 5.923e-05 | 3.7348e-05 | 0.24312 | 0.24312 | 0.24312 | 0.99865 | -0.025871 | 0.99825 | -0.033462 | 16.698
22 | 0.25618 | 0.064698 | -0.25601 | -0.06459 | 0.0001695 | 0.00010783 | 0.38205 | 0.38205 | 0.38205 | 0.99825 | -0.033388 | 0.99753 | -0.047205 | 26.2394
23 | -0.037284 | -0.009352 | 0.037292 | 0.0093567 | 7.4814e-06 | 4.7058e-06 | 0.055945 | 0.055945 | 0.055945 | 0.99173 | -0.15917 | 0.99194 | -0.15496 | 15.3695
24 | 0.037284 | 0.009352 | -0.037275 | -0.0093465 | 8.7996e-06 | 5.535e-06 | 0.055945 | 0.055945 | 0.055945 | 0.99173 | -0.15917 | 0.99147 | -0.16412 | 15.3695
25 | -0.043934 | -0.011022 | 0.043959 | 0.011037 | 2.4388e-05 | 1.5415e-05 | 0.06591 | 0.06591 | 0.06591 | 0.99194 | -0.15496 | 0.99254 | -0.14332 | 18.1071
26 | 0.028617 | 0.0071765 | -0.02861 | -0.0071721 | 7.0876e-06 | 4.404e-06 | 0.042951 | 0.042951 | 0.042951 | 0.99147 | -0.16412 | 0.9912 | -0.16932 | 11.7996
27 | -0.0097445 | -0.0024422 | 0.0097458 | 0.0024428 | 1.2555e-06 | 6.0006e-07 | 0.014597 | 0.014596 | 0.014597 | 0.99338 | -0.1272 | 0.99352 | -0.1245 | 4.01
28 | -0.019236 | -0.0048214 | 0.019241 | 0.0048243 | 4.889e-06 | 2.9255e-06 | 0.028811 | 0.028811 | 0.028811 | 0.99352 | -0.1245 | 0.9938 | -0.11916 | 7.915
29 | -0.036017 | -0.0090268 | 0.036057 | 0.0090519 | 3.9895e-05 | 2.5067e-05 | 0.054158 | 0.054158 | 0.054158 | 0.9896 | -0.20018 | 0.9908 | -0.17695 | 14.8785
30 | 0.050438 | 0.012671 | -0.05041 | -0.012654 | 2.7419e-05 | 1.7383e-05 | 0.075582 | 0.075582 | 0.075582 | 0.99313 | -0.13192 | 0.99254 | -0.14332 | 20.7643
31 | -0.020539 | -0.0051477 | 0.020544 | 0.0051507 | 5.1196e-06 | 3.0916e-06 | 0.030843 | 0.030843 | 0.030843 | 0.99093 | -0.17455 | 0.9912 | -0.16932 | 8.4732

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.47985 | 0.12083

## res_load
| p_mw | q_mvar
0 | 0.095933 | 0.024043
1 | 0.053625 | 0.01344
2 | 0.0094948 | 0.0023796
3 | 0.0079583 | 0.0019945
4 | 0.02879 | 0.0072154
5 | 0.0064584 | 0.0016186
6 | 0.038954 | 0.0097627
7 | 0.0088309 | 0.0022132
8 | 0.020618 | 0.0051673
9 | 0.0080047 | 0.0020062
10 | 0.0066428 | 0.0016648
11 | 0.0086582 | 0.00217
12 | 0.012642 | 0.0031685
13 | 0.0097445 | 0.0024422
14 | 0.0094906 | 0.0023786
15 | 0.0094744 | 0.0023745
16 | 0.036017 | 0.0090268
17 | 0.0062308 | 0.0015616
18 | 0.01371 | 0.003436
19 | 0.0087328 | 0.0021886
20 | 0.019769 | 0.0049546
21 | 0.020539 | 0.0051477
22 | 0.0080655 | 0.0020214
23 | 0.020798 | 0.0052126
24 | 0.0064516 | 0.0016169

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1