## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-346_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-346_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-346_0_3_node_7 | 0.4 | n |  | TRUE
3 | bus_LV_261-346_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-346_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_261-346_0_3_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_261-346_0_3_node_23 | 0.4 | n |  | TRUE
7 | bus_LV_261-346_0_3_node_44 | 0.4 | n |  | TRUE
8 | bus_LV_261-346_0_3_node_22 | 0.4 | n |  | TRUE
9 | bus_LV_261-346_0_3_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_261-346_0_3_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_261-346_0_3_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_261-346_0_3_node_15 | 0.4 | n |  | TRUE
13 | bus_LV_261-346_0_3_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_261-346_0_3_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_261-346_0_3_node_40 | 0.4 | n |  | TRUE
16 | bus_LV_261-346_0_3_node_39 | 0.4 | n |  | TRUE
17 | bus_LV_261-346_0_3_node_36 | 0.4 | n |  | TRUE
18 | bus_LV_261-346_0_3_node_37 | 0.4 | n |  | TRUE
19 | bus_LV_261-346_0_3_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_261-346_0_3_node_45 | 0.4 | n |  | TRUE
21 | bus_LV_261-346_0_3_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_261-346_0_3_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_261-346_0_3_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_261-346_0_3_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_261-346_0_3_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_261-346_0_3_node_68 | 0.4 | n |  | TRUE
27 | bus_LV_261-346_0_3_node_65 | 0.4 | n |  | TRUE
28 | bus_LV_261-346_0_3_node_41 | 0.4 | n |  | TRUE
29 | bus_LV_261-346_0_3_node_67 | 0.4 | n |  | TRUE
30 | bus_LV_261-346_0_3_node_69 | 0.4 | n |  | TRUE
31 | bus_LV_261-346_0_3_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_261-346_0_3_node_38 | 0.4 | n |  | TRUE
33 | bus_LV_261-346_0_3_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_261-346_0_3_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_261-346_0_3_node_35 | 0.4 | n |  | TRUE
36 | bus_LV_261-346_0_3_node_34 | 0.4 | n |  | TRUE
37 | bus_LV_261-346_0_3_node_77 | 0.4 | n |  | TRUE
38 | bus_LV_261-346_0_3_node_47 | 0.4 | n |  | TRUE
39 | bus_LV_261-346_0_3_node_32 | 0.4 | n |  | TRUE
40 | bus_LV_261-346_0_3_node_78 | 0.4 | n |  | TRUE
41 | bus_LV_261-346_0_3_node_29 | 0.4 | n |  | TRUE
42 | bus_LV_261-346_0_3_node_27 | 0.4 | n |  | TRUE
43 | bus_LV_261-346_0_3_node_28 | 0.4 | n |  | TRUE
44 | bus_LV_261-346_0_3_node_31 | 0.4 | n |  | TRUE
45 | bus_LV_261-346_0_3_node_26 | 0.4 | n |  | TRUE
46 | bus_LV_261-346_0_3_node_30 | 0.4 | n |  | TRUE
47 | bus_LV_261-346_0_3_node_33 | 0.4 | n |  | TRUE
48 | bus_LV_261-346_0_3_node_48 | 0.4 | n |  | TRUE
49 | bus_LV_261-346_0_3_node_76 | 0.4 | n |  | TRUE
50 | bus_LV_261-346_0_3_node_66 | 0.4 | n |  | TRUE
51 | bus_LV_261-346_0_3_node_52 | 0.4 | n |  | TRUE
52 | bus_LV_261-346_0_3_node_54 | 0.4 | n |  | TRUE
53 | bus_LV_261-346_0_3_node_50 | 0.4 | n |  | TRUE
54 | bus_LV_261-346_0_3_node_63 | 0.4 | n |  | TRUE
55 | bus_LV_261-346_0_3_node_60 | 0.4 | n |  | TRUE
56 | bus_LV_261-346_0_3_node_61 | 0.4 | n |  | TRUE
57 | bus_LV_261-346_0_3_node_46 | 0.4 | n |  | TRUE
58 | bus_LV_261-346_0_3_node_72 | 0.4 | n |  | TRUE
59 | bus_LV_261-346_0_3_node_70 | 0.4 | n |  | TRUE
60 | bus_LV_261-346_0_3_node_49 | 0.4 | n |  | TRUE
61 | bus_LV_261-346_0_3_node_51 | 0.4 | n |  | TRUE
62 | bus_LV_261-346_0_3_node_53 | 0.4 | n |  | TRUE
63 | bus_LV_261-346_0_3_node_58 | 0.4 | n |  | TRUE
64 | bus_LV_261-346_0_3_node_56 | 0.4 | n |  | TRUE
65 | bus_LV_261-346_0_3_node_55 | 0.4 | n |  | TRUE
66 | bus_LV_261-346_0_3_node_57 | 0.4 | n |  | TRUE
67 | bus_LV_261-346_0_3_node_59 | 0.4 | n |  | TRUE
68 | bus_LV_261-346_0_3_node_64 | 0.4 | n |  | TRUE
69 | bus_LV_261-346_0_3_node_62 | 0.4 | n |  | TRUE
70 | bus_LV_261-346_0_3_node_75 | 0.4 | n |  | TRUE
71 | bus_LV_261-346_0_3_node_71 | 0.4 | n |  | TRUE
72 | bus_LV_261-346_0_3_node_73 | 0.4 | n |  | TRUE
73 | bus_LV_261-346_0_3_node_74 | 0.4 | n |  | TRUE
74 | bus_MV_551_0_node_10 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-346_0_3_load_0 | 0 | 0.0097605 | 0.0024462 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-346_0_3_load_44 | 7 | 0.002704 | 0.00067769 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-346_0_3_load_22 | 8 | 0.011647 | 0.0029191 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-346_0_3_load_11 | 9 | 0.01525 | 0.003822 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-346_0_3_load_15 | 12 | 0.0091931 | 0.002304 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-346_0_3_load_13 | 13 | 0.012307 | 0.0030845 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-346_0_3_load_39 | 16 | 0.0036684 | 0.00091939 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-346_0_3_load_36 | 17 | 0.0047682 | 0.001195 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-346_0_3_load_37 | 18 | 0.0020895 | 0.00052369 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-346_0_3_load_24 | 19 | 0.0024749 | 0.00062028 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-346_0_3_load_45 | 20 | 0.0025095 | 0.00062895 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-346_0_3_load_18 | 21 | 0.011734 | 0.0029409 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-346_0_3_load_12 | 23 | 0.0088768 | 0.0022247 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-346_0_3_load_16 | 24 | 0.0059397 | 0.0014886 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-346_0_3_load_14 | 25 | 0.010519 | 0.0026364 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-346_0_3_load_68 | 26 | 0.0014671 | 0.0003677 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-346_0_3_load_65 | 27 | 0.0065598 | 0.001644 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-346_0_3_load_67 | 29 | 0.0052007 | 0.0013034 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-346_0_3_load_69 | 30 | 0.018282 | 0.0045818 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-346_0_3_load_38 | 32 | 0.0015266 | 0.00038261 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-346_0_3_load_21 | 34 | 0.0021175 | 0.00053069 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-346_0_3_load_35 | 35 | 0.014931 | 0.003742 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-346_0_3_load_34 | 36 | 0.0049306 | 0.0012357 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-346_0_3_load_47 | 38 | 0.00389 | 0.00097494 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-346_0_3_load_32 | 39 | 0.0035257 | 0.00088361 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-346_0_3_load_78 | 40 | 0.0066417 | 0.0016646 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-346_0_3_load_29 | 41 | 0.0027198 | 0.00068164 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-346_0_3_load_28 | 43 | 0.0084101 | 0.0021078 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-346_0_3_load_26 | 45 | 0.012453 | 0.003121 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-346_0_3_load_30 | 46 | 0.0025901 | 0.00064914 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-346_0_3_load_33 | 47 | 0.0038777 | 0.00097185 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-346_0_3_load_48 | 48 | 0.0026742 | 0.00067023 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-346_0_3_load_76 | 49 | 0.00296 | 0.00074185 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-346_0_3_load_66 | 50 | 0.015077 | 0.0037787 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-346_0_3_load_54 | 52 | 0.016069 | 0.0040272 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-346_0_3_load_50 | 53 | 0.013763 | 0.0034494 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-346_0_3_load_63 | 54 | 0.0065598 | 0.001644 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-346_0_3_load_60 | 55 | 0.0094794 | 0.0023758 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-346_0_3_load_61 | 56 | 0.0082324 | 0.0020632 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-346_0_3_load_46 | 57 | 0.0023269 | 0.00058316 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-346_0_3_load_72 | 58 | 0.0011262 | 0.00028224 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-346_0_3_load_70 | 59 | 0.0022752 | 0.00057023 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-346_0_3_load_49 | 60 | 0.0025902 | 0.00064915 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-346_0_3_load_53 | 62 | 0.0025975 | 0.00065099 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-346_0_3_load_58 | 63 | 0.0022676 | 0.00056832 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-346_0_3_load_56 | 64 | 0.0027751 | 0.00069551 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-346_0_3_load_55 | 65 | 0.013728 | 0.0034406 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-346_0_3_load_57 | 66 | 0.0014139 | 0.00035436 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-346_0_3_load_59 | 67 | 0.0035749 | 0.00089595 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-346_0_3_load_64 | 68 | 0.0013074 | 0.00032765 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-346_0_3_load_62 | 69 | 0.0013102 | 0.00032836 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-346_0_3_load_75 | 70 | 0.0011789 | 0.00029545 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-346_0_3_load_71 | 71 | 0.0025575 | 0.00064098 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-346_0_3_load_73 | 72 | 0.0017566 | 0.00044025 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-346_0_3_load_74 | 73 | 0.0011838 | 0.00029668 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 57 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-346_0_3_line_0 |  | 0 | 1 | 0.027742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-346_0_3_line_1 |  | 1 | 2 | 0.048567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-346_0_3_line_2 |  | 2 | 9 | 0.0076281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-346_0_3_line_3 |  | 2 | 3 | 0.067986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-346_0_3_line_4 |  | 3 | 4 | 0.067246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-346_0_3_line_5 |  | 4 | 8 | 0.027278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-346_0_3_line_6 |  | 5 | 6 | 0.025488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_261-346_0_3_line_7 |  | 5 | 7 | 0.023815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_261-346_0_3_line_8 |  | 6 | 19 | 0.014437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_261-346_0_3_line_9 |  | 6 | 8 | 0.019925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-346_0_3_line_10 |  | 7 | 20 | 0.038673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_261-346_0_3_line_11 |  | 9 | 23 | 0.029551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-346_0_3_line_12 |  | 10 | 11 | 0.054577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-346_0_3_line_13 |  | 10 | 12 | 0.081231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-346_0_3_line_14 |  | 11 | 13 | 0.018202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-346_0_3_line_15 |  | 12 | 24 | 0.022629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-346_0_3_line_16 |  | 13 | 25 | 0.016021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-346_0_3_line_17 |  | 14 | 15 | 0.008996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-346_0_3_line_18 |  | 14 | 16 | 0.01908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-346_0_3_line_19 |  | 15 | 26 | 0.025279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-346_0_3_line_20 |  | 15 | 27 | 0.0034802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-346_0_3_line_21 |  | 16 | 31 | 0.015755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-346_0_3_line_22 |  | 17 | 18 | 0.024185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-346_0_3_line_23 |  | 18 | 32 | 0.024791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-346_0_3_line_24 |  | 19 | 41 | 0.013754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_261-346_0_3_line_25 |  | 20 | 57 | 0.0010833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_261-346_0_3_line_26 |  | 21 | 22 | 0.018638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-346_0_3_line_27 |  | 22 | 33 | 0.020425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-346_0_3_line_28 |  | 22 | 34 | 0.032167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-346_0_3_line_29 |  | 24 | 31 | 0.01922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-346_0_3_line_30 |  | 26 | 49 | 3.5419e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-346_0_3_line_31 |  | 27 | 50 | 0.0071037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-346_0_3_line_32 |  | 28 | 29 | 0.048522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-346_0_3_line_33 |  | 28 | 30 | 0.037952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-346_0_3_line_34 |  | 29 | 50 | 0.017254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-346_0_3_line_35 |  | 30 | 54 | 0.018846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-346_0_3_line_36 |  | 31 | 32 | 0.03851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-346_0_3_line_37 |  | 33 | 35 | 0.012128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-346_0_3_line_38 |  | 33 | 36 | 0.020059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-346_0_3_line_39 |  | 34 | 37 | 0.0019393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-346_0_3_line_40 |  | 35 | 38 | 0.013161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-346_0_3_line_41 |  | 36 | 39 | 0.01586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-346_0_3_line_42 |  | 37 | 40 | 0.021381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-346_0_3_line_43 |  | 38 | 48 | 0.039195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-346_0_3_line_44 |  | 39 | 44 | 0.012525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-346_0_3_line_45 |  | 41 | 42 | 0.0031312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_261-346_0_3_line_46 |  | 42 | 46 | 0.016054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_261-346_0_3_line_47 |  | 42 | 45 | 0.020155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-346_0_3_line_48 |  | 43 | 44 | 0.02269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-346_0_3_line_49 |  | 44 | 47 | 0.0015928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-346_0_3_line_50 |  | 46 | 47 | 0.012952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
51 | LV_261-346_0_3_line_51 |  | 48 | 60 | 0.0010682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-346_0_3_line_52 |  | 49 | 70 | 0.020194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-346_0_3_line_53 |  | 51 | 52 | 0.046001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-346_0_3_line_54 |  | 51 | 53 | 0.01538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-346_0_3_line_55 |  | 53 | 61 | 0.038139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-346_0_3_line_56 |  | 55 | 56 | 0.00087401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-346_0_3_line_57 |  | 56 | 69 | 0.015291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-346_0_3_line_58 |  | 57 | 58 | 0.01241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-346_0_3_line_59 |  | 58 | 59 | 0.007604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-346_0_3_line_60 |  | 59 | 71 | 0.00013956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-346_0_3_line_61 |  | 60 | 61 | 0.015165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-346_0_3_line_62 |  | 61 | 62 | 0.0049033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-346_0_3_line_63 |  | 62 | 63 | 0.00026149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-346_0_3_line_64 |  | 63 | 64 | 0.018397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-346_0_3_line_65 |  | 64 | 65 | 0.018548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-346_0_3_line_66 |  | 65 | 66 | 0.0010109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-346_0_3_line_67 |  | 66 | 67 | 0.0011596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-346_0_3_line_68 |  | 67 | 68 | 0.022978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-346_0_3_line_69 |  | 68 | 69 | 0.00013316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-346_0_3_line_70 |  | 70 | 73 | 2.0528e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-346_0_3_line_71 |  | 71 | 72 | 0.01779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-346_0_3_line_72 |  | 72 | 73 | 0.0011137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-346_0_3_trafo_46 | 0.63 MVA 20/0.4 kV | 74 | 57 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2686042.9867 | 1251117.2393 | 2686016.6381 | 1251108.5581
1 | 2686006.8549 | 1251123.1193 | 2686009.8716 | 1251123.3187 | 2686034.319 | 1251131.8911 | 2686035.1154 | 1251129.5565 | 2686036.0854 | 1251126.7018 | 2686036.8422 | 1251124.4889 | 2686039.9331 | 1251125.301 | 2686041.5187 | 1251121.1209 | 2686042.9867 | 1251117.2393
2 | 2686006.8549 | 1251123.1193 | 2686009.6039 | 1251125.6388 | 2686013.2774 | 1251126.9459
3 | 2685941.7897 | 1251106.5074 | 2685958.1554 | 1251106.0221 | 2686006.8549 | 1251123.1193
4 | 2685926.7748 | 1251148.6436 | 2685948.7125 | 1251135.6074 | 2685931.9992 | 1251109.0673 | 2685936.843 | 1251106.6469 | 2685941.7897 | 1251106.5074
5 | 2685926.7748 | 1251148.6436 | 2685941.8575 | 1251171.3722
6 | 2685974.7236 | 1251174.792 | 2685958.2658 | 1251185.2723 | 2685952.8745 | 1251187.9739
7 | 2685974.7236 | 1251174.792 | 2685987.8983 | 1251194.6311
8 | 2685952.8745 | 1251187.9739 | 2685942.4794 | 1251193.1938 | 2685940.0987 | 1251194.6766
9 | 2685952.8745 | 1251187.9739 | 2685941.8575 | 1251171.3722
10 | 2685987.8983 | 1251194.6311 | 2686001.1778 | 1251214.628 | 2686009.2916 | 1251226.8481
11 | 2686013.2774 | 1251126.9459 | 2686041.1183 | 1251136.8517
12 | 2686089.2735 | 1251165.2698 | 2686092.9152 | 1251162.9765 | 2686110.2204 | 1251167.965 | 2686112.3452 | 1251171.354 | 2686118.9343 | 1251181.8132 | 2686121.6413 | 1251186.178 | 2686122.4964 | 1251191.2276 | 2686120.4571 | 1251196.4908
13 | 2686120.4571 | 1251196.4908 | 2686108.0951 | 1251199.9138 | 2686106.4281 | 1251210.2084 | 2686105.2484 | 1251219.6985 | 2686106.0979 | 1251232.9208 | 2686097.7289 | 1251241.0386 | 2686095.9805 | 1251241.3579 | 2686087.741 | 1251247.8431 | 2686085.3049 | 1251247.6965 | 2686080.1699 | 1251240.5499
14 | 2686089.2735 | 1251165.2698 | 2686073.8677 | 1251174.9637
15 | 2686080.1699 | 1251240.5499 | 2686061.5213 | 1251253.3684
16 | 2686060.3076 | 1251183.4962 | 2686073.8677 | 1251174.9637
17 | 2686056.6778 | 1251298.2189 | 2686064.4293 | 1251293.6168
18 | 2686064.4293 | 1251293.6168 | 2686054.1611 | 1251277.5352
19 | 2686056.6778 | 1251298.2189 | 2686042.6958 | 1251277.1588
20 | 2686056.6778 | 1251298.2189 | 2686058.6359 | 1251301.096
21 | 2686045.6821 | 1251264.2558 | 2686054.1611 | 1251277.5352
22 | 2685996.9453 | 1251191.6062 | 2686010.507 | 1251211.6314
23 | 2686010.507 | 1251211.6314 | 2686024.4086 | 1251232.1585
24 | 2685928.4238 | 1251201.9483 | 2685940.0987 | 1251194.6766
25 | 2686009.2916 | 1251226.8481 | 2686009.8908 | 1251227.7506
26 | 2685849.6066 | 1251230.5982 | 2685839.134 | 1251215.1811
27 | 2685849.6066 | 1251230.5982 | 2685860.8789 | 1251247.6521
28 | 2685849.6066 | 1251230.5982 | 2685820.6406 | 1251244.5878
29 | 2686045.6821 | 1251264.2558 | 2686061.5213 | 1251253.3684
30 | 2686042.6763 | 1251277.1293 | 2686042.6958 | 1251277.1588
31 | 2686058.6359 | 1251301.096 | 2686062.6328 | 1251306.9686
32 | 2686099.641 | 1251361.346 | 2686072.3405 | 1251321.2325
33 | 2686099.641 | 1251361.346 | 2686067.8357 | 1251382.0533
34 | 2686062.6328 | 1251306.9686 | 2686072.3405 | 1251321.2325
35 | 2686067.8357 | 1251382.0533 | 2686052.0424 | 1251392.3358
36 | 2686045.6821 | 1251264.2558 | 2686038.0281 | 1251252.269 | 2686024.4086 | 1251232.1585
37 | 2685860.8789 | 1251247.6521 | 2685867.5688 | 1251257.768
38 | 2685860.8789 | 1251247.6521 | 2685877.5353 | 1251236.4753
39 | 2685818.8943 | 1251245.4312 | 2685820.6406 | 1251244.5878
40 | 2685874.8283 | 1251268.7454 | 2685867.5688 | 1251257.768
41 | 2685890.7053 | 1251227.6379 | 2685877.5353 | 1251236.4753
42 | 2685818.8943 | 1251245.4312 | 2685807.0381 | 1251227.6386
43 | 2685874.8283 | 1251268.7454 | 2685888.3801 | 1251289.2374 | 2685896.4467 | 1251301.4395
44 | 2685901.1056 | 1251220.6591 | 2685890.7053 | 1251227.6379
45 | 2685925.766 | 1251203.6037 | 2685928.4238 | 1251201.9483
46 | 2685925.766 | 1251203.6037 | 2685924.4711 | 1251204.4078 | 2685917.5971 | 1251206.7988 | 2685913.1806 | 1251212.5502
47 | 2685925.766 | 1251203.6037 | 2685914.7141 | 1251186.7494
48 | 2685901.1056 | 1251220.6591 | 2685889.7018 | 1251201.0429
49 | 2685901.1056 | 1251220.6591 | 2685902.4279 | 1251219.7711
50 | 2685913.1806 | 1251212.5502 | 2685902.4279 | 1251219.7711
51 | 2685897.0358 | 1251302.3306 | 2685896.4467 | 1251301.4395
52 | 2686031.5062 | 1251260.3054 | 2686036.9912 | 1251268.5662 | 2686042.6763 | 1251277.1293
53 | 2685856.1493 | 1251335.9278 | 2685864.5793 | 1251358.9673 | 2685866.5902 | 1251362.9328 | 2685875.8723 | 1251377.178 | 2685875.8827 | 1251377.194
54 | 2685856.1493 | 1251335.9278 | 2685870.3022 | 1251329.9084
55 | 2685905.399 | 1251314.9813 | 2685870.3022 | 1251329.9084
56 | 2685951.4866 | 1251384.677 | 2685951.0046 | 1251383.948
57 | 2685951.0046 | 1251383.948 | 2685942.5705 | 1251371.1929
58 | 2686009.8908 | 1251227.7506 | 2686016.7553 | 1251238.0892
59 | 2686020.9614 | 1251244.424 | 2686016.7553 | 1251238.0892
60 | 2686020.9614 | 1251244.424 | 2686021.0386 | 1251244.5402
61 | 2685905.399 | 1251314.9813 | 2685897.0358 | 1251302.3306
62 | 2685905.399 | 1251314.9813 | 2685908.1037 | 1251319.0711
63 | 2685908.248 | 1251319.2892 | 2685908.1037 | 1251319.0711
64 | 2685918.3958 | 1251334.6339 | 2685908.248 | 1251319.2892
65 | 2685928.6264 | 1251350.1047 | 2685924.0799 | 1251343.2289 | 2685918.3958 | 1251334.6339
66 | 2685928.6264 | 1251350.1047 | 2685929.184 | 1251350.9479
67 | 2685929.8236 | 1251351.9152 | 2685929.184 | 1251350.9479
68 | 2685929.8236 | 1251351.9152 | 2685942.4971 | 1251371.0818
69 | 2685942.5705 | 1251371.1929 | 2685942.4971 | 1251371.0818
70 | 2686031.4949 | 1251260.2883 | 2686031.5062 | 1251260.3054
71 | 2686030.8788 | 1251259.3605 | 2686021.0386 | 1251244.5402
72 | 2686030.8788 | 1251259.3605 | 2686031.4949 | 1251260.2883

## bus_geodata
| x | y | coords
0 | 2686016.6381 | 1251108.5581
1 | 2686042.9867 | 1251117.2393
2 | 2686006.8549 | 1251123.1193
3 | 2685941.7897 | 1251106.5074
4 | 2685926.7748 | 1251148.6436
5 | 2685974.7236 | 1251174.792
6 | 2685952.8745 | 1251187.9739
7 | 2685987.8983 | 1251194.6311
8 | 2685941.8575 | 1251171.3722
9 | 2686013.2774 | 1251126.9459
10 | 2686120.4571 | 1251196.4908
11 | 2686089.2735 | 1251165.2698
12 | 2686080.1699 | 1251240.5499
13 | 2686073.8677 | 1251174.9637
14 | 2686064.4293 | 1251293.6168
15 | 2686056.6778 | 1251298.2189
16 | 2686054.1611 | 1251277.5352
17 | 2685996.9453 | 1251191.6062
18 | 2686010.507 | 1251211.6314
19 | 2685940.0987 | 1251194.6766
20 | 2686009.2916 | 1251226.8481
21 | 2685839.134 | 1251215.1811
22 | 2685849.6066 | 1251230.5982
23 | 2686041.1183 | 1251136.8517
24 | 2686061.5213 | 1251253.3684
25 | 2686060.3076 | 1251183.4962
26 | 2686042.6958 | 1251277.1588
27 | 2686058.6359 | 1251301.096
28 | 2686099.641 | 1251361.346
29 | 2686072.3405 | 1251321.2325
30 | 2686067.8357 | 1251382.0533
31 | 2686045.6821 | 1251264.2558
32 | 2686024.4086 | 1251232.1585
33 | 2685860.8789 | 1251247.6521
34 | 2685820.6406 | 1251244.5878
35 | 2685867.5688 | 1251257.768
36 | 2685877.5353 | 1251236.4753
37 | 2685818.8943 | 1251245.4312
38 | 2685874.8283 | 1251268.7454
39 | 2685890.7053 | 1251227.6379
40 | 2685807.0381 | 1251227.6386
41 | 2685928.4238 | 1251201.9483
42 | 2685925.766 | 1251203.6037
43 | 2685889.7018 | 1251201.0429
44 | 2685901.1056 | 1251220.6591
45 | 2685914.7141 | 1251186.7494
46 | 2685913.1806 | 1251212.5502
47 | 2685902.4279 | 1251219.7711
48 | 2685896.4467 | 1251301.4395
49 | 2686042.6763 | 1251277.1293
50 | 2686062.6328 | 1251306.9686
51 | 2685856.1493 | 1251335.9278
52 | 2685875.8827 | 1251377.194
53 | 2685870.3022 | 1251329.9084
54 | 2686052.0424 | 1251392.3358
55 | 2685951.4866 | 1251384.677
56 | 2685951.0046 | 1251383.948
57 | 2686009.8908 | 1251227.7506
58 | 2686016.7553 | 1251238.0892
59 | 2686020.9614 | 1251244.424
60 | 2685897.0358 | 1251302.3306
61 | 2685905.399 | 1251314.9813
62 | 2685908.1037 | 1251319.0711
63 | 2685908.248 | 1251319.2892
64 | 2685918.3958 | 1251334.6339
65 | 2685928.6264 | 1251350.1047
66 | 2685929.184 | 1251350.9479
67 | 2685929.8236 | 1251351.9152
68 | 2685942.4971 | 1251371.0818
69 | 2685942.5705 | 1251371.1929
70 | 2686031.5062 | 1251260.3054
71 | 2686021.0386 | 1251244.5402
72 | 2686030.8788 | 1251259.3605
73 | 2686031.4949 | 1251260.2883
74 | 2685974.7236 | 1251174.792

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9848 | -0.29136 | 0.0097605 | 0.0024462
1 | 0.98505 | -0.28649 | 0 | 0
2 | 0.98548 | -0.27798 | 0 | 0
3 | 0.9876 | -0.23672 | 0 | 0
4 | 0.9897 | -0.19607 | 0 | 0
5 | 0.99384 | -0.11672 | 0 | 0
6 | 0.99139 | -0.16353 | 0 | 0
7 | 0.99613 | -0.073186 | 0.002704 | 0.00067769
8 | 0.99055 | -0.17963 | 0.011647 | 0.0029191
9 | 0.98531 | -0.28128 | 0.01525 | 0.003822
10 | 0.98662 | -0.25756 | 0 | 0
11 | 0.98547 | -0.27989 | 0 | 0
12 | 0.98832 | -0.22441 | 0.0091931 | 0.002304
13 | 0.98509 | -0.28735 | 0.012307 | 0.0030845
14 | 0.99121 | -0.16855 | 0 | 0
15 | 0.99162 | -0.16057 | 0 | 0
16 | 0.99033 | -0.1855 | 0.0036684 | 0.00091939
17 | 0.9891 | -0.20932 | 0.0047682 | 0.001195
18 | 0.98921 | -0.20727 | 0.0020895 | 0.00052369
19 | 0.9903 | -0.1843 | 0.0024749 | 0.00062028
20 | 0.99989 | -0.0020098 | 0.0025095 | 0.00062895
21 | 0.98071 | -0.36968 | 0.011734 | 0.0029409
22 | 0.98091 | -0.36572 | 0 | 0
23 | 0.98507 | -0.28599 | 0.0088768 | 0.0022247
24 | 0.98899 | -0.21148 | 0.0059397 | 0.0014886
25 | 0.98493 | -0.29038 | 0.010519 | 0.0026364
26 | 0.99398 | -0.11511 | 0.0014671 | 0.0003677
27 | 0.99146 | -0.16376 | 0.0065598 | 0.001644
28 | 0.98958 | -0.20008 | 0 | 0
29 | 0.99069 | -0.17865 | 0.0052007 | 0.0013034
30 | 0.98872 | -0.21688 | 0.018282 | 0.0045818
31 | 0.98966 | -0.19849 | 0 | 0
32 | 0.98936 | -0.20424 | 0.0015266 | 0.00038261
33 | 0.98129 | -0.35814 | 0 | 0
34 | 0.98065 | -0.37083 | 0.0021175 | 0.00053069
35 | 0.98016 | -0.38025 | 0.014931 | 0.003742
36 | 0.98355 | -0.31427 | 0.0049306 | 0.0012357
37 | 0.98064 | -0.37106 | 0 | 0
38 | 0.97911 | -0.40073 | 0.00389 | 0.00097494
39 | 0.98541 | -0.27832 | 0.0035257 | 0.00088361
40 | 0.9805 | -0.37363 | 0.0066417 | 0.0016646
41 | 0.98928 | -0.20383 | 0.0027198 | 0.00068164
42 | 0.98905 | -0.20821 | 0 | 0
43 | 0.98675 | -0.25265 | 0.0084101 | 0.0021078
44 | 0.98692 | -0.24924 | 0 | 0
45 | 0.98882 | -0.21268 | 0.012453 | 0.003121
46 | 0.98798 | -0.22889 | 0.0025901 | 0.00064914
47 | 0.98712 | -0.2453 | 0.0038777 | 0.00097185
48 | 0.97612 | -0.45919 | 0.0026742 | 0.00067023
49 | 0.99398 | -0.11504 | 0.00296 | 0.00074185
50 | 0.99116 | -0.16945 | 0.015077 | 0.0037787
51 | 0.97367 | -0.50742 | 0 | 0
52 | 0.97298 | -0.52102 | 0.016069 | 0.0040272
53 | 0.9739 | -0.50288 | 0.013763 | 0.0034494
54 | 0.9886 | -0.21908 | 0.0065598 | 0.001644
55 | 0.9726 | -0.52861 | 0.0094794 | 0.0023758
56 | 0.97261 | -0.52846 | 0.0082324 | 0.0020632
57 | 1 | 0 | -0.33562 | -0.085606
58 | 0.99868 | -0.025171 | 0.0011262 | 0.00028224
59 | 0.99788 | -0.040476 | 0.0022752 | 0.00057023
60 | 0.97604 | -0.46074 | 0.0025902 | 0.00064915
61 | 0.97496 | -0.48199 | 0 | 0
62 | 0.97475 | -0.48619 | 0.0025975 | 0.00065099
63 | 0.97474 | -0.4864 | 0.0022676 | 0.00056832
64 | 0.97402 | -0.50053 | 0.0027751 | 0.00069551
65 | 0.97335 | -0.51384 | 0.013728 | 0.0034406
66 | 0.97332 | -0.51432 | 0.0014139 | 0.00035436
67 | 0.9733 | -0.51483 | 0.0035749 | 0.00089595
68 | 0.97286 | -0.52342 | 0.0013074 | 0.00032765
69 | 0.97286 | -0.52347 | 0.0013102 | 0.00032836
70 | 0.99595 | -0.077308 | 0.0011789 | 0.00029545
71 | 0.99786 | -0.040752 | 0.0025575 | 0.00064098
72 | 0.99606 | -0.075147 | 0.0017566 | 0.00044025
73 | 0.99595 | -0.07727 | 0.0011838 | 0.00029668
74 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0097605 | -0.0024462 | 0.0097627 | 0.0024473 | 2.2627e-06 | 1.0951e-06 | 0.014748 | 0.014748 | 0.014748 | 0.9848 | -0.29136 | 0.98505 | -0.28649 | 4.0516
1 | -0.0097627 | -0.0024473 | 0.0097667 | 0.0024492 | 3.9612e-06 | 1.9166e-06 | 0.014748 | 0.014748 | 0.014748 | 0.98505 | -0.28649 | 0.98548 | -0.27798 | 4.0516
2 | 0.024132 | 0.0060499 | -0.024129 | -0.0060476 | 3.7982e-06 | 2.3337e-06 | 0.036439 | 0.036439 | 0.036439 | 0.98548 | -0.27798 | 0.98531 | -0.28128 | 10.0107
3 | -0.033899 | -0.0084991 | 0.033966 | 0.008541 | 6.6798e-05 | 4.1882e-05 | 0.051187 | 0.051186 | 0.051187 | 0.98548 | -0.27798 | 0.9876 | -0.23672 | 14.0622
4 | -0.033966 | -0.008541 | 0.034032 | 0.0085824 | 6.607e-05 | 4.1422e-05 | 0.051186 | 0.051186 | 0.051186 | 0.9876 | -0.23672 | 0.9897 | -0.19607 | 14.0621
5 | -0.034032 | -0.0085824 | 0.034059 | 0.0085992 | 2.68e-05 | 1.6801e-05 | 0.051186 | 0.051186 | 0.051186 | 0.9897 | -0.19607 | 0.99055 | -0.17963 | 14.0621
6 | 0.21023 | 0.053697 | -0.20976 | -0.053394 | 0.00047458 | 0.00030307 | 0.31513 | 0.31513 | 0.31513 | 0.99384 | -0.11672 | 0.99139 | -0.16353 | 43.2868
7 | -0.21023 | -0.053697 | 0.21068 | 0.05398 | 0.00044343 | 0.00028318 | 0.31513 | 0.31513 | 0.31513 | 0.99384 | -0.11672 | 0.99613 | -0.073186 | 43.2867
8 | 0.16402 | 0.041853 | -0.16385 | -0.041748 | 0.0001644 | 0.00010485 | 0.24645 | 0.24645 | 0.24645 | 0.99139 | -0.16353 | 0.9903 | -0.1843 | 33.8524
9 | 0.045741 | 0.011541 | -0.045706 | -0.011518 | 3.5246e-05 | 2.2301e-05 | 0.068682 | 0.068683 | 0.068683 | 0.99139 | -0.16353 | 0.99055 | -0.17963 | 18.8688
10 | -0.21338 | -0.054658 | 0.21412 | 0.055129 | 0.00073866 | 0.00047173 | 0.31917 | 0.31917 | 0.31917 | 0.99613 | -0.073186 | 0.99989 | -0.0020098 | 43.8415
11 | 0.0088788 | 0.0022256 | -0.0088768 | -0.0022247 | 1.9924e-06 | 8.9887e-07 | 0.013409 | 0.013409 | 0.013409 | 0.98531 | -0.28128 | 0.98507 | -0.28599 | 3.6838
12 | 0.022861 | 0.0057415 | -0.022836 | -0.0057267 | 2.4336e-05 | 1.4879e-05 | 0.034483 | 0.034483 | 0.034483 | 0.98662 | -0.25756 | 0.98547 | -0.27989 | 9.4734
13 | -0.022861 | -0.0057415 | 0.022897 | 0.0057637 | 3.6221e-05 | 2.2142e-05 | 0.034483 | 0.034483 | 0.034483 | 0.98662 | -0.25756 | 0.98832 | -0.22441 | 9.4733
14 | 0.022836 | 0.0057267 | -0.022828 | -0.0057217 | 8.1164e-06 | 4.9627e-06 | 0.034483 | 0.034483 | 0.034483 | 0.98547 | -0.27989 | 0.98509 | -0.28735 | 9.4734
15 | -0.03209 | -0.0080677 | 0.03211 | 0.0080801 | 1.9816e-05 | 1.2392e-05 | 0.048324 | 0.048324 | 0.048324 | 0.98832 | -0.22441 | 0.98899 | -0.21148 | 13.2757
16 | 0.010521 | 0.0026372 | -0.010519 | -0.0026364 | 1.5174e-06 | 7.6721e-07 | 0.015892 | 0.015892 | 0.015892 | 0.98509 | -0.28735 | 0.98493 | -0.29038 | 4.366
17 | -0.050199 | -0.01265 | 0.050219 | 0.012662 | 1.9171e-05 | 1.2153e-05 | 0.075384 | 0.075384 | 0.075384 | 0.99121 | -0.16855 | 0.99162 | -0.16057 | 20.71
18 | 0.050199 | 0.01265 | -0.050159 | -0.012624 | 4.0661e-05 | 2.5777e-05 | 0.075384 | 0.075384 | 0.075384 | 0.99121 | -0.16855 | 0.99033 | -0.1855 | 20.71
19 | -0.10198 | -0.025663 | 0.1022 | 0.025805 | 0.00022209 | 0.00014181 | 0.15306 | 0.15306 | 0.15306 | 0.99162 | -0.16057 | 0.99398 | -0.11511 | 42.0502
20 | 0.051758 | 0.013001 | -0.051751 | -0.012996 | 7.8749e-06 | 4.995e-06 | 0.077678 | 0.077678 | 0.077678 | 0.99162 | -0.16057 | 0.99146 | -0.16376 | 21.3402
21 | 0.04649 | 0.011704 | -0.046461 | -0.011686 | 2.8845e-05 | 1.8258e-05 | 0.069872 | 0.069873 | 0.069873 | 0.99033 | -0.1855 | 0.98966 | -0.19849 | 19.1958
22 | -0.0047682 | -0.001195 | 0.0047687 | 0.001195 | 4.6668e-07 | -1.1772e-08 | 0.0071734 | 0.0071733 | 0.0071734 | 0.9891 | -0.20932 | 0.98921 | -0.20727 | 1.9707
23 | -0.0068582 | -0.0017187 | 0.0068592 | 0.001719 | 9.8944e-07 | 3.1493e-07 | 0.010316 | 0.010316 | 0.010316 | 0.98921 | -0.20727 | 0.98936 | -0.20424 | 2.8342
24 | 0.16138 | 0.041128 | -0.16122 | -0.041031 | 0.00015194 | 9.6889e-05 | 0.24273 | 0.24273 | 0.24273 | 0.9903 | -0.1843 | 0.98928 | -0.20383 | 33.3416
25 | -0.21663 | -0.055758 | 0.21665 | 0.055772 | 2.1178e-05 | 1.3526e-05 | 0.3229 | 0.3229 | 0.3229 | 0.99989 | -0.0020098 | 1 | 0 | 44.3545
26 | -0.011734 | -0.0029409 | 0.011736 | 0.0029421 | 2.2155e-06 | 1.1827e-06 | 0.017804 | 0.017804 | 0.017804 | 0.98071 | -0.36968 | 0.98091 | -0.36572 | 4.8913
27 | -0.020499 | -0.0051386 | 0.020506 | 0.005143 | 7.4065e-06 | 4.4822e-06 | 0.031096 | 0.031096 | 0.031096 | 0.98091 | -0.36572 | 0.98129 | -0.35814 | 8.543
28 | 0.0087622 | 0.0021965 | -0.0087601 | -0.0021955 | 2.1313e-06 | 9.581e-07 | 0.013292 | 0.013292 | 0.013292 | 0.98091 | -0.36572 | 0.98065 | -0.37083 | 3.6518
29 | -0.03805 | -0.0095687 | 0.038073 | 0.0095836 | 2.3632e-05 | 1.4878e-05 | 0.05726 | 0.05726 | 0.05726 | 0.98899 | -0.21148 | 0.98966 | -0.19849 | 15.7309
30 | -0.10367 | -0.026172 | 0.10367 | 0.026173 | 3.2017e-07 | 2.0445e-07 | 0.15526 | 0.15526 | 0.15526 | 0.99398 | -0.11511 | 0.99398 | -0.11504 | 42.6536
31 | 0.045191 | 0.011352 | -0.045178 | -0.011344 | 1.2258e-05 | 7.7532e-06 | 0.067833 | 0.067833 | 0.067833 | 0.99146 | -0.16376 | 0.99116 | -0.16945 | 18.6355
32 | -0.024862 | -0.0062383 | 0.024887 | 0.0062539 | 2.5434e-05 | 1.5653e-05 | 0.037387 | 0.037387 | 0.037387 | 0.98958 | -0.20008 | 0.99069 | -0.17865 | 10.2711
33 | 0.024862 | 0.0062383 | -0.024842 | -0.006226 | 1.9893e-05 | 1.2245e-05 | 0.037387 | 0.037387 | 0.037387 | 0.98958 | -0.20008 | 0.98872 | -0.21688 | 10.2712
34 | -0.030088 | -0.0075573 | 0.030101 | 0.0075656 | 1.3218e-05 | 8.2372e-06 | 0.045198 | 0.045198 | 0.045198 | 0.99069 | -0.17865 | 0.99116 | -0.16945 | 12.4171
35 | 0.0065605 | 0.0016442 | -0.0065598 | -0.001644 | 6.8895e-07 | 1.9926e-07 | 0.0098735 | 0.0098736 | 0.0098736 | 0.98872 | -0.21688 | 0.9886 | -0.21908 | 2.7125
36 | 0.0083882 | 0.0021026 | -0.0083859 | -0.0021016 | 2.2972e-06 | 9.7552e-07 | 0.012612 | 0.012612 | 0.012612 | 0.98966 | -0.19849 | 0.98936 | -0.20424 | 3.465
37 | 0.10123 | 0.025611 | -0.10112 | -0.025542 | 0.00010728 | 6.8509e-05 | 0.15359 | 0.15359 | 0.15359 | 0.98129 | -0.35814 | 0.98016 | -0.38025 | 42.1947
38 | -0.12174 | -0.030754 | 0.12199 | 0.030918 | 0.00025657 | 0.00016395 | 0.18468 | 0.18468 | 0.18468 | 0.98129 | -0.35814 | 0.98355 | -0.31427 | 50.7376
39 | 0.0066426 | 0.0016648 | -0.0066425 | -0.0016648 | 7.3883e-08 | 2.2818e-08 | 0.010079 | 0.010079 | 0.010079 | 0.98065 | -0.37083 | 0.98064 | -0.37106 | 2.7691
40 | 0.086191 | 0.0218 | -0.086107 | -0.021746 | 8.4593e-05 | 5.3974e-05 | 0.13092 | 0.13092 | 0.13092 | 0.98016 | -0.38025 | 0.97911 | -0.40073 | 35.9675
41 | -0.12692 | -0.032153 | 0.12714 | 0.032294 | 0.00021958 | 0.00014033 | 0.19214 | 0.19214 | 0.19214 | 0.98355 | -0.31427 | 0.98541 | -0.27832 | 52.7869
42 | 0.0066425 | 0.0016648 | -0.0066417 | -0.0016646 | 8.1457e-07 | 2.5162e-07 | 0.010079 | 0.010079 | 0.010079 | 0.98064 | -0.37106 | 0.9805 | -0.37363 | 2.7691
43 | 0.082217 | 0.020771 | -0.081987 | -0.020625 | 0.00022969 | 0.00014651 | 0.12501 | 0.12501 | 0.12501 | 0.97911 | -0.40073 | 0.97612 | -0.45919 | 34.3434
44 | -0.13067 | -0.033177 | 0.13085 | 0.033294 | 0.00018315 | 0.00011705 | 0.19747 | 0.19747 | 0.19747 | 0.98541 | -0.27832 | 0.98692 | -0.24924 | 54.2494
45 | 0.1585 | 0.040349 | -0.15847 | -0.040328 | 3.3433e-05 | 2.1317e-05 | 0.23864 | 0.23864 | 0.23864 | 0.98928 | -0.20383 | 0.98905 | -0.20821 | 32.7797
46 | 0.14602 | 0.037206 | -0.14587 | -0.037113 | 0.00014555 | 9.2741e-05 | 0.2199 | 0.2199 | 0.2199 | 0.98905 | -0.20821 | 0.98798 | -0.22889 | 30.2056
47 | 0.012456 | 0.0031225 | -0.012453 | -0.003121 | 2.6542e-06 | 1.4401e-06 | 0.01874 | 0.01874 | 0.01874 | 0.98905 | -0.20821 | 0.98882 | -0.21268 | 5.1483
48 | -0.0084101 | -0.0021078 | 0.0084115 | 0.0021084 | 1.3686e-06 | 5.8601e-07 | 0.012683 | 0.012682 | 0.012683 | 0.98675 | -0.25265 | 0.98692 | -0.24924 | 3.4842
49 | -0.13926 | -0.035403 | 0.13929 | 0.03542 | 2.6379e-05 | 1.6862e-05 | 0.21015 | 0.21015 | 0.21015 | 0.98692 | -0.24924 | 0.98712 | -0.2453 | 57.7336
50 | 0.14328 | 0.036464 | -0.14317 | -0.036392 | 0.0001133 | 7.2182e-05 | 0.216 | 0.216 | 0.216 | 0.98798 | -0.22889 | 0.98712 | -0.2453 | 29.6697
51 | 0.079313 | 0.019955 | -0.079307 | -0.019951 | 5.8585e-06 | 3.7361e-06 | 0.12093 | 0.12093 | 0.12093 | 0.97612 | -0.45919 | 0.97604 | -0.46074 | 33.2234
52 | -0.10663 | -0.026914 | 0.10682 | 0.027038 | 0.00019312 | 0.00012333 | 0.15969 | 0.15969 | 0.15969 | 0.99398 | -0.11504 | 0.99595 | -0.077308 | 43.8709
53 | 0.016079 | 0.0040333 | -0.016069 | -0.0040272 | 1.0417e-05 | 6.0955e-06 | 0.024574 | 0.024574 | 0.024574 | 0.97367 | -0.50742 | 0.97298 | -0.52102 | 6.7512
54 | -0.016079 | -0.0040333 | 0.016083 | 0.0040353 | 3.4829e-06 | 2.0377e-06 | 0.024574 | 0.024574 | 0.024574 | 0.97367 | -0.50742 | 0.9739 | -0.50288 | 6.7512
55 | -0.029846 | -0.0074847 | 0.029876 | 0.0075033 | 2.9743e-05 | 1.8561e-05 | 0.045603 | 0.045603 | 0.045603 | 0.9739 | -0.50288 | 0.97496 | -0.48199 | 12.5283
56 | -0.0094794 | -0.0023758 | 0.0094794 | 0.0023758 | 6.8938e-08 | 3.3273e-08 | 0.014503 | 0.014503 | 0.014503 | 0.9726 | -0.52861 | 0.97261 | -0.52846 | 3.9843
57 | -0.017712 | -0.004439 | 0.017716 | 0.0044415 | 4.2106e-06 | 2.505e-06 | 0.027098 | 0.027098 | 0.027098 | 0.97261 | -0.52846 | 0.97286 | -0.52347 | 7.4445
58 | 0.11732 | 0.029834 | -0.11718 | -0.029744 | 0.00014208 | 9.0768e-05 | 0.17473 | 0.17473 | 0.17473 | 1 | 0 | 0.99868 | -0.025171 | 48.0024
59 | 0.11605 | 0.029461 | -0.11597 | -0.029407 | 8.5392e-05 | 5.4552e-05 | 0.17305 | 0.17305 | 0.17305 | 0.99868 | -0.025171 | 0.99788 | -0.040476 | 47.5414
60 | 0.11369 | 0.028837 | -0.11369 | -0.028836 | 1.5064e-06 | 9.6226e-07 | 0.16966 | 0.16966 | 0.16966 | 0.99788 | -0.040476 | 0.99786 | -0.040752 | 46.6093
61 | 0.076717 | 0.019302 | -0.076639 | -0.019252 | 7.7828e-05 | 4.962e-05 | 0.11698 | 0.11698 | 0.11698 | 0.97604 | -0.46074 | 0.97496 | -0.48199 | 32.1386
62 | 0.046763 | 0.011749 | -0.046754 | -0.011743 | 9.369e-06 | 5.935e-06 | 0.071382 | 0.071382 | 0.071382 | 0.97496 | -0.48199 | 0.97475 | -0.48619 | 19.6104
63 | 0.044156 | 0.011092 | -0.044156 | -0.011092 | 4.4567e-07 | 2.8197e-07 | 0.067417 | 0.067417 | 0.067417 | 0.97475 | -0.48619 | 0.97474 | -0.4864 | 18.521
64 | 0.041888 | 0.010523 | -0.04186 | -0.010505 | 2.8217e-05 | 1.783e-05 | 0.063955 | 0.063955 | 0.063955 | 0.97474 | -0.4864 | 0.97402 | -0.50053 | 17.5701
65 | 0.039085 | 0.0098099 | -0.03906 | -0.0097943 | 2.4802e-05 | 1.5643e-05 | 0.059715 | 0.059716 | 0.059716 | 0.97402 | -0.50053 | 0.97335 | -0.51384 | 16.4054
66 | 0.025332 | 0.0063536 | -0.025331 | -0.0063533 | 5.686e-07 | 3.5134e-07 | 0.038728 | 0.038728 | 0.038728 | 0.97335 | -0.51384 | 0.97332 | -0.51432 | 10.6396
67 | 0.023917 | 0.0059989 | -0.023917 | -0.0059986 | 5.8146e-07 | 3.5772e-07 | 0.036567 | 0.036567 | 0.036567 | 0.97332 | -0.51432 | 0.9733 | -0.51483 | 10.0458
68 | 0.020342 | 0.0051026 | -0.020334 | -0.0050976 | 8.3348e-06 | 5.0488e-06 | 0.031101 | 0.031101 | 0.031101 | 0.9733 | -0.51483 | 0.97286 | -0.52342 | 8.5443
69 | 0.019026 | 0.0047699 | -0.019026 | -0.0047699 | 4.2291e-08 | 2.5413e-08 | 0.029102 | 0.029102 | 0.029102 | 0.97286 | -0.52342 | 0.97286 | -0.52347 | 7.995
70 | -0.108 | -0.027333 | 0.108 | 0.027333 | 2.0066e-07 | 1.2816e-07 | 0.16145 | 0.16145 | 0.16145 | 0.99595 | -0.077308 | 0.99595 | -0.07727 | 44.3548
71 | 0.11113 | 0.028195 | -0.11095 | -0.028077 | 0.00018348 | 0.0001172 | 0.16584 | 0.16584 | 0.16584 | 0.99786 | -0.040752 | 0.99606 | -0.075147 | 45.5616
72 | 0.10919 | 0.027637 | -0.10918 | -0.02763 | 1.1126e-05 | 7.1063e-06 | 0.16322 | 0.16322 | 0.16322 | 0.99606 | -0.075147 | 0.99595 | -0.07727 | 44.8407

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.33795 | 0.086189

## res_load
| p_mw | q_mvar
0 | 0.0097605 | 0.0024462
1 | 0.002704 | 0.00067769
2 | 0.011647 | 0.0029191
3 | 0.01525 | 0.003822
4 | 0.0091931 | 0.002304
5 | 0.012307 | 0.0030845
6 | 0.0036684 | 0.00091939
7 | 0.0047682 | 0.001195
8 | 0.0020895 | 0.00052369
9 | 0.0024749 | 0.00062028
10 | 0.0025095 | 0.00062895
11 | 0.011734 | 0.0029409
12 | 0.0088768 | 0.0022247
13 | 0.0059397 | 0.0014886
14 | 0.010519 | 0.0026364
15 | 0.0014671 | 0.0003677
16 | 0.0065598 | 0.001644
17 | 0.0052007 | 0.0013034
18 | 0.018282 | 0.0045818
19 | 0.0015266 | 0.00038261
20 | 0.0021175 | 0.00053069
21 | 0.014931 | 0.003742
22 | 0.0049306 | 0.0012357
23 | 0.00389 | 0.00097494
24 | 0.0035257 | 0.00088361
25 | 0.0066417 | 0.0016646
26 | 0.0027198 | 0.00068164
27 | 0.0084101 | 0.0021078
28 | 0.012453 | 0.003121
29 | 0.0025901 | 0.00064914
30 | 0.0038777 | 0.00097185
31 | 0.0026742 | 0.00067023
32 | 0.00296 | 0.00074185
33 | 0.015077 | 0.0037787
34 | 0.016069 | 0.0040272
35 | 0.013763 | 0.0034494
36 | 0.0065598 | 0.001644
37 | 0.0094794 | 0.0023758
38 | 0.0082324 | 0.0020632
39 | 0.0023269 | 0.00058316
40 | 0.0011262 | 0.00028224
41 | 0.0022752 | 0.00057023
42 | 0.0025902 | 0.00064915
43 | 0.0025975 | 0.00065099
44 | 0.0022676 | 0.00056832
45 | 0.0027751 | 0.00069551
46 | 0.013728 | 0.0034406
47 | 0.0014139 | 0.00035436
48 | 0.0035749 | 0.00089595
49 | 0.0013074 | 0.00032765
50 | 0.0013102 | 0.00032836
51 | 0.0011789 | 0.00029545
52 | 0.0025575 | 0.00064098
53 | 0.0017566 | 0.00044025
54 | 0.0011838 | 0.00029668

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1