## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-356_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-356_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-356_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_261-356_0_4_node_41 | 0.4 | n |  | TRUE
4 | bus_LV_261-356_0_4_node_30 | 0.4 | n |  | TRUE
5 | bus_LV_261-356_0_4_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_261-356_0_4_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_261-356_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_261-356_0_4_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_261-356_0_4_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_261-356_0_4_node_19 | 0.4 | n |  | TRUE
11 | bus_LV_261-356_0_4_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_261-356_0_4_node_22 | 0.4 | n |  | TRUE
13 | bus_LV_261-356_0_4_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_261-356_0_4_node_13 | 0.4 | n |  | TRUE
15 | bus_LV_261-356_0_4_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_261-356_0_4_node_20 | 0.4 | n |  | TRUE
17 | bus_LV_261-356_0_4_node_45 | 0.4 | n |  | TRUE
18 | bus_LV_261-356_0_4_node_21 | 0.4 | n |  | TRUE
19 | bus_LV_261-356_0_4_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_261-356_0_4_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_261-356_0_4_node_40 | 0.4 | n |  | TRUE
22 | bus_LV_261-356_0_4_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_261-356_0_4_node_37 | 0.4 | n |  | TRUE
24 | bus_LV_261-356_0_4_node_27 | 0.4 | n |  | TRUE
25 | bus_LV_261-356_0_4_node_36 | 0.4 | n |  | TRUE
26 | bus_LV_261-356_0_4_node_33 | 0.4 | n |  | TRUE
27 | bus_LV_261-356_0_4_node_11 | 0.4 | n |  | TRUE
28 | bus_LV_261-356_0_4_node_12 | 0.4 | n |  | TRUE
29 | bus_LV_261-356_0_4_node_44 | 0.4 | n |  | TRUE
30 | bus_LV_261-356_0_4_node_35 | 0.4 | n |  | TRUE
31 | bus_LV_261-356_0_4_node_34 | 0.4 | n |  | TRUE
32 | bus_LV_261-356_0_4_node_32 | 0.4 | n |  | TRUE
33 | bus_LV_261-356_0_4_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_261-356_0_4_node_38 | 0.4 | n |  | TRUE
35 | bus_LV_261-356_0_4_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_261-356_0_4_node_24 | 0.4 | n |  | TRUE
37 | bus_LV_261-356_0_4_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_261-356_0_4_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_261-356_0_4_node_26 | 0.4 | n |  | TRUE
40 | bus_LV_261-356_0_4_node_39 | 0.4 | n |  | TRUE
41 | bus_LV_261-356_0_4_node_29 | 0.4 | n |  | TRUE
42 | bus_LV_261-356_0_4_node_42 | 0.4 | n |  | TRUE
43 | bus_LV_261-356_0_4_node_43 | 0.4 | n |  | TRUE
44 | bus_MV_533_0_node_7 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-356_0_4_load_0 | 0 | 0.0021226 | 0.00053198 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-356_0_4_load_41 | 3 | 0.0013327 | 0.00033402 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-356_0_4_load_4 | 5 | 0.0072759 | 0.0018235 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-356_0_4_load_5 | 6 | 0.0054001 | 0.0013534 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-356_0_4_load_6 | 7 | 0.033596 | 0.00842 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-356_0_4_load_7 | 8 | 0.0049553 | 0.0012419 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-356_0_4_load_8 | 9 | 0.0062145 | 0.0015575 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-356_0_4_load_10 | 13 | 0.033503 | 0.0083967 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-356_0_4_load_45 | 17 | 0.012433 | 0.003116 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-356_0_4_load_21 | 18 | 0.012149 | 0.0030449 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-356_0_4_load_40 | 21 | 0.011242 | 0.0028174 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-356_0_4_load_37 | 23 | 0.01212 | 0.0030374 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-356_0_4_load_27 | 24 | 0.011678 | 0.0029267 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-356_0_4_load_36 | 25 | 0.045478 | 0.011398 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-356_0_4_load_33 | 26 | 0.014677 | 0.0036783 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-356_0_4_load_11 | 27 | 0.036248 | 0.0090845 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-356_0_4_load_12 | 28 | 0.049336 | 0.012365 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-356_0_4_load_44 | 29 | 0.012241 | 0.003068 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-356_0_4_load_35 | 30 | 0.0055715 | 0.0013963 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-356_0_4_load_34 | 31 | 0.0058968 | 0.0014779 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-356_0_4_load_32 | 32 | 0.0032165 | 0.00080613 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-356_0_4_load_31 | 33 | 0.0083958 | 0.0021042 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-356_0_4_load_28 | 35 | 0.0070048 | 0.0017556 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-356_0_4_load_24 | 36 | 0.0054879 | 0.0013754 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-356_0_4_load_23 | 37 | 0.013435 | 0.003367 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-356_0_4_load_25 | 38 | 0.0063133 | 0.0015823 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-356_0_4_load_26 | 39 | 0.0062799 | 0.0015739 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-356_0_4_load_29 | 41 | 0.008397 | 0.0021045 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-356_0_4_load_42 | 42 | 0.034393 | 0.0086197 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-356_0_4_load_43 | 43 | 0.045192 | 0.011326 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 43 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-356_0_4_line_0 |  | 0 | 1 | 0.0081599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-356_0_4_line_1 |  | 1 | 2 | 0.18593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-356_0_4_line_2 |  | 2 | 3 | 0.027287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-356_0_4_line_3 |  | 3 | 4 | 0.024464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-356_0_4_line_4 |  | 4 | 22 | 0.056389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-356_0_4_line_5 |  | 5 | 6 | 0.033757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-356_0_4_line_6 |  | 5 | 7 | 0.037169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-356_0_4_line_7 |  | 6 | 8 | 0.0033598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-356_0_4_line_8 |  | 7 | 9 | 0.003301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-356_0_4_line_9 |  | 8 | 10 | 0.047507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-356_0_4_line_10 |  | 9 | 11 | 0.0077292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-356_0_4_line_11 |  | 10 | 12 | 0.082998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-356_0_4_line_12 |  | 11 | 13 | 0.022873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-356_0_4_line_13 |  | 12 | 36 | 0.045603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-356_0_4_line_14 |  | 13 | 27 | 0.0031698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-356_0_4_line_15 |  | 14 | 15 | 0.009378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_261-356_0_4_line_16 |  | 14 | 16 | 0.029196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-356_0_4_line_17 |  | 14 | 17 | 0.013601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_261-356_0_4_line_18 |  | 15 | 18 | 0.013291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_261-356_0_4_line_19 |  | 16 | 25 | 0.043598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-356_0_4_line_20 |  | 16 | 26 | 0.01528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-356_0_4_line_21 |  | 17 | 29 | 0.00030868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_261-356_0_4_line_22 |  | 18 | 28 | 0.018186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_261-356_0_4_line_23 |  | 19 | 20 | 0.012239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-356_0_4_line_24 |  | 19 | 21 | 0.045846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-356_0_4_line_25 |  | 20 | 24 | 0.040203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-356_0_4_line_26 |  | 21 | 22 | 0.016438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-356_0_4_line_27 |  | 22 | 23 | 0.030035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-356_0_4_line_28 |  | 23 | 34 | 0.020378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-356_0_4_line_29 |  | 24 | 35 | 0.025906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-356_0_4_line_30 |  | 26 | 31 | 0.017312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-356_0_4_line_31 |  | 27 | 28 | 0.030579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
32 | LV_261-356_0_4_line_32 |  | 29 | 43 | 0.046859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_261-356_0_4_line_33 |  | 30 | 31 | 0.012205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-356_0_4_line_34 |  | 32 | 33 | 0.016206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-356_0_4_line_35 |  | 33 | 41 | 0.020868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-356_0_4_line_36 |  | 34 | 40 | 0.013185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-356_0_4_line_37 |  | 35 | 41 | 0.029261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-356_0_4_line_38 |  | 36 | 37 | 0.036998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-356_0_4_line_39 |  | 37 | 38 | 0.037357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-356_0_4_line_40 |  | 38 | 39 | 0.011684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-356_0_4_line_41 |  | 40 | 42 | 0.043083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-356_0_4_line_42 |  | 42 | 43 | 0.036107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-356_0_4_trafo_43 | 0.63 MVA 20/0.4 kV | 44 | 43 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2680783.2568 | 1247598.7605 | 2680788.9888 | 1247604.5681
1 | 2680783.2568 | 1247598.7605 | 2680783.1056 | 1247594.889 | 2680791.4246 | 1247587.4858 | 2680795.3091 | 1247587.8834 | 2680810.2438 | 1247575.5668 | 2680833.2305 | 1247557.7003 | 2680862.3185 | 1247521.159 | 2680859.3707 | 1247517.9832 | 2680850.069 | 1247508.2715 | 2680821.504 | 1247478.2158 | 2680812.8057 | 1247469.1128
2 | 2680812.8057 | 1247469.1128 | 2680832.5541 | 1247450.2827
3 | 2680850.267 | 1247433.4084 | 2680847.9636 | 1247435.5897 | 2680832.5541 | 1247450.2827
4 | 2680850.267 | 1247433.4084 | 2680869.6959 | 1247415.0488 | 2680871.6395 | 1247413.2184 | 2680878.8166 | 1247407.0339 | 2680889.4717 | 1247401.7198 | 2680888.4744 | 1247396.2022
5 | 2680692.8545 | 1247305.9765 | 2680665.3209 | 1247325.5062
6 | 2680692.8545 | 1247305.9765 | 2680714.6562 | 1247290.5125 | 2680723.1499 | 1247284.443
7 | 2680665.3209 | 1247325.5062 | 2680662.5805 | 1247327.45
8 | 2680725.8356 | 1247282.5238 | 2680723.1499 | 1247284.443
9 | 2680624.0159 | 1247355.1935 | 2680655.2548 | 1247332.6462 | 2680662.5805 | 1247327.45
10 | 2680732.1242 | 1247278.03 | 2680725.8356 | 1247282.5238
11 | 2680676.7878 | 1247419.3802 | 2680624.0159 | 1247355.1935
12 | 2680732.1242 | 1247278.03 | 2680750.64 | 1247264.6016
13 | 2680676.7878 | 1247419.3802 | 2680696.9829 | 1247405.1779 | 2680713.9683 | 1247392.9758
14 | 2680753.2059 | 1247262.7407 | 2680750.64 | 1247264.6016
15 | 2680811.107 | 1247220.875 | 2680803.4414 | 1247226.3079
16 | 2680811.107 | 1247220.875 | 2680834.9512 | 1247203.932
17 | 2680811.107 | 1247220.875 | 2680815.0973 | 1247226.8337 | 2680818.7396 | 1247232.1317
18 | 2680803.4414 | 1247226.3079 | 2680792.6819 | 1247234.1111
19 | 2680834.9512 | 1247203.932 | 2680838.6218 | 1247209.5083 | 2680850.3578 | 1247224.1012 | 2680858.4441 | 1247233.7852 | 2680861.1106 | 1247236.0009 | 2680863.1343 | 1247236.6067
20 | 2680834.9512 | 1247203.932 | 2680847.4161 | 1247195.0944
21 | 2680818.9144 | 1247232.3861 | 2680818.7396 | 1247232.1317
22 | 2680792.6819 | 1247234.1111 | 2680777.96 | 1247244.788
23 | 2680938.7888 | 1247360.2401 | 2680939.5553 | 1247357.7599 | 2680939.8096 | 1247355.1837 | 2680939.5426 | 1247352.6115 | 2680939.0745 | 1247348.1685
24 | 2680938.7888 | 1247360.2401 | 2680937.2797 | 1247362.8881 | 2680935.1795 | 1247365.1167 | 2680932.6186 | 1247366.794 | 2680902.5084 | 1247387.733
25 | 2680939.0745 | 1247348.1685 | 2680934.8636 | 1247308.1868
26 | 2680888.4744 | 1247396.2022 | 2680894.7632 | 1247393.119 | 2680902.5084 | 1247387.733
27 | 2680888.4744 | 1247396.2022 | 2680887.4978 | 1247390.8294 | 2680871.0855 | 1247372.5399
28 | 2680857.4756 | 1247357.3733 | 2680871.0855 | 1247372.5399
29 | 2680934.8636 | 1247308.1868 | 2680932.1502 | 1247282.4231
30 | 2680847.4161 | 1247195.0944 | 2680861.539 | 1247185.0811
31 | 2680753.2059 | 1247262.7407 | 2680777.96 | 1247244.788
32 | 2680842.587 | 1247272.5968 | 2680832.9381 | 1247257.9329 | 2680827.8874 | 1247245.5439 | 2680822.6596 | 1247237.8337 | 2680818.9144 | 1247232.3861
33 | 2680871.4956 | 1247178.0218 | 2680861.539 | 1247185.0811
34 | 2680925.2022 | 1247216.4531 | 2680926.8997 | 1247232.5703
35 | 2680926.8997 | 1247232.5703 | 2680929.0854 | 1247253.3232
36 | 2680849.3004 | 1247347.0099 | 2680857.4756 | 1247357.3733
37 | 2680932.1502 | 1247282.4231 | 2680929.0854 | 1247253.3232
38 | 2680713.9683 | 1247392.9758 | 2680744.0168 | 1247371.3895
39 | 2680774.3566 | 1247349.5939 | 2680744.0168 | 1247371.3895
40 | 2680774.3566 | 1247349.5939 | 2680779.0093 | 1247346.2515 | 2680784.9645 | 1247346.2308
41 | 2680849.3004 | 1247347.0099 | 2680847.0415 | 1247343.7211 | 2680844.8501 | 1247338.2428 | 2680844.9863 | 1247333.241 | 2680849.2995 | 1247314.4083 | 2680851.4643 | 1247305.8082
42 | 2680851.4643 | 1247305.8082 | 2680851.9271 | 1247303.9698 | 2680853.3141 | 1247296.4276 | 2680853.331 | 1247293.5258 | 2680852.6378 | 1247290.6364 | 2680845.4076 | 1247276.8834 | 2680842.587 | 1247272.5968

## bus_geodata
| x | y | coords
0 | 2680788.9888 | 1247604.5681
1 | 2680783.2568 | 1247598.7605
2 | 2680812.8057 | 1247469.1128
3 | 2680832.5541 | 1247450.2827
4 | 2680850.267 | 1247433.4084
5 | 2680692.8545 | 1247305.9765
6 | 2680665.3209 | 1247325.5062
7 | 2680723.1499 | 1247284.443
8 | 2680662.5805 | 1247327.45
9 | 2680725.8356 | 1247282.5238
10 | 2680624.0159 | 1247355.1935
11 | 2680732.1242 | 1247278.03
12 | 2680676.7878 | 1247419.3802
13 | 2680750.64 | 1247264.6016
14 | 2680811.107 | 1247220.875
15 | 2680803.4414 | 1247226.3079
16 | 2680834.9512 | 1247203.932
17 | 2680818.7396 | 1247232.1317
18 | 2680792.6819 | 1247234.1111
19 | 2680938.7888 | 1247360.2401
20 | 2680939.0745 | 1247348.1685
21 | 2680902.5084 | 1247387.733
22 | 2680888.4744 | 1247396.2022
23 | 2680871.0855 | 1247372.5399
24 | 2680934.8636 | 1247308.1868
25 | 2680863.1343 | 1247236.6067
26 | 2680847.4161 | 1247195.0944
27 | 2680753.2059 | 1247262.7407
28 | 2680777.96 | 1247244.788
29 | 2680818.9144 | 1247232.386
30 | 2680871.4956 | 1247178.0218
31 | 2680861.539 | 1247185.0811
32 | 2680925.2022 | 1247216.4531
33 | 2680926.8997 | 1247232.5703
34 | 2680857.4756 | 1247357.3733
35 | 2680932.1502 | 1247282.4231
36 | 2680713.9683 | 1247392.9758
37 | 2680744.0168 | 1247371.3895
38 | 2680774.3566 | 1247349.5939
39 | 2680784.9645 | 1247346.2308
40 | 2680849.3004 | 1247347.0099
41 | 2680929.0854 | 1247253.3232
42 | 2680851.4643 | 1247305.8082
43 | 2680842.587 | 1247272.5968
44 | 2680811.107 | 1247220.875

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98993 | -0.19341 | 0.0021226 | 0.00053198
1 | 0.98994 | -0.1931 | 0 | 0
2 | 0.9903 | -0.18607 | 0 | 0
3 | 0.99036 | -0.18504 | 0.0013327 | 0.00033402
4 | 0.99043 | -0.18354 | 0 | 0
5 | 0.98448 | -0.29851 | 0.0072759 | 0.0018235
6 | 0.98317 | -0.32397 | 0.0054001 | 0.0013534
7 | 0.98617 | -0.26571 | 0.033596 | 0.00842
8 | 0.98306 | -0.32618 | 0.0049553 | 0.0012419
9 | 0.98643 | -0.26081 | 0.0062145 | 0.0015575
10 | 0.98167 | -0.35322 | 0 | 0
11 | 0.98706 | -0.2485 | 0 | 0
12 | 0.97924 | -0.40066 | 0 | 0
13 | 0.98894 | -0.21217 | 0.033503 | 0.0083967
14 | 0.99422 | -0.11041 | 0 | 0
15 | 0.99359 | -0.12256 | 0 | 0
16 | 0.99231 | -0.14736 | 0 | 0
17 | 0.99543 | -0.087113 | 0.012433 | 0.003116
18 | 0.99269 | -0.1398 | 0.012149 | 0.0030449
19 | 0.98822 | -0.22627 | 0 | 0
20 | 0.98779 | -0.23472 | 0 | 0
21 | 0.98986 | -0.19466 | 0.011242 | 0.0028174
22 | 0.99061 | -0.18007 | 0 | 0
23 | 0.99209 | -0.15162 | 0.01212 | 0.0030374
24 | 0.98636 | -0.26255 | 0.011678 | 0.0029267
25 | 0.99049 | -0.18252 | 0.045478 | 0.011398
26 | 0.99194 | -0.15443 | 0.014677 | 0.0036783
27 | 0.9893 | -0.20525 | 0.036248 | 0.0090845
28 | 0.99153 | -0.16213 | 0.049336 | 0.012365
29 | 0.99546 | -0.086562 | 0.012241 | 0.003068
30 | 0.9917 | -0.15916 | 0.0055715 | 0.0013963
31 | 0.99176 | -0.15795 | 0.0058968 | 0.0014779
32 | 0.9849 | -0.2909 | 0.0032165 | 0.00080613
33 | 0.98495 | -0.28996 | 0.0083958 | 0.0021042
34 | 0.99331 | -0.128 | 0 | 0
35 | 0.98571 | -0.2751 | 0.0070048 | 0.0017556
36 | 0.97791 | -0.42682 | 0.0054879 | 0.0013754
37 | 0.97701 | -0.44439 | 0.013435 | 0.003367
38 | 0.97657 | -0.45299 | 0.0063133 | 0.0015823
39 | 0.97651 | -0.45433 | 0.0062799 | 0.0015739
40 | 0.9941 | -0.11275 | 0 | 0
41 | 0.98518 | -0.28561 | 0.008397 | 0.0021045
42 | 0.9967 | -0.063091 | 0.034393 | 0.0086197
43 | 1 | 0 | -0.42222 | -0.10701
44 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0021226 | -0.00053198 | 0.0021227 | 0.00053189 | 3.115e-08 | -8.4971e-08 | 0.0031906 | 0.0031906 | 0.0031906 | 0.98993 | -0.19341 | 0.98994 | -0.1931 | 0.87655
1 | -0.0021227 | -0.00053189 | 0.0021234 | 0.00052996 | 7.0959e-07 | -1.9372e-06 | 0.0031906 | 0.0031898 | 0.0031906 | 0.98994 | -0.1931 | 0.9903 | -0.18607 | 0.87654
2 | -0.0021234 | -0.00052996 | 0.0021235 | 0.00052967 | 1.0411e-07 | -2.8446e-07 | 0.0031898 | 0.0031896 | 0.0031898 | 0.9903 | -0.18607 | 0.99036 | -0.18504 | 0.87631
3 | -0.0034562 | -0.00086369 | 0.0034564 | 0.00086353 | 2.473e-07 | -1.5654e-07 | 0.0051921 | 0.005192 | 0.0051921 | 0.99036 | -0.18504 | 0.99043 | -0.18354 | 1.4264
4 | -0.0034564 | -0.00086353 | 0.003457 | 0.00086317 | 5.6999e-07 | -3.6103e-07 | 0.005192 | 0.0051917 | 0.005192 | 0.99043 | -0.18354 | 0.99061 | -0.18007 | 1.4264
5 | 0.042106 | 0.01064 | -0.042055 | -0.010608 | 5.1322e-05 | 3.2418e-05 | 0.063673 | 0.063673 | 0.063673 | 0.98448 | -0.29851 | 0.98317 | -0.32397 | 17.4927
6 | -0.049382 | -0.012464 | 0.04946 | 0.012513 | 7.7715e-05 | 4.9264e-05 | 0.074671 | 0.07467 | 0.074671 | 0.98448 | -0.29851 | 0.98617 | -0.26571 | 20.5139
7 | 0.036654 | 0.0092546 | -0.036651 | -0.0092521 | 3.8809e-06 | 2.4412e-06 | 0.0555 | 0.0555 | 0.0555 | 0.98317 | -0.32397 | 0.98306 | -0.32618 | 15.2474
8 | -0.083056 | -0.020933 | 0.083075 | 0.020946 | 1.9454e-05 | 1.2409e-05 | 0.12536 | 0.12536 | 0.12536 | 0.98617 | -0.26571 | 0.98643 | -0.26081 | 34.4404
9 | 0.031695 | 0.0080102 | -0.031654 | -0.0079845 | 4.1046e-05 | 2.5668e-05 | 0.048 | 0.048 | 0.048 | 0.98306 | -0.32618 | 0.98167 | -0.35322 | 13.1868
10 | -0.08929 | -0.022503 | 0.089342 | 0.022537 | 5.2619e-05 | 3.3577e-05 | 0.13474 | 0.13474 | 0.13474 | 0.98643 | -0.26081 | 0.98706 | -0.2485 | 37.0158
11 | 0.031654 | 0.0079845 | -0.031583 | -0.0079397 | 7.1711e-05 | 4.4848e-05 | 0.048 | 0.048 | 0.048 | 0.98167 | -0.35322 | 0.97924 | -0.40066 | 13.1869
12 | -0.089342 | -0.022537 | 0.089498 | 0.022636 | 0.00015571 | 9.9363e-05 | 0.13474 | 0.13474 | 0.13474 | 0.98706 | -0.2485 | 0.98894 | -0.21217 | 37.0158
13 | 0.031583 | 0.0079397 | -0.031543 | -0.007915 | 3.9402e-05 | 2.4644e-05 | 0.048 | 0.048001 | 0.048001 | 0.97924 | -0.40066 | 0.97791 | -0.42682 | 13.187
14 | -0.123 | -0.031033 | 0.12304 | 0.031059 | 4.0747e-05 | 2.6037e-05 | 0.18515 | 0.18515 | 0.18515 | 0.98894 | -0.21217 | 0.9893 | -0.20525 | 50.8649
15 | 0.22164 | 0.056104 | -0.22151 | -0.056022 | 0.00012915 | 8.229e-05 | 0.33192 | 0.33192 | 0.33192 | 0.99422 | -0.11041 | 0.99359 | -0.12256 | 30.3956
16 | 0.071837 | 0.018086 | -0.071711 | -0.018005 | 0.00012663 | 8.0666e-05 | 0.10755 | 0.10755 | 0.10755 | 0.99422 | -0.11041 | 0.99231 | -0.14736 | 29.5455
17 | -0.29348 | -0.07419 | 0.29381 | 0.0744 | 0.00032833 | 0.0002096 | 0.43947 | 0.43947 | 0.43947 | 0.99422 | -0.11041 | 0.99543 | -0.087113 | 40.2441
18 | 0.22151 | 0.056022 | -0.22133 | -0.055906 | 0.00018304 | 0.00011663 | 0.33192 | 0.33192 | 0.33192 | 0.99359 | -0.12256 | 0.99269 | -0.1398 | 30.3956
19 | 0.045555 | 0.011446 | -0.045478 | -0.011398 | 7.6317e-05 | 4.8281e-05 | 0.068322 | 0.068322 | 0.068322 | 0.99231 | -0.14736 | 0.99049 | -0.18252 | 18.7699
20 | 0.026156 | 0.006559 | -0.026147 | -0.0065536 | 8.8156e-06 | 5.4446e-06 | 0.039224 | 0.039224 | 0.039224 | 0.99231 | -0.14736 | 0.99194 | -0.15443 | 10.7758
21 | -0.30624 | -0.077516 | 0.30625 | 0.077521 | 8.0956e-06 | 5.1691e-06 | 0.45805 | 0.45805 | 0.45805 | 0.99543 | -0.087113 | 0.99546 | -0.086562 | 41.946
22 | 0.20918 | 0.052861 | -0.20896 | -0.052718 | 0.00022372 | 0.00014247 | 0.31371 | 0.31371 | 0.31371 | 0.99269 | -0.1398 | 0.99153 | -0.16213 | 28.7279
23 | 0.038788 | 0.0097566 | -0.038772 | -0.0097467 | 1.5662e-05 | 9.8671e-06 | 0.058417 | 0.058417 | 0.058417 | 0.98822 | -0.22627 | 0.98779 | -0.23472 | 16.0486
24 | -0.038788 | -0.0097566 | 0.038846 | 0.0097935 | 5.867e-05 | 3.696e-05 | 0.058417 | 0.058417 | 0.058417 | 0.98822 | -0.22627 | 0.98986 | -0.19466 | 16.0486
25 | 0.038772 | 0.0097467 | -0.03872 | -0.0097143 | 5.1448e-05 | 3.2413e-05 | 0.058417 | 0.058417 | 0.058417 | 0.98779 | -0.23472 | 0.98636 | -0.26255 | 16.0487
26 | -0.050088 | -0.012611 | 0.050123 | 0.012633 | 3.4966e-05 | 2.2167e-05 | 0.075316 | 0.075316 | 0.075316 | 0.98986 | -0.19466 | 0.99061 | -0.18007 | 20.6911
27 | -0.05358 | -0.013496 | 0.053653 | 0.013543 | 7.3e-05 | 4.6333e-05 | 0.080507 | 0.080507 | 0.080507 | 0.99061 | -0.18007 | 0.99209 | -0.15162 | 22.1174
28 | -0.065772 | -0.01658 | 0.065847 | 0.016627 | 7.442e-05 | 4.7366e-05 | 0.098685 | 0.098685 | 0.098685 | 0.99209 | -0.15162 | 0.99331 | -0.128 | 27.1113
29 | 0.027043 | 0.0067876 | -0.027027 | -0.0067776 | 1.6172e-05 | 1.002e-05 | 0.0408 | 0.0408 | 0.0408 | 0.98636 | -0.26255 | 0.98571 | -0.2751 | 11.2089
30 | 0.011471 | 0.0028753 | -0.011469 | -0.0028743 | 1.9223e-06 | 1.0068e-06 | 0.017207 | 0.017207 | 0.017207 | 0.99194 | -0.15443 | 0.99176 | -0.15795 | 4.7273
31 | -0.15929 | -0.040143 | 0.15962 | 0.040353 | 0.00032934 | 0.00020999 | 0.23967 | 0.23967 | 0.23967 | 0.9893 | -0.20525 | 0.99153 | -0.16213 | 32.9215
32 | -0.31849 | -0.080589 | 0.31982 | 0.081438 | 0.0013291 | 0.00084878 | 0.47635 | 0.47635 | 0.47635 | 0.99546 | -0.086562 | 1 | 0 | 43.6217
33 | -0.0055715 | -0.0013963 | 0.0055718 | 0.0013964 | 3.1987e-07 | 4.723e-08 | 0.0083599 | 0.0083598 | 0.0083599 | 0.9917 | -0.15916 | 0.99176 | -0.15795 | 2.2967
34 | -0.0032165 | -0.00080613 | 0.0032166 | 0.00080601 | 1.4352e-07 | -1.144e-07 | 0.0048595 | 0.0048595 | 0.0048595 | 0.9849 | -0.2909 | 0.98495 | -0.28996 | 1.335
35 | -0.011612 | -0.0029102 | 0.011615 | 0.0029115 | 2.4084e-06 | 1.2757e-06 | 0.017543 | 0.017543 | 0.017543 | 0.98495 | -0.28996 | 0.98518 | -0.28561 | 4.8196
36 | -0.065847 | -0.016627 | 0.065895 | 0.016658 | 4.8152e-05 | 3.0646e-05 | 0.098685 | 0.098685 | 0.098685 | 0.99331 | -0.128 | 0.9941 | -0.11275 | 27.1113
37 | 0.020022 | 0.005022 | -0.020012 | -0.005016 | 1.0025e-05 | 6.0432e-06 | 0.030226 | 0.030226 | 0.030226 | 0.98571 | -0.2751 | 0.98518 | -0.28561 | 8.3039
38 | 0.026055 | 0.0065396 | -0.026033 | -0.0065261 | 2.1812e-05 | 1.3496e-05 | 0.03965 | 0.03965 | 0.03965 | 0.97791 | -0.42682 | 0.97701 | -0.44439 | 10.8929
39 | 0.012599 | 0.0031591 | -0.012594 | -0.0031563 | 5.1583e-06 | 2.8337e-06 | 0.019189 | 0.019189 | 0.019189 | 0.97701 | -0.44439 | 0.97657 | -0.45299 | 5.2717
40 | 0.0062803 | 0.001574 | -0.0062799 | -0.0015739 | 4.0122e-07 | 1.106e-07 | 0.0095693 | 0.0095694 | 0.0095694 | 0.97657 | -0.45299 | 0.97651 | -0.45433 | 2.6289
41 | -0.065895 | -0.016658 | 0.066052 | 0.016758 | 0.00015734 | 0.00010014 | 0.098685 | 0.098685 | 0.098685 | 0.9941 | -0.11275 | 0.9967 | -0.063091 | 27.1112
42 | -0.10045 | -0.025378 | 0.10075 | 0.025572 | 0.00030478 | 0.00019459 | 0.15003 | 0.15003 | 0.15003 | 0.9967 | -0.063091 | 1 | 0 | 41.2174

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.46741 | 0.11834

## res_load
| p_mw | q_mvar
0 | 0.0021226 | 0.00053198
1 | 0.0013327 | 0.00033402
2 | 0.0072759 | 0.0018235
3 | 0.0054001 | 0.0013534
4 | 0.033596 | 0.00842
5 | 0.0049553 | 0.0012419
6 | 0.0062145 | 0.0015575
7 | 0.033503 | 0.0083967
8 | 0.012433 | 0.003116
9 | 0.012149 | 0.0030449
10 | 0.011242 | 0.0028174
11 | 0.01212 | 0.0030374
12 | 0.011678 | 0.0029267
13 | 0.045478 | 0.011398
14 | 0.014677 | 0.0036783
15 | 0.036248 | 0.0090845
16 | 0.049336 | 0.012365
17 | 0.012241 | 0.003068
18 | 0.0055715 | 0.0013963
19 | 0.0058968 | 0.0014779
20 | 0.0032165 | 0.00080613
21 | 0.0083958 | 0.0021042
22 | 0.0070048 | 0.0017556
23 | 0.0054879 | 0.0013754
24 | 0.013435 | 0.003367
25 | 0.0063133 | 0.0015823
26 | 0.0062799 | 0.0015739
27 | 0.008397 | 0.0021045
28 | 0.034393 | 0.0086197
29 | 0.045192 | 0.011326

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1