## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-371_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-371_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-371_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-371_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-371_0_4_node_19 | 0.4 | n |  | TRUE
5 | bus_LV_261-371_0_4_node_46 | 0.4 | n |  | TRUE
6 | bus_LV_261-371_0_4_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_261-371_0_4_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_261-371_0_4_node_42 | 0.4 | n |  | TRUE
9 | bus_LV_261-371_0_4_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_261-371_0_4_node_50 | 0.4 | n |  | TRUE
11 | bus_LV_261-371_0_4_node_18 | 0.4 | n |  | TRUE
12 | bus_LV_261-371_0_4_node_21 | 0.4 | n |  | TRUE
13 | bus_LV_261-371_0_4_node_29 | 0.4 | n |  | TRUE
14 | bus_LV_261-371_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_261-371_0_4_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_261-371_0_4_node_25 | 0.4 | n |  | TRUE
17 | bus_LV_261-371_0_4_node_7 | 0.4 | n |  | TRUE
18 | bus_LV_261-371_0_4_node_51 | 0.4 | n |  | TRUE
19 | bus_LV_261-371_0_4_node_47 | 0.4 | n |  | TRUE
20 | bus_LV_261-371_0_4_node_5 | 0.4 | n |  | TRUE
21 | bus_LV_261-371_0_4_node_35 | 0.4 | n |  | TRUE
22 | bus_LV_261-371_0_4_node_33 | 0.4 | n |  | TRUE
23 | bus_LV_261-371_0_4_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_261-371_0_4_node_34 | 0.4 | n |  | TRUE
25 | bus_LV_261-371_0_4_node_30 | 0.4 | n |  | TRUE
26 | bus_LV_261-371_0_4_node_41 | 0.4 | n |  | TRUE
27 | bus_LV_261-371_0_4_node_45 | 0.4 | n |  | TRUE
28 | bus_LV_261-371_0_4_node_43 | 0.4 | n |  | TRUE
29 | bus_LV_261-371_0_4_node_6 | 0.4 | n |  | TRUE
30 | bus_LV_261-371_0_4_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_261-371_0_4_node_49 | 0.4 | n |  | TRUE
32 | bus_LV_261-371_0_4_node_37 | 0.4 | n |  | TRUE
33 | bus_LV_261-371_0_4_node_44 | 0.4 | n |  | TRUE
34 | bus_LV_261-371_0_4_node_40 | 0.4 | n |  | TRUE
35 | bus_LV_261-371_0_4_node_31 | 0.4 | n |  | TRUE
36 | bus_LV_261-371_0_4_node_36 | 0.4 | n |  | TRUE
37 | bus_LV_261-371_0_4_node_39 | 0.4 | n |  | TRUE
38 | bus_LV_261-371_0_4_node_38 | 0.4 | n |  | TRUE
39 | bus_LV_261-371_0_4_node_27 | 0.4 | n |  | TRUE
40 | bus_LV_261-371_0_4_node_48 | 0.4 | n |  | TRUE
41 | bus_LV_261-371_0_4_node_22 | 0.4 | n |  | TRUE
42 | bus_LV_261-371_0_4_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_261-371_0_4_node_26 | 0.4 | n |  | TRUE
44 | bus_LV_261-371_0_4_node_28 | 0.4 | n |  | TRUE
45 | bus_LV_261-371_0_4_node_32 | 0.4 | n |  | TRUE
46 | bus_MV_533_0_node_18 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-371_0_4_load_0 | 0 | 0.0081669 | 0.0020468 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-371_0_4_load_1 | 1 | 0.0048358 | 0.001212 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-371_0_4_load_2 | 2 | 0.0081434 | 0.0020409 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-371_0_4_load_46 | 5 | 0.0090559 | 0.0022696 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-371_0_4_load_42 | 8 | 0.0085638 | 0.0021463 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-371_0_4_load_50 | 10 | 0.0059404 | 0.0014888 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-371_0_4_load_29 | 13 | 0.0065202 | 0.0016341 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-371_0_4_load_25 | 16 | 0.018284 | 0.0045823 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-371_0_4_load_51 | 18 | 0.0083509 | 0.0020929 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-371_0_4_load_47 | 19 | 0.0045273 | 0.0011347 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-371_0_4_load_5 | 20 | 0.021836 | 0.0054725 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-371_0_4_load_35 | 21 | 0.0059704 | 0.0014963 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-371_0_4_load_33 | 22 | 0.0079602 | 0.001995 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-371_0_4_load_34 | 24 | 0.013381 | 0.0033536 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-371_0_4_load_30 | 25 | 0.017257 | 0.004325 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-371_0_4_load_41 | 26 | 0.010502 | 0.0026321 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-371_0_4_load_45 | 27 | 0.0049319 | 0.0012361 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-371_0_4_load_43 | 28 | 0.0081588 | 0.0020448 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-371_0_4_load_6 | 29 | 0.021003 | 0.0052638 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-371_0_4_load_23 | 30 | 0.024337 | 0.0060993 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-371_0_4_load_49 | 31 | 0.0084642 | 0.0021213 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-371_0_4_load_37 | 32 | 0.0088208 | 0.0022107 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-371_0_4_load_44 | 33 | 0.0083337 | 0.0020886 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-371_0_4_load_40 | 34 | 0.0091863 | 0.0023023 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-371_0_4_load_31 | 35 | 0.015483 | 0.0038804 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-371_0_4_load_36 | 36 | 0.017513 | 0.0043891 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-371_0_4_load_39 | 37 | 0.021355 | 0.0053521 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-371_0_4_load_38 | 38 | 0.017121 | 0.0042909 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-371_0_4_load_27 | 39 | 0.011019 | 0.0027617 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-371_0_4_load_48 | 40 | 0.0047441 | 0.001189 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-371_0_4_load_22 | 41 | 0.012559 | 0.0031477 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-371_0_4_load_24 | 42 | 0.028789 | 0.0072151 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-371_0_4_load_26 | 43 | 0.010408 | 0.0026085 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-371_0_4_load_28 | 44 | 0.0056499 | 0.001416 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-371_0_4_load_32 | 45 | 0.03167 | 0.0079371 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 22 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-371_0_4_line_0 |  | 0 | 1 | 0.015804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-371_0_4_line_1 |  | 0 | 2 | 0.019715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-371_0_4_line_2 |  | 1 | 3 | 0.018599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-371_0_4_line_3 |  | 3 | 4 | 0.011749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-371_0_4_line_4 |  | 3 | 5 | 0.012707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-371_0_4_line_5 |  | 4 | 9 | 0.004049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-371_0_4_line_6 |  | 4 | 10 | 0.0066104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-371_0_4_line_7 |  | 5 | 27 | 0.013522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-371_0_4_line_8 |  | 6 | 7 | 0.011974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-371_0_4_line_9 |  | 6 | 8 | 0.011177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-371_0_4_line_10 |  | 7 | 18 | 0.022341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-371_0_4_line_11 |  | 8 | 28 | 0.01832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-371_0_4_line_12 |  | 9 | 19 | 0.016416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-371_0_4_line_13 |  | 9 | 17 | 0.010751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-371_0_4_line_14 |  | 10 | 40 | 0.0146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-371_0_4_line_15 |  | 11 | 12 | 0.012668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-371_0_4_line_16 |  | 11 | 13 | 0.02231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-371_0_4_line_17 |  | 12 | 26 | 0.020887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-371_0_4_line_18 |  | 13 | 39 | 0.011186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_261-371_0_4_line_19 |  | 14 | 15 | 0.011868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_261-371_0_4_line_20 |  | 14 | 16 | 0.012594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_261-371_0_4_line_21 |  | 14 | 17 | 0.006546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-371_0_4_line_22 |  | 15 | 21 | 0.013409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-371_0_4_line_23 |  | 15 | 22 | 0.014976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_261-371_0_4_line_24 |  | 16 | 30 | 0.01185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_261-371_0_4_line_25 |  | 17 | 20 | 0.0066018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-371_0_4_line_26 |  | 18 | 31 | 0.020788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-371_0_4_line_27 |  | 20 | 29 | 0.012903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-371_0_4_line_28 |  | 21 | 32 | 0.012702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-371_0_4_line_29 |  | 23 | 24 | 0.016267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-371_0_4_line_30 |  | 23 | 25 | 0.011337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-371_0_4_line_31 |  | 24 | 34 | 0.015216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-371_0_4_line_32 |  | 25 | 35 | 0.022015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-371_0_4_line_33 |  | 26 | 34 | 0.012179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-371_0_4_line_34 |  | 27 | 33 | 0.012987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-371_0_4_line_35 |  | 30 | 41 | 0.014673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_261-371_0_4_line_36 |  | 31 | 40 | 0.016354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-371_0_4_line_37 |  | 32 | 36 | 0.01566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-371_0_4_line_38 |  | 35 | 45 | 0.0097068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-371_0_4_line_39 |  | 37 | 38 | 0.0036729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-371_0_4_line_40 |  | 38 | 45 | 0.0012408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-371_0_4_line_41 |  | 39 | 44 | 0.00036026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_261-371_0_4_line_42 |  | 41 | 42 | 0.0071805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_261-371_0_4_line_43 |  | 42 | 43 | 0.0072986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_261-371_0_4_line_44 |  | 43 | 44 | 0.013242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-371_0_4_trafo_33 | 0.63 MVA 20/0.4 kV | 46 | 22 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2681148.592 | 1247748.9291 | 2681160.0562 | 1247738.0511
1 | 2681148.592 | 1247748.9291 | 2681134.2908 | 1247762.4991
2 | 2681173.5481 | 1247725.249 | 2681160.0562 | 1247738.0511
3 | 2681165.4085 | 1247716.7758 | 2681169.0055 | 1247720.5167 | 2681173.5481 | 1247725.249
4 | 2681173.5481 | 1247725.249 | 2681175.1382 | 1247724.4035 | 2681176.9309 | 1247724.2168 | 2681178.3912 | 1247724.5815 | 2681179.6642 | 1247725.3884 | 2681180.6225 | 1247726.5579 | 2681184.0433 | 1247729.6025
5 | 2681165.2428 | 1247712.8818 | 2681165.7538 | 1247714.1787 | 2681165.7961 | 1247715.5024 | 2681165.4085 | 1247716.7758
6 | 2681165.4085 | 1247716.7758 | 2681160.5999 | 1247721.3118
7 | 2681194.1438 | 1247738.5922 | 2681184.0433 | 1247729.6025
8 | 2681106.7104 | 1247772.1466 | 2681114.7383 | 1247781.0518
9 | 2681114.7383 | 1247781.0518 | 2681122.2198 | 1247789.3559
10 | 2681106.7104 | 1247772.1466 | 2681122.9615 | 1247756.8168
11 | 2681122.2198 | 1247789.3559 | 2681134.4825 | 1247802.9669
12 | 2681165.2428 | 1247712.8818 | 2681164.3055 | 1247711.8349 | 2681153.0925 | 1247701.8547
13 | 2681165.2428 | 1247712.8818 | 2681169.442 | 1247709.0476 | 2681173.1897 | 1247705.6408
14 | 2681149.9793 | 1247731.3304 | 2681160.5999 | 1247721.3118
15 | 2681252.0209 | 1247634.6684 | 2681256.7243 | 1247638.6913 | 2681261.6441 | 1247642.9063
16 | 2681252.0209 | 1247634.6684 | 2681251.5568 | 1247635.4626 | 2681235.9998 | 1247650.1435
17 | 2681261.6441 | 1247642.9063 | 2681246.3876 | 1247657.1723
18 | 2681235.9998 | 1247650.1435 | 2681227.8641 | 1247657.8209
19 | 2681178.9912 | 1247703.9412 | 2681183.1435 | 1247708.4903 | 2681186.9984 | 1247712.7017
20 | 2681178.9912 | 1247703.9412 | 2681188.1505 | 1247695.2978
21 | 2681173.1897 | 1247705.6408 | 2681174.1216 | 1247705.9872 | 2681175.1095 | 1247706.1008 | 2681176.4876 | 1247705.8528 | 2681177.7056 | 1247705.1579 | 2681178.9912 | 1247703.9412
22 | 2681186.9984 | 1247712.7017 | 2681186.1043 | 1247714.0126 | 2681185.8109 | 1247715.5764 | 2681186.2191 | 1247717.2054 | 2681187.2889 | 1247718.5099 | 2681192.4092 | 1247723.0826
23 | 2681186.9984 | 1247712.7017 | 2681197.9383 | 1247702.4737
24 | 2681196.7691 | 1247687.1646 | 2681188.1505 | 1247695.2978
25 | 2681173.1897 | 1247705.6408 | 2681168.252 | 1247701.2588
26 | 2681138.083 | 1247742.5524 | 2681122.9615 | 1247756.8168
27 | 2681168.252 | 1247701.2588 | 2681158.601 | 1247692.6939
28 | 2681201.8829 | 1247731.5431 | 2681192.4092 | 1247723.0826
29 | 2681214.4968 | 1247686.9927 | 2681226.3784 | 1247675.8825
30 | 2681214.4968 | 1247686.9927 | 2681222.9311 | 1247694.568
31 | 2681237.4921 | 1247665.4903 | 2681226.3784 | 1247675.8825
32 | 2681239.3097 | 1247709.2782 | 2681222.9311 | 1247694.568
33 | 2681246.3876 | 1247657.1723 | 2681237.4921 | 1247665.4903
34 | 2681203.8446 | 1247747.2262 | 2681194.1438 | 1247738.5922
35 | 2681207.4408 | 1247677.094 | 2681196.7691 | 1247687.1646
36 | 2681149.9793 | 1247731.3304 | 2681138.083 | 1247742.5524
37 | 2681201.8829 | 1247731.5431 | 2681213.563 | 1247741.9739
38 | 2681246.5313 | 1247715.7643 | 2681239.3097 | 1247709.2782
39 | 2681247.4544 | 1247716.5934 | 2681250.187 | 1247719.0476
40 | 2681246.5313 | 1247715.7643 | 2681247.4544 | 1247716.5934
41 | 2681227.8641 | 1247657.8209 | 2681227.6021 | 1247658.0682
42 | 2681212.6631 | 1247672.1658 | 2681207.4408 | 1247677.094
43 | 2681212.6631 | 1247672.1658 | 2681217.9713 | 1247667.1566
44 | 2681227.6021 | 1247658.0682 | 2681217.9713 | 1247667.1566

## bus_geodata
| x | y | coords
0 | 2681148.592 | 1247748.9291
1 | 2681160.0562 | 1247738.0511
2 | 2681134.2908 | 1247762.4991
3 | 2681173.5481 | 1247725.249
4 | 2681165.4085 | 1247716.7758
5 | 2681184.0433 | 1247729.6025
6 | 2681114.7383 | 1247781.0518
7 | 2681106.7104 | 1247772.1466
8 | 2681122.2198 | 1247789.3559
9 | 2681165.2428 | 1247712.8818
10 | 2681160.5999 | 1247721.3118
11 | 2681252.0209 | 1247634.6684
12 | 2681261.6441 | 1247642.9063
13 | 2681235.9998 | 1247650.1435
14 | 2681178.9912 | 1247703.9412
15 | 2681186.9984 | 1247712.7017
16 | 2681188.1505 | 1247695.2978
17 | 2681173.1897 | 1247705.6408
18 | 2681122.9615 | 1247756.8168
19 | 2681153.0925 | 1247701.8547
20 | 2681168.252 | 1247701.2588
21 | 2681192.4092 | 1247723.0826
22 | 2681197.9383 | 1247702.4737
23 | 2681214.4968 | 1247686.9927
24 | 2681226.3784 | 1247675.8825
25 | 2681222.9311 | 1247694.568
26 | 2681246.3876 | 1247657.1723
27 | 2681194.1438 | 1247738.5922
28 | 2681134.4825 | 1247802.9669
29 | 2681158.601 | 1247692.6939
30 | 2681196.7691 | 1247687.1646
31 | 2681138.083 | 1247742.5524
32 | 2681201.8829 | 1247731.5431
33 | 2681203.8446 | 1247747.2262
34 | 2681237.4921 | 1247665.4903
35 | 2681239.3097 | 1247709.2782
36 | 2681213.563 | 1247741.9739
37 | 2681250.187 | 1247719.0476
38 | 2681247.4544 | 1247716.5934
39 | 2681227.8641 | 1247657.8209
40 | 2681149.9793 | 1247731.3304
41 | 2681207.4408 | 1247677.094
42 | 2681212.6631 | 1247672.1658
43 | 2681217.9713 | 1247667.1566
44 | 2681227.6021 | 1247658.0682
45 | 2681246.5313 | 1247715.7643
46 | 2681186.9984 | 1247712.7017

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99441 | -0.1073 | 0.0081669 | 0.0020468
1 | 0.99464 | -0.10275 | 0.0048358 | 0.001212
2 | 0.99426 | -0.11013 | 0.0081434 | 0.0020409
3 | 0.995 | -0.095826 | 0 | 0
4 | 0.99547 | -0.086839 | 0 | 0
5 | 0.99474 | -0.10082 | 0.0090559 | 0.0022696
6 | 0.99319 | -0.13082 | 0 | 0
7 | 0.99337 | -0.12729 | 0 | 0
8 | 0.99302 | -0.13413 | 0.0085638 | 0.0021463
9 | 0.99579 | -0.080595 | 0 | 0
10 | 0.9952 | -0.091982 | 0.0059404 | 0.0014888
11 | 0.99075 | -0.17652 | 0 | 0
12 | 0.98916 | -0.20715 | 0 | 0
13 | 0.99356 | -0.12281 | 0.0065202 | 0.0016341
14 | 0.9975 | -0.047683 | 0 | 0
15 | 0.99856 | -0.027507 | 0 | 0
16 | 0.99677 | -0.061676 | 0.018284 | 0.0045823
17 | 0.99669 | -0.063183 | 0 | 0
18 | 0.99371 | -0.12069 | 0.0083509 | 0.0020929
19 | 0.99572 | -0.081902 | 0.0045273 | 0.0011347
20 | 0.99644 | -0.068146 | 0.021836 | 0.0054725
21 | 0.99816 | -0.035082 | 0.0059704 | 0.0014963
22 | 1 | 0 | -0.42622 | -0.10783
23 | 0.98193 | -0.3473 | 0 | 0
24 | 0.98348 | -0.3171 | 0.013381 | 0.0033536
25 | 0.98085 | -0.36841 | 0.017257 | 0.004325
26 | 0.98653 | -0.25787 | 0.010502 | 0.0026321
27 | 0.99458 | -0.10398 | 0.0049319 | 0.0012361
28 | 0.99288 | -0.13677 | 0.0081588 | 0.0020448
29 | 0.99619 | -0.072905 | 0.021003 | 0.0052638
30 | 0.99612 | -0.07391 | 0.024337 | 0.0060993
31 | 0.99419 | -0.11149 | 0.0084642 | 0.0021213
32 | 0.99786 | -0.040935 | 0.0088208 | 0.0022107
33 | 0.99448 | -0.10589 | 0.0083337 | 0.0020886
34 | 0.98512 | -0.28527 | 0.0091863 | 0.0023023
35 | 0.9791 | -0.40263 | 0.015483 | 0.0038804
36 | 0.99761 | -0.045737 | 0.017513 | 0.0043891
37 | 0.97835 | -0.41731 | 0.021355 | 0.0053521
38 | 0.97842 | -0.41588 | 0.017121 | 0.0042909
39 | 0.9943 | -0.10875 | 0.011019 | 0.0027617
40 | 0.99469 | -0.10182 | 0.0047441 | 0.001189
41 | 0.99541 | -0.08751 | 0.012559 | 0.0031477
42 | 0.99508 | -0.093775 | 0.028789 | 0.0072151
43 | 0.9948 | -0.099223 | 0.010408 | 0.0026085
44 | 0.99431 | -0.10851 | 0.0056499 | 0.001416
45 | 0.97847 | -0.41501 | 0.03167 | 0.0079371
46 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.016311 | -0.0040882 | 0.016315 | 0.0040902 | 3.5307e-06 | 2.0546e-06 | 0.024408 | 0.024408 | 0.024408 | 0.99441 | -0.1073 | 0.99464 | -0.10275 | 6.7055
1 | 0.0081445 | 0.0020414 | -0.0081434 | -0.0020409 | 1.0981e-06 | 4.4706e-07 | 0.012187 | 0.012187 | 0.012187 | 0.99441 | -0.1073 | 0.99426 | -0.11013 | 3.3482
2 | -0.021151 | -0.0053022 | 0.021158 | 0.0053064 | 6.9834e-06 | 4.2279e-06 | 0.031643 | 0.031643 | 0.031643 | 0.99464 | -0.10275 | 0.995 | -0.095826 | 8.693
3 | -0.043487 | -0.010905 | 0.043506 | 0.010917 | 1.8637e-05 | 1.1775e-05 | 0.065037 | 0.065037 | 0.065037 | 0.995 | -0.095826 | 0.99547 | -0.086839 | 17.8674
4 | 0.02233 | 0.005599 | -0.022324 | -0.0055957 | 5.3142e-06 | 3.2361e-06 | 0.033395 | 0.033395 | 0.033395 | 0.995 | -0.095826 | 0.99474 | -0.10082 | 9.1744
5 | -0.087795 | -0.022042 | 0.087821 | 0.022058 | 2.6156e-05 | 1.6687e-05 | 0.13125 | 0.13125 | 0.13125 | 0.99547 | -0.086839 | 0.99579 | -0.080595 | 36.0575
6 | 0.044289 | 0.011124 | -0.044278 | -0.011118 | 1.0868e-05 | 6.8694e-06 | 0.066212 | 0.066212 | 0.066212 | 0.99547 | -0.086839 | 0.9952 | -0.091982 | 18.1901
7 | 0.013268 | 0.0033261 | -0.013266 | -0.003325 | 1.9976e-06 | 1.1029e-06 | 0.019848 | 0.019848 | 0.019848 | 0.99474 | -0.10082 | 0.99458 | -0.10398 | 5.4528
8 | -0.016726 | -0.0041931 | 0.016729 | 0.0041947 | 2.8199e-06 | 1.6498e-06 | 0.02506 | 0.02506 | 0.02506 | 0.99319 | -0.13082 | 0.99337 | -0.12729 | 6.8846
9 | 0.016726 | 0.0041931 | -0.016724 | -0.0041915 | 2.6323e-06 | 1.54e-06 | 0.02506 | 0.02506 | 0.02506 | 0.99319 | -0.13082 | 0.99302 | -0.13413 | 6.8847
10 | -0.016729 | -0.0041947 | 0.016734 | 0.0041978 | 5.2612e-06 | 3.0779e-06 | 0.02506 | 0.02506 | 0.02506 | 0.99337 | -0.12729 | 0.99371 | -0.12069 | 6.8846
11 | 0.0081599 | 0.0020452 | -0.0081588 | -0.0020448 | 1.0272e-06 | 4.2041e-07 | 0.012227 | 0.012228 | 0.012228 | 0.99302 | -0.13413 | 0.99288 | -0.13677 | 3.3592
12 | 0.0045276 | 0.0011346 | -0.0045273 | -0.0011347 | 2.8179e-07 | -3.3202e-08 | 0.0067656 | 0.0067657 | 0.0067657 | 0.99579 | -0.080595 | 0.99572 | -0.081902 | 1.8587
13 | -0.092349 | -0.023193 | 0.092426 | 0.023242 | 7.6795e-05 | 4.9009e-05 | 0.13801 | 0.13801 | 0.13801 | 0.99579 | -0.080595 | 0.99669 | -0.063183 | 37.9162
14 | 0.038338 | 0.0096288 | -0.03832 | -0.0096175 | 1.7995e-05 | 1.1327e-05 | 0.05733 | 0.05733 | 0.05733 | 0.9952 | -0.091982 | 0.99469 | -0.10182 | 15.7501
15 | 0.13727 | 0.034915 | -0.13707 | -0.034786 | 0.00020228 | 0.00012929 | 0.20635 | 0.20635 | 0.20635 | 0.99075 | -0.17652 | 0.98916 | -0.20715 | 56.6902
16 | -0.13727 | -0.034915 | 0.13763 | 0.035143 | 0.00035625 | 0.00022771 | 0.20635 | 0.20635 | 0.20635 | 0.99075 | -0.17652 | 0.99356 | -0.12281 | 56.6902
17 | 0.13707 | 0.034786 | -0.13674 | -0.034572 | 0.00033353 | 0.00021319 | 0.20635 | 0.20635 | 0.20635 | 0.98916 | -0.20715 | 0.98653 | -0.25787 | 56.6902
18 | -0.14415 | -0.036777 | 0.14425 | 0.036839 | 9.7963e-05 | 6.2407e-05 | 0.21612 | 0.21612 | 0.21612 | 0.99356 | -0.12281 | 0.9943 | -0.10875 | 29.6864
19 | -0.3913 | -0.099122 | 0.39168 | 0.099364 | 0.00037961 | 0.00024233 | 0.5841 | 0.5841 | 0.5841 | 0.9975 | -0.047683 | 0.99856 | -0.027507 | 40.1166
20 | 0.25592 | 0.06507 | -0.25575 | -0.064961 | 0.00017238 | 0.00010967 | 0.3821 | 0.3821 | 0.3821 | 0.9975 | -0.047683 | 0.99677 | -0.061676 | 26.2433
21 | 0.13538 | 0.034052 | -0.13528 | -0.033988 | 0.00010016 | 6.4016e-05 | 0.202 | 0.202 | 0.202 | 0.9975 | -0.047683 | 0.99669 | -0.063183 | 55.4931
22 | 0.032327 | 0.0081103 | -0.032315 | -0.008103 | 1.167e-05 | 7.2937e-06 | 0.048175 | 0.048175 | 0.048175 | 0.99856 | -0.027507 | 0.99816 | -0.035082 | 13.235
23 | -0.42401 | -0.10747 | 0.42457 | 0.10783 | 0.00056129 | 0.00035844 | 0.63227 | 0.63227 | 0.63227 | 0.99856 | -0.027507 | 1 | 0 | 43.4253
24 | 0.23747 | 0.060378 | -0.23733 | -0.06029 | 0.00013986 | 8.8891e-05 | 0.35481 | 0.35481 | 0.35481 | 0.99677 | -0.061676 | 0.99612 | -0.07391 | 24.3687
25 | 0.042853 | 0.010746 | -0.042843 | -0.010739 | 1.0134e-05 | 6.3998e-06 | 0.06398 | 0.06398 | 0.06398 | 0.99669 | -0.063183 | 0.99644 | -0.068146 | 17.577
26 | -0.025085 | -0.0062907 | 0.025096 | 0.0062975 | 1.1e-05 | 6.7707e-06 | 0.037565 | 0.037565 | 0.037565 | 0.99371 | -0.12069 | 0.99419 | -0.11149 | 10.32
27 | 0.021008 | 0.0052667 | -0.021003 | -0.0052638 | 4.7624e-06 | 2.8799e-06 | 0.031372 | 0.031372 | 0.031372 | 0.99644 | -0.068146 | 0.99619 | -0.072905 | 8.6187
28 | 0.026345 | 0.0066067 | -0.026337 | -0.0066021 | 7.3472e-06 | 4.5362e-06 | 0.039275 | 0.039275 | 0.039275 | 0.99816 | -0.035082 | 0.99786 | -0.040935 | 10.7898
29 | -0.10317 | -0.02597 | 0.10332 | 0.026065 | 0.00014919 | 9.5278e-05 | 0.15639 | 0.15639 | 0.15639 | 0.98193 | -0.3473 | 0.98348 | -0.3171 | 42.9643
30 | 0.10317 | 0.02597 | -0.10307 | -0.025903 | 0.00010398 | 6.6402e-05 | 0.15639 | 0.15639 | 0.15639 | 0.98193 | -0.3473 | 0.98085 | -0.36841 | 42.9643
31 | -0.1167 | -0.029418 | 0.11688 | 0.029532 | 0.00017802 | 0.00011374 | 0.17664 | 0.17664 | 0.17664 | 0.98348 | -0.3171 | 0.98512 | -0.28527 | 48.5263
32 | 0.085813 | 0.021578 | -0.085673 | -0.021489 | 0.00013997 | 8.9303e-05 | 0.13021 | 0.13021 | 0.13021 | 0.98085 | -0.36841 | 0.9791 | -0.40263 | 35.772
33 | 0.12623 | 0.03194 | -0.12607 | -0.031834 | 0.00016576 | 0.00010593 | 0.19051 | 0.19051 | 0.19051 | 0.98653 | -0.25787 | 0.98512 | -0.28527 | 52.3383
34 | 0.0083345 | 0.002089 | -0.0083337 | -0.0020886 | 7.5723e-07 | 3.1611e-07 | 0.01247 | 0.01247 | 0.01247 | 0.99458 | -0.10398 | 0.99448 | -0.10589 | 3.4257
35 | 0.21299 | 0.05419 | -0.21285 | -0.054102 | 0.00013951 | 8.852e-05 | 0.31845 | 0.31845 | 0.31845 | 0.99612 | -0.07391 | 0.99541 | -0.08751 | 21.8719
36 | -0.033561 | -0.0084188 | 0.033576 | 0.0084285 | 1.5475e-05 | 9.6921e-06 | 0.050233 | 0.050233 | 0.050233 | 0.99419 | -0.11149 | 0.99469 | -0.10182 | 13.8004
37 | 0.017517 | 0.0043914 | -0.017513 | -0.0043891 | 4.0069e-06 | 2.3599e-06 | 0.026121 | 0.026121 | 0.026121 | 0.99786 | -0.040935 | 0.99761 | -0.045737 | 7.1762
38 | 0.07019 | 0.017608 | -0.070149 | -0.017582 | 4.1426e-05 | 2.639e-05 | 0.10668 | 0.10668 | 0.10668 | 0.9791 | -0.40263 | 0.97847 | -0.41501 | 29.3076
39 | -0.021355 | -0.0053521 | 0.021356 | 0.005353 | 1.453e-06 | 8.838e-07 | 0.03248 | 0.03248 | 0.03248 | 0.97835 | -0.41731 | 0.97842 | -0.41588 | 8.923
40 | -0.038477 | -0.0096439 | 0.038479 | 0.0096449 | 1.5933e-06 | 1.0041e-06 | 0.058518 | 0.058518 | 0.058518 | 0.97842 | -0.41588 | 0.97847 | -0.41501 | 16.0763
41 | -0.15527 | -0.039601 | 0.15527 | 0.039602 | 1.8274e-06 | 1.1509e-06 | 0.23261 | 0.23261 | 0.23261 | 0.9943 | -0.10875 | 0.99431 | -0.10851 | 15.9758
42 | 0.20029 | 0.050954 | -0.20023 | -0.050916 | 6.0456e-05 | 3.8319e-05 | 0.29968 | 0.29968 | 0.29968 | 0.99541 | -0.08751 | 0.99508 | -0.093775 | 20.5825
43 | 0.17144 | 0.043701 | -0.1714 | -0.043672 | 4.5064e-05 | 2.8462e-05 | 0.25663 | 0.25663 | 0.25663 | 0.99508 | -0.093775 | 0.9948 | -0.099223 | 17.6258
44 | 0.16099 | 0.041064 | -0.16092 | -0.041018 | 7.2142e-05 | 4.5484e-05 | 0.24106 | 0.24106 | 0.24106 | 0.9948 | -0.099223 | 0.99431 | -0.10851 | 16.5565

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.43418 | 0.10983

## res_load
| p_mw | q_mvar
0 | 0.0081669 | 0.0020468
1 | 0.0048358 | 0.001212
2 | 0.0081434 | 0.0020409
3 | 0.0090559 | 0.0022696
4 | 0.0085638 | 0.0021463
5 | 0.0059404 | 0.0014888
6 | 0.0065202 | 0.0016341
7 | 0.018284 | 0.0045823
8 | 0.0083509 | 0.0020929
9 | 0.0045273 | 0.0011347
10 | 0.021836 | 0.0054725
11 | 0.0059704 | 0.0014963
12 | 0.0079602 | 0.001995
13 | 0.013381 | 0.0033536
14 | 0.017257 | 0.004325
15 | 0.010502 | 0.0026321
16 | 0.0049319 | 0.0012361
17 | 0.0081588 | 0.0020448
18 | 0.021003 | 0.0052638
19 | 0.024337 | 0.0060993
20 | 0.0084642 | 0.0021213
21 | 0.0088208 | 0.0022107
22 | 0.0083337 | 0.0020886
23 | 0.0091863 | 0.0023023
24 | 0.015483 | 0.0038804
25 | 0.017513 | 0.0043891
26 | 0.021355 | 0.0053521
27 | 0.017121 | 0.0042909
28 | 0.011019 | 0.0027617
29 | 0.0047441 | 0.001189
30 | 0.012559 | 0.0031477
31 | 0.028789 | 0.0072151
32 | 0.010408 | 0.0026085
33 | 0.0056499 | 0.001416
34 | 0.03167 | 0.0079371

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1