## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-383_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-383_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-383_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-383_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-383_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-383_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-383_0_5_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_261-383_0_5_node_12 | 0.4 | n |  | TRUE
8 | bus_LV_261-383_0_5_node_27 | 0.4 | n |  | TRUE
9 | bus_LV_261-383_0_5_node_146 | 0.4 | n |  | TRUE
10 | bus_LV_261-383_0_5_node_62 | 0.4 | n |  | TRUE
11 | bus_LV_261-383_0_5_node_64 | 0.4 | n |  | TRUE
12 | bus_LV_261-383_0_5_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_261-383_0_5_node_133 | 0.4 | n |  | TRUE
14 | bus_LV_261-383_0_5_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_261-383_0_5_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_261-383_0_5_node_105 | 0.4 | n |  | TRUE
17 | bus_LV_261-383_0_5_node_125 | 0.4 | n |  | TRUE
18 | bus_LV_261-383_0_5_node_8 | 0.4 | n |  | TRUE
19 | bus_LV_261-383_0_5_node_29 | 0.4 | n |  | TRUE
20 | bus_LV_261-383_0_5_node_129 | 0.4 | n |  | TRUE
21 | bus_LV_261-383_0_5_node_68 | 0.4 | n |  | TRUE
22 | bus_LV_261-383_0_5_node_63 | 0.4 | n |  | TRUE
23 | bus_LV_261-383_0_5_node_36 | 0.4 | n |  | TRUE
24 | bus_LV_261-383_0_5_node_37 | 0.4 | n |  | TRUE
25 | bus_LV_261-383_0_5_node_35 | 0.4 | n |  | TRUE
26 | bus_LV_261-383_0_5_node_11 | 0.4 | n |  | TRUE
27 | bus_LV_261-383_0_5_node_13 | 0.4 | n |  | TRUE
28 | bus_LV_261-383_0_5_node_148 | 0.4 | n |  | TRUE
29 | bus_LV_261-383_0_5_node_74 | 0.4 | n |  | TRUE
30 | bus_LV_261-383_0_5_node_118 | 0.4 | n |  | TRUE
31 | bus_LV_261-383_0_5_node_127 | 0.4 | n |  | TRUE
32 | bus_LV_261-383_0_5_node_14 | 0.4 | n |  | TRUE
33 | bus_LV_261-383_0_5_node_15 | 0.4 | n |  | TRUE
34 | bus_LV_261-383_0_5_node_16 | 0.4 | n |  | TRUE
35 | bus_LV_261-383_0_5_node_45 | 0.4 | n |  | TRUE
36 | bus_LV_261-383_0_5_node_94 | 0.4 | n |  | TRUE
37 | bus_LV_261-383_0_5_node_17 | 0.4 | n |  | TRUE
38 | bus_LV_261-383_0_5_node_131 | 0.4 | n |  | TRUE
39 | bus_LV_261-383_0_5_node_130 | 0.4 | n |  | TRUE
40 | bus_LV_261-383_0_5_node_18 | 0.4 | n |  | TRUE
41 | bus_LV_261-383_0_5_node_19 | 0.4 | n |  | TRUE
42 | bus_LV_261-383_0_5_node_132 | 0.4 | n |  | TRUE
43 | bus_LV_261-383_0_5_node_21 | 0.4 | n |  | TRUE
44 | bus_LV_261-383_0_5_node_80 | 0.4 | n |  | TRUE
45 | bus_LV_261-383_0_5_node_79 | 0.4 | n |  | TRUE
46 | bus_LV_261-383_0_5_node_22 | 0.4 | n |  | TRUE
47 | bus_LV_261-383_0_5_node_137 | 0.4 | n |  | TRUE
48 | bus_LV_261-383_0_5_node_28 | 0.4 | n |  | TRUE
49 | bus_LV_261-383_0_5_node_136 | 0.4 | n |  | TRUE
50 | bus_LV_261-383_0_5_node_24 | 0.4 | n |  | TRUE
51 | bus_LV_261-383_0_5_node_139 | 0.4 | n |  | TRUE
52 | bus_LV_261-383_0_5_node_60 | 0.4 | n |  | TRUE
53 | bus_LV_261-383_0_5_node_32 | 0.4 | n |  | TRUE
54 | bus_LV_261-383_0_5_node_122 | 0.4 | n |  | TRUE
55 | bus_LV_261-383_0_5_node_150 | 0.4 | n |  | TRUE
56 | bus_LV_261-383_0_5_node_145 | 0.4 | n |  | TRUE
57 | bus_LV_261-383_0_5_node_61 | 0.4 | n |  | TRUE
58 | bus_LV_261-383_0_5_node_65 | 0.4 | n |  | TRUE
59 | bus_LV_261-383_0_5_node_134 | 0.4 | n |  | TRUE
60 | bus_LV_261-383_0_5_node_104 | 0.4 | n |  | TRUE
61 | bus_LV_261-383_0_5_node_128 | 0.4 | n |  | TRUE
62 | bus_LV_261-383_0_5_node_42 | 0.4 | n |  | TRUE
63 | bus_LV_261-383_0_5_node_41 | 0.4 | n |  | TRUE
64 | bus_LV_261-383_0_5_node_71 | 0.4 | n |  | TRUE
65 | bus_LV_261-383_0_5_node_116 | 0.4 | n |  | TRUE
66 | bus_LV_261-383_0_5_node_126 | 0.4 | n |  | TRUE
67 | bus_LV_261-383_0_5_node_43 | 0.4 | n |  | TRUE
68 | bus_LV_261-383_0_5_node_92 | 0.4 | n |  | TRUE
69 | bus_LV_261-383_0_5_node_103 | 0.4 | n |  | TRUE
70 | bus_LV_261-383_0_5_node_78 | 0.4 | n |  | TRUE
71 | bus_LV_261-383_0_5_node_147 | 0.4 | n |  | TRUE
72 | bus_LV_261-383_0_5_node_101 | 0.4 | n |  | TRUE
73 | bus_LV_261-383_0_5_node_100 | 0.4 | n |  | TRUE
74 | bus_LV_261-383_0_5_node_140 | 0.4 | n |  | TRUE
75 | bus_LV_261-383_0_5_node_123 | 0.4 | n |  | TRUE
76 | bus_LV_261-383_0_5_node_58 | 0.4 | n |  | TRUE
77 | bus_LV_261-383_0_5_node_57 | 0.4 | n |  | TRUE
78 | bus_LV_261-383_0_5_node_38 | 0.4 | n |  | TRUE
79 | bus_LV_261-383_0_5_node_39 | 0.4 | n |  | TRUE
80 | bus_LV_261-383_0_5_node_135 | 0.4 | n |  | TRUE
81 | bus_LV_261-383_0_5_node_59 | 0.4 | n |  | TRUE
82 | bus_LV_261-383_0_5_node_40 | 0.4 | n |  | TRUE
83 | bus_LV_261-383_0_5_node_44 | 0.4 | n |  | TRUE
84 | bus_LV_261-383_0_5_node_46 | 0.4 | n |  | TRUE
85 | bus_LV_261-383_0_5_node_49 | 0.4 | n |  | TRUE
86 | bus_LV_261-383_0_5_node_47 | 0.4 | n |  | TRUE
87 | bus_LV_261-383_0_5_node_48 | 0.4 | n |  | TRUE
88 | bus_LV_261-383_0_5_node_50 | 0.4 | n |  | TRUE
89 | bus_LV_261-383_0_5_node_51 | 0.4 | n |  | TRUE
90 | bus_LV_261-383_0_5_node_52 | 0.4 | n |  | TRUE
91 | bus_LV_261-383_0_5_node_53 | 0.4 | n |  | TRUE
92 | bus_LV_261-383_0_5_node_56 | 0.4 | n |  | TRUE
93 | bus_LV_261-383_0_5_node_54 | 0.4 | n |  | TRUE
94 | bus_LV_261-383_0_5_node_55 | 0.4 | n |  | TRUE
95 | bus_LV_261-383_0_5_node_66 | 0.4 | n |  | TRUE
96 | bus_LV_261-383_0_5_node_67 | 0.4 | n |  | TRUE
97 | bus_LV_261-383_0_5_node_119 | 0.4 | n |  | TRUE
98 | bus_LV_261-383_0_5_node_120 | 0.4 | n |  | TRUE
99 | bus_LV_261-383_0_5_node_69 | 0.4 | n |  | TRUE
100 | bus_LV_261-383_0_5_node_70 | 0.4 | n |  | TRUE
101 | bus_LV_261-383_0_5_node_72 | 0.4 | n |  | TRUE
102 | bus_LV_261-383_0_5_node_73 | 0.4 | n |  | TRUE
103 | bus_LV_261-383_0_5_node_75 | 0.4 | n |  | TRUE
104 | bus_LV_261-383_0_5_node_83 | 0.4 | n |  | TRUE
105 | bus_LV_261-383_0_5_node_76 | 0.4 | n |  | TRUE
106 | bus_LV_261-383_0_5_node_84 | 0.4 | n |  | TRUE
107 | bus_LV_261-383_0_5_node_77 | 0.4 | n |  | TRUE
108 | bus_LV_261-383_0_5_node_82 | 0.4 | n |  | TRUE
109 | bus_LV_261-383_0_5_node_90 | 0.4 | n |  | TRUE
110 | bus_LV_261-383_0_5_node_89 | 0.4 | n |  | TRUE
111 | bus_LV_261-383_0_5_node_87 | 0.4 | n |  | TRUE
112 | bus_LV_261-383_0_5_node_85 | 0.4 | n |  | TRUE
113 | bus_LV_261-383_0_5_node_86 | 0.4 | n |  | TRUE
114 | bus_LV_261-383_0_5_node_88 | 0.4 | n |  | TRUE
115 | bus_LV_261-383_0_5_node_91 | 0.4 | n |  | TRUE
116 | bus_LV_261-383_0_5_node_93 | 0.4 | n |  | TRUE
117 | bus_LV_261-383_0_5_node_95 | 0.4 | n |  | TRUE
118 | bus_LV_261-383_0_5_node_96 | 0.4 | n |  | TRUE
119 | bus_LV_261-383_0_5_node_97 | 0.4 | n |  | TRUE
120 | bus_LV_261-383_0_5_node_98 | 0.4 | n |  | TRUE
121 | bus_LV_261-383_0_5_node_99 | 0.4 | n |  | TRUE
122 | bus_LV_261-383_0_5_node_106 | 0.4 | n |  | TRUE
123 | bus_LV_261-383_0_5_node_102 | 0.4 | n |  | TRUE
124 | bus_LV_261-383_0_5_node_107 | 0.4 | n |  | TRUE
125 | bus_LV_261-383_0_5_node_149 | 0.4 | n |  | TRUE
126 | bus_LV_261-383_0_5_node_108 | 0.4 | n |  | TRUE
127 | bus_LV_261-383_0_5_node_109 | 0.4 | n |  | TRUE
128 | bus_LV_261-383_0_5_node_113 | 0.4 | n |  | TRUE
129 | bus_LV_261-383_0_5_node_115 | 0.4 | n |  | TRUE
130 | bus_LV_261-383_0_5_node_111 | 0.4 | n |  | TRUE
131 | bus_LV_261-383_0_5_node_110 | 0.4 | n |  | TRUE
132 | bus_LV_261-383_0_5_node_112 | 0.4 | n |  | TRUE
133 | bus_LV_261-383_0_5_node_114 | 0.4 | n |  | TRUE
134 | bus_LV_261-383_0_5_node_117 | 0.4 | n |  | TRUE
135 | bus_LV_261-383_0_5_node_121 | 0.4 | n |  | TRUE
136 | bus_LV_261-383_0_5_node_124 | 0.4 | n |  | TRUE
137 | bus_LV_261-383_0_5_node_142 | 0.4 | n |  | TRUE
138 | bus_LV_261-383_0_5_node_144 | 0.4 | n |  | TRUE
139 | bus_LV_261-383_0_5_node_143 | 0.4 | n |  | TRUE
140 | bus_MV_528_0_node_16 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-383_0_5_load_0 | 0 | 0.0088053 | 0.0022068 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-383_0_5_load_1 | 1 | 0.0067785 | 0.0016989 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-383_0_5_load_146 | 9 | 0.0040708 | 0.0010202 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-383_0_5_load_64 | 11 | 0.0022709 | 0.00056914 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-383_0_5_load_133 | 13 | 0.0028462 | 0.00071331 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-383_0_5_load_105 | 16 | 0.0033683 | 0.00084418 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-383_0_5_load_125 | 17 | 0.0041446 | 0.0010387 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-383_0_5_load_129 | 20 | 0.0026409 | 0.00066186 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-383_0_5_load_68 | 21 | 0.0031862 | 0.00079854 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-383_0_5_load_63 | 22 | 0.0047598 | 0.0011929 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-383_0_5_load_37 | 24 | 0.0073237 | 0.0018355 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-383_0_5_load_35 | 25 | 0.0075602 | 0.0018948 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-383_0_5_load_148 | 28 | 0.0013355 | 0.00033471 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-383_0_5_load_74 | 29 | 0.0028327 | 0.00070994 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-383_0_5_load_118 | 30 | 0.0017922 | 0.00044918 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-383_0_5_load_127 | 31 | 0.0012002 | 0.0003008 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-383_0_5_load_45 | 35 | 0.049448 | 0.012393 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-383_0_5_load_94 | 36 | 0.002847 | 0.00071353 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-383_0_5_load_131 | 38 | 0.0026828 | 0.00067238 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-383_0_5_load_130 | 39 | 0.0025446 | 0.00063774 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-383_0_5_load_132 | 42 | 0.0026356 | 0.00066053 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-383_0_5_load_80 | 44 | 0.0013635 | 0.00034172 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-383_0_5_load_79 | 45 | 0.001664 | 0.00041703 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-383_0_5_load_136 | 49 | 0.0032341 | 0.00081055 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-383_0_5_load_139 | 51 | 0.011866 | 0.0029739 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-383_0_5_load_60 | 52 | 0.0031632 | 0.00079278 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-383_0_5_load_122 | 54 | 0.016494 | 0.0041337 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-383_0_5_load_150 | 55 | 0.039451 | 0.0098873 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-383_0_5_load_145 | 56 | 0.0057326 | 0.0014367 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-383_0_5_load_61 | 57 | 0.0041263 | 0.0010342 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-383_0_5_load_65 | 58 | 0.0024497 | 0.00061395 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-383_0_5_load_134 | 59 | 0.0032853 | 0.00082338 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-383_0_5_load_104 | 60 | 0.0029507 | 0.0007395 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-383_0_5_load_128 | 61 | 0.0027379 | 0.00068618 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-383_0_5_load_42 | 62 | 0.0066693 | 0.0016715 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-383_0_5_load_41 | 63 | 0.014788 | 0.0037061 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-383_0_5_load_116 | 65 | 0.0013209 | 0.00033104 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-383_0_5_load_126 | 66 | 0.0029445 | 0.00073795 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-383_0_5_load_43 | 67 | 0.023592 | 0.0059126 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-383_0_5_load_92 | 68 | 0.0036765 | 0.00092141 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-383_0_5_load_103 | 69 | 0.0028293 | 0.00070909 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-383_0_5_load_78 | 70 | 0.00148 | 0.00037092 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-383_0_5_load_147 | 71 | 0.0052222 | 0.0013088 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-383_0_5_load_101 | 72 | 0.0021579 | 0.00054083 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-383_0_5_load_123 | 75 | 0.0075607 | 0.0018949 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-383_0_5_load_58 | 76 | 0.0030155 | 0.00075575 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-383_0_5_load_38 | 78 | 0.0090751 | 0.0022744 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-383_0_5_load_39 | 79 | 0.0086517 | 0.0021683 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-383_0_5_load_135 | 80 | 0.0016644 | 0.00041714 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-383_0_5_load_59 | 81 | 0.0072717 | 0.0018225 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-383_0_5_load_40 | 82 | 0.0086805 | 0.0021755 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-383_0_5_load_44 | 83 | 0.0079583 | 0.0019945 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-383_0_5_load_46 | 84 | 0.0082857 | 0.0020766 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-383_0_5_load_49 | 85 | 0.0082653 | 0.0020715 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-383_0_5_load_47 | 86 | 0.0035836 | 0.00089814 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-383_0_5_load_48 | 87 | 0.013999 | 0.0035085 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-383_0_5_load_50 | 88 | 0.0090651 | 0.0022719 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-383_0_5_load_51 | 89 | 0.011457 | 0.0028715 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-383_0_5_load_52 | 90 | 0.01408 | 0.0035289 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-383_0_5_load_53 | 91 | 0.0048351 | 0.0012118 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-383_0_5_load_54 | 93 | 0.0034375 | 0.00086151 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-383_0_5_load_55 | 94 | 0.0034688 | 0.00086936 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-383_0_5_load_66 | 95 | 0.007614 | 0.0019082 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-383_0_5_load_67 | 96 | 0.0083223 | 0.0020858 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-383_0_5_load_119 | 97 | 0.016443 | 0.0041209 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-383_0_5_load_120 | 98 | 0.0089951 | 0.0022544 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-383_0_5_load_69 | 99 | 0.0031767 | 0.00079617 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-383_0_5_load_70 | 100 | 0.001961 | 0.00049148 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-383_0_5_load_72 | 101 | 0.0045899 | 0.0011503 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-383_0_5_load_73 | 102 | 0.0023689 | 0.0005937 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-383_0_5_load_75 | 103 | 0.0011866 | 0.00029738 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-383_0_5_load_83 | 104 | 0.0064712 | 0.0016218 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-383_0_5_load_76 | 105 | 0.0011955 | 0.00029961 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-383_0_5_load_84 | 106 | 0.0024188 | 0.00060621 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-383_0_5_load_77 | 107 | 0.0021847 | 0.00054754 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-383_0_5_load_82 | 108 | 0.002644 | 0.00066265 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-383_0_5_load_90 | 109 | 0.0025589 | 0.00064133 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-383_0_5_load_89 | 110 | 0.0013635 | 0.00034172 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-383_0_5_load_87 | 111 | 0.001264 | 0.00031679 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-383_0_5_load_85 | 112 | 0.0018998 | 0.00047612 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-383_0_5_load_86 | 113 | 0.002573 | 0.00064485 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-383_0_5_load_88 | 114 | 0.0020618 | 0.00051673 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_261-383_0_5_load_91 | 115 | 0.0046829 | 0.0011736 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_261-383_0_5_load_93 | 116 | 0.0052027 | 0.0013039 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_261-383_0_5_load_95 | 117 | 0.0046353 | 0.0011617 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_261-383_0_5_load_96 | 118 | 0.0040367 | 0.0010117 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_261-383_0_5_load_98 | 120 | 0.0047148 | 0.0011816 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_261-383_0_5_load_99 | 121 | 0.0033133 | 0.00083039 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_261-383_0_5_load_106 | 122 | 0.0013313 | 0.00033364 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_261-383_0_5_load_102 | 123 | 0.0015689 | 0.0003932 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_261-383_0_5_load_107 | 124 | 0.001297 | 0.00032507 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_261-383_0_5_load_149 | 125 | 0.0016283 | 0.0004081 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_261-383_0_5_load_108 | 126 | 0.0013689 | 0.00034307 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_261-383_0_5_load_109 | 127 | 0.0012995 | 0.00032567 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_261-383_0_5_load_115 | 129 | 0.0018175 | 0.00045551 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_261-383_0_5_load_111 | 130 | 0.0013836 | 0.00034676 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_261-383_0_5_load_110 | 131 | 0.0013019 | 0.00032629 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_261-383_0_5_load_114 | 133 | 0.0013127 | 0.000329 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_261-383_0_5_load_117 | 134 | 0.0013414 | 0.00033618 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_261-383_0_5_load_121 | 135 | 0.0057195 | 0.0014334 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_261-383_0_5_load_124 | 136 | 0.0083883 | 0.0021023 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_261-383_0_5_load_144 | 138 | 0.0038849 | 0.00097365 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_261-383_0_5_load_143 | 139 | 0.0053662 | 0.0013449 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 67 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-383_0_5_line_0 |  | 0 | 1 | 0.035058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_261-383_0_5_line_1 |  | 0 | 2 | 0.022839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_261-383_0_5_line_2 |  | 1 | 3 | 0.020395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_261-383_0_5_line_3 |  | 2 | 4 | 0.039891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-383_0_5_line_4 |  | 2 | 5 | 0.037754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_261-383_0_5_line_5 |  | 3 | 6 | 0.0080999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_261-383_0_5_line_6 |  | 3 | 7 | 0.00762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-383_0_5_line_7 |  | 4 | 8 | 0.023272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-383_0_5_line_8 |  | 4 | 9 | 0.012781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-383_0_5_line_9 |  | 5 | 10 | 0.004902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-383_0_5_line_10 |  | 5 | 11 | 0.037518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_261-383_0_5_line_11 |  | 6 | 21 | 0.002771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_261-383_0_5_line_12 |  | 6 | 22 | 0.017546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-383_0_5_line_13 |  | 7 | 29 | 0.0098936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-383_0_5_line_14 |  | 8 | 52 | 0.013912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-383_0_5_line_15 |  | 9 | 56 | 0.041765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-383_0_5_line_16 |  | 10 | 57 | 0.017054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-383_0_5_line_17 |  | 11 | 58 | 0.020939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_261-383_0_5_line_18 |  | 12 | 13 | 0.010804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-383_0_5_line_19 |  | 12 | 14 | 0.004183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-383_0_5_line_20 |  | 12 | 15 | 0.0085233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-383_0_5_line_21 |  | 13 | 59 | 0.01726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-383_0_5_line_22 |  | 14 | 16 | 0.024135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-383_0_5_line_23 |  | 14 | 17 | 0.011563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-383_0_5_line_24 |  | 15 | 23 | 0.038406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-383_0_5_line_25 |  | 15 | 24 | 0.009189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-383_0_5_line_26 |  | 15 | 25 | 0.022052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-383_0_5_line_27 |  | 16 | 60 | 0.018287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-383_0_5_line_28 |  | 18 | 19 | 0.003814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-383_0_5_line_29 |  | 18 | 20 | 0.029952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-383_0_5_line_30 |  | 19 | 39 | 0.033945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-383_0_5_line_31 |  | 20 | 61 | 0.0067328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-383_0_5_line_32 |  | 21 | 33 | 0.017882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_261-383_0_5_line_33 |  | 23 | 62 | 0.044999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-383_0_5_line_34 |  | 23 | 63 | 0.014218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-383_0_5_line_35 |  | 25 | 40 | 0.0082802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-383_0_5_line_36 |  | 26 | 27 | 0.002585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-383_0_5_line_37 |  | 26 | 28 | 0.0093214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-383_0_5_line_38 |  | 27 | 30 | 0.025821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_261-383_0_5_line_39 |  | 27 | 31 | 0.011052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-383_0_5_line_40 |  | 29 | 64 | 0.032575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-383_0_5_line_41 |  | 30 | 65 | 0.0085649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_261-383_0_5_line_42 |  | 31 | 66 | 0.01977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-383_0_5_line_43 |  | 32 | 33 | 0.010503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_261-383_0_5_line_44 |  | 32 | 34 | 0.014597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_261-383_0_5_line_45 |  | 33 | 35 | 0.03295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_261-383_0_5_line_46 |  | 34 | 36 | 0.01345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_261-383_0_5_line_47 |  | 35 | 67 | 0.0024399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_261-383_0_5_line_48 |  | 36 | 68 | 0.0033909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_261-383_0_5_line_49 |  | 37 | 38 | 0.0054227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-383_0_5_line_50 |  | 37 | 39 | 0.0011772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-383_0_5_line_51 |  | 38 | 41 | 0.0091384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-383_0_5_line_52 |  | 40 | 41 | 0.0089134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-383_0_5_line_53 |  | 41 | 42 | 0.0059386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-383_0_5_line_54 |  | 43 | 44 | 0.047757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-383_0_5_line_55 |  | 43 | 45 | 0.045477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-383_0_5_line_56 |  | 45 | 70 | 0.0063388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-383_0_5_line_57 |  | 46 | 47 | 0.008736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-383_0_5_line_58 |  | 46 | 48 | 0.012822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-383_0_5_line_59 |  | 46 | 49 | 0.0098758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-383_0_5_line_60 |  | 47 | 71 | 0.016588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-383_0_5_line_61 |  | 47 | 50 | 0.004236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-383_0_5_line_62 |  | 48 | 53 | 0.096198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-383_0_5_line_63 |  | 48 | 54 | 0.0015955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-383_0_5_line_64 |  | 50 | 51 | 0.027028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-383_0_5_line_65 |  | 51 | 74 | 0.027331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-383_0_5_line_66 |  | 53 | 55 | 0.053919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-383_0_5_line_67 |  | 54 | 75 | 0.00024877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-383_0_5_line_68 |  | 58 | 95 | 0.020441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_261-383_0_5_line_69 |  | 60 | 69 | 0.018454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-383_0_5_line_70 |  | 61 | 66 | 0.0166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-383_0_5_line_71 |  | 62 | 82 | 0.0039084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-383_0_5_line_72 |  | 64 | 102 | 0.014091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-383_0_5_line_73 |  | 64 | 99 | 0.0063726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-383_0_5_line_74 |  | 65 | 134 | 0.0059347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
75 | LV_261-383_0_5_line_75 |  | 67 | 83 | 0.026345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-383_0_5_line_76 |  | 68 | 115 | 0.018044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_261-383_0_5_line_77 |  | 70 | 107 | 0.0017982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-383_0_5_line_78 |  | 72 | 73 | 0.0088194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-383_0_5_line_79 |  | 73 | 123 | 0.021812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-383_0_5_line_80 |  | 73 | 120 | 0.012823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_261-383_0_5_line_81 |  | 74 | 137 | 0.040387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-383_0_5_line_82 |  | 75 | 136 | 0.0087169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_261-383_0_5_line_83 |  | 76 | 77 | 0.016092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_261-383_0_5_line_84 |  | 77 | 81 | 0.007534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_261-383_0_5_line_85 |  | 77 | 92 | 0.001926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_261-383_0_5_line_86 |  | 78 | 79 | 0.01311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_261-383_0_5_line_87 |  | 79 | 82 | 0.010564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_261-383_0_5_line_88 |  | 80 | 81 | 0.0059771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_261-383_0_5_line_89 |  | 83 | 84 | 0.0083868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_261-383_0_5_line_90 |  | 84 | 85 | 0.0089972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_261-383_0_5_line_91 |  | 85 | 86 | 0.00042837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_261-383_0_5_line_92 |  | 86 | 87 | 0.011191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_261-383_0_5_line_93 |  | 87 | 88 | 0.010685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_261-383_0_5_line_94 |  | 88 | 89 | 0.020177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_261-383_0_5_line_95 |  | 89 | 90 | 0.0037546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_261-383_0_5_line_96 |  | 90 | 91 | 0.015843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_261-383_0_5_line_97 |  | 91 | 92 | 0.014553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_261-383_0_5_line_98 |  | 92 | 93 | 0.012789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_261-383_0_5_line_99 |  | 93 | 94 | 0.016992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_261-383_0_5_line_100 |  | 95 | 96 | 0.0087127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
101 | LV_261-383_0_5_line_101 |  | 96 | 97 | 0.001427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_261-383_0_5_line_102 |  | 97 | 98 | 0.0077364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_261-383_0_5_line_103 |  | 98 | 135 | 0.0052269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_261-383_0_5_line_104 |  | 99 | 100 | 0.019391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_261-383_0_5_line_105 |  | 100 | 101 | 0.011677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_261-383_0_5_line_106 |  | 101 | 103 | 0.0048821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_261-383_0_5_line_107 |  | 102 | 104 | 0.0042797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_261-383_0_5_line_108 |  | 103 | 105 | 0.0064211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_261-383_0_5_line_109 |  | 104 | 106 | 0.027546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-383_0_5_line_110 |  | 105 | 107 | 0.013292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_261-383_0_5_line_111 |  | 106 | 111 | 0.0024946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_261-383_0_5_line_112 |  | 108 | 109 | 0.00015176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_261-383_0_5_line_113 |  | 109 | 110 | 0.013927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_261-383_0_5_line_114 |  | 110 | 114 | 0.0063457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_261-383_0_5_line_115 |  | 111 | 112 | 0.006858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_261-383_0_5_line_116 |  | 112 | 113 | 0.012115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_261-383_0_5_line_117 |  | 113 | 114 | 0.0071858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_261-383_0_5_line_118 |  | 115 | 116 | 0.0091039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
119 | LV_261-383_0_5_line_119 |  | 116 | 117 | 0.013459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_261-383_0_5_line_120 |  | 117 | 118 | 0.020626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
121 | LV_261-383_0_5_line_121 |  | 118 | 119 | 0.0027215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
122 | LV_261-383_0_5_line_122 |  | 119 | 120 | 0.018605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_261-383_0_5_line_123 |  | 119 | 121 | 0.012327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
124 | LV_261-383_0_5_line_124 |  | 121 | 122 | 0.011143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
125 | LV_261-383_0_5_line_125 |  | 122 | 124 | 0.0088998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
126 | LV_261-383_0_5_line_126 |  | 123 | 125 | 0.0048439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_261-383_0_5_line_127 |  | 124 | 126 | 0.0083517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
128 | LV_261-383_0_5_line_128 |  | 126 | 127 | 0.019768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
129 | LV_261-383_0_5_line_129 |  | 127 | 128 | 0.0029974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
130 | LV_261-383_0_5_line_130 |  | 128 | 129 | 0.0069194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
131 | LV_261-383_0_5_line_131 |  | 128 | 130 | 0.011534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_261-383_0_5_line_132 |  | 129 | 134 | 0.012626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
133 | LV_261-383_0_5_line_133 |  | 130 | 131 | 0.009218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_261-383_0_5_line_134 |  | 131 | 132 | 0.0047234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_261-383_0_5_line_135 |  | 132 | 133 | 0.015954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_261-383_0_5_line_136 |  | 135 | 136 | 0.0039683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_261-383_0_5_line_137 |  | 137 | 138 | 0.013663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_261-383_0_5_line_138 |  | 138 | 139 | 0.024851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-383_0_5_trafo_43 | 0.63 MVA 20/0.4 kV | 140 | 67 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2682220.6354 | 1251755.5608 | 2682223.9876 | 1251756.9493 | 2682228.8705 | 1251760.264 | 2682234.4506 | 1251766.0902 | 2682242.4145 | 1251777.9985 | 2682244.1542 | 1251780.6059
1 | 2682198.525 | 1251750.1021 | 2682204.278 | 1251751.0937 | 2682209.5904 | 1251752.2794 | 2682216.7379 | 1251753.9465 | 2682220.6354 | 1251755.5608
2 | 2682255.0622 | 1251797.7554 | 2682254.7182 | 1251796.4386 | 2682244.1542 | 1251780.6059
3 | 2682198.525 | 1251750.1021 | 2682159.7573 | 1251759.9608
4 | 2682235.1043 | 1251740.7581 | 2682222.5065 | 1251744.0302 | 2682198.525 | 1251750.1021
5 | 2682261.775 | 1251793.223 | 2682258.62 | 1251795.3919 | 2682255.0622 | 1251797.7554
6 | 2682254.1533 | 1251805.0482 | 2682253.7792 | 1251801.0067 | 2682254.6109 | 1251799.8174 | 2682255.0622 | 1251797.7554
7 | 2682159.7573 | 1251759.9608 | 2682137.1392 | 1251765.7071
8 | 2682159.7573 | 1251759.9608 | 2682162.5467 | 1251772.4341
9 | 2682235.6859 | 1251745.6254 | 2682235.1043 | 1251740.7581
10 | 2682235.1043 | 1251740.7581 | 2682248.702 | 1251737.2331 | 2682271.4572 | 1251731.4808
11 | 2682261.775 | 1251793.223 | 2682263.3381 | 1251795.511
12 | 2682261.775 | 1251793.223 | 2682251.8986 | 1251778.721
13 | 2682254.1533 | 1251805.0482 | 2682244.2874 | 1251805.7868
14 | 2682137.1392 | 1251765.7071 | 2682140.2642 | 1251779.2637
15 | 2682194.3584 | 1251776.6904 | 2682165.0876 | 1251783.7969 | 2682162.5467 | 1251772.4341
16 | 2682235.6859 | 1251745.6254 | 2682240.8045 | 1251743.9174 | 2682250.5226 | 1251741.4726 | 2682252.1047 | 1251741.052
17 | 2682271.4572 | 1251731.4808 | 2682291.7574 | 1251726.349
18 | 2682331.1648 | 1251909.3288 | 2682322.2834 | 1251915.481
19 | 2682328.8203 | 1251905.8603 | 2682331.1648 | 1251909.3288
20 | 2682331.1648 | 1251909.3288 | 2682334.1599 | 1251907.2578 | 2682337.2467 | 1251903.4756
21 | 2682308.0953 | 1251925.3092 | 2682322.2834 | 1251915.481
22 | 2682328.8203 | 1251905.8603 | 2682315.3342 | 1251885.8442
23 | 2682328.8203 | 1251905.8603 | 2682319.1209 | 1251912.1553
24 | 2682337.2467 | 1251903.4756 | 2682315.6033 | 1251871.7068
25 | 2682343.0521 | 1251896.3398 | 2682337.2467 | 1251903.4756
26 | 2682337.2467 | 1251903.4756 | 2682349.3202 | 1251921.9293
27 | 2682305.0927 | 1251870.6942 | 2682307.7733 | 1251874.6224 | 2682315.3342 | 1251885.8442
28 | 2682369.5456 | 1251975.5338 | 2682373.2924 | 1251974.7631
29 | 2682369.5456 | 1251975.5338 | 2682340.081 | 1251980.9175
30 | 2682373.2924 | 1251974.7631 | 2682372.4771 | 1251970.4374 | 2682355.9268 | 1251945.9655
31 | 2682333.4578 | 1251982.1276 | 2682340.081 | 1251980.9175
32 | 2682275.8999 | 1251805.5283 | 2682274.5422 | 1251801.6621 | 2682270.8498 | 1251801.2216 | 2682268.6117 | 1251800.957 | 2682266.1533 | 1251799.7108 | 2682263.654 | 1251795.9733 | 2682263.3381 | 1251795.511
33 | 2682315.6033 | 1251871.7068 | 2682330.2594 | 1251868.041 | 2682339.225 | 1251864.3405 | 2682351.8777 | 1251857.1109 | 2682357.355 | 1251855.8544
34 | 2682315.6033 | 1251871.7068 | 2682307.6781 | 1251859.9025
35 | 2682354.678 | 1251928.203 | 2682352.8533 | 1251926.4429 | 2682350.5353 | 1251923.7865 | 2682349.3202 | 1251921.9293
36 | 2682284.2582 | 1251991.1162 | 2682286.8082 | 1251990.6513
37 | 2682284.2582 | 1251991.1162 | 2682275.0901 | 1251992.7999
38 | 2682286.8082 | 1251990.6513 | 2682282.8732 | 1251972.9167 | 2682280.4181 | 1251965.6662
39 | 2682286.8082 | 1251990.6513 | 2682297.68 | 1251988.6648
40 | 2682211.8029 | 1251808.2185 | 2682244.2874 | 1251805.7868
41 | 2682277.644 | 1251957.5648 | 2682277.7472 | 1251957.7787 | 2682280.4181 | 1251965.6662
42 | 2682317.1282 | 1251985.1113 | 2682297.68 | 1251988.6648
43 | 2682275.8999 | 1251805.5283 | 2682277.345 | 1251809.6292 | 2682276.3755 | 1251810.9611 | 2682275.9346 | 1251812.2671 | 2682275.7782 | 1251813.7438 | 2682275.8158 | 1251815.39
44 | 2682275.8158 | 1251815.39 | 2682272.4288 | 1251817.4112 | 2682276.4987 | 1251824.3617 | 2682274.8406 | 1251826.3624
45 | 2682275.8999 | 1251805.5283 | 2682307.8874 | 1251797.6221
46 | 2682274.8406 | 1251826.3624 | 2682266.2442 | 1251836.7073
47 | 2682307.8874 | 1251797.6221 | 2682310.256 | 1251797.0367
48 | 2682264.077 | 1251839.3153 | 2682266.2442 | 1251836.7073
49 | 2682355.2673 | 1251944.9903 | 2682352.2322 | 1251940.4966
50 | 2682355.2673 | 1251944.9903 | 2682355.9268 | 1251945.9655
51 | 2682347.1174 | 1251932.9236 | 2682352.2322 | 1251940.4966
52 | 2682347.1174 | 1251932.9236 | 2682350.6655 | 1251930.7046 | 2682354.678 | 1251928.203
53 | 2682347.1174 | 1251932.9236 | 2682343.7912 | 1251928.004
54 | 2682098.6473 | 1251830.2774 | 2682118.8343 | 1251873.5584
55 | 2682098.6473 | 1251830.2774 | 2682109.8468 | 1251826.0406 | 2682122.6987 | 1251822.3937 | 2682142.4559 | 1251818.4671
56 | 2682142.4559 | 1251818.4671 | 2682148.6731 | 1251817.2315
57 | 2682345.2215 | 1251699.612 | 2682353.6627 | 1251697.272
58 | 2682345.2215 | 1251699.612 | 2682346.6583 | 1251705.9367 | 2682348.0593 | 1251712.1163
59 | 2682345.2215 | 1251699.612 | 2682335.6441 | 1251702.0214
60 | 2682353.6627 | 1251697.272 | 2682353.4474 | 1251692.6656 | 2682350.5542 | 1251681.044
61 | 2682353.6627 | 1251697.272 | 2682357.8258 | 1251696.4292
62 | 2682348.0593 | 1251712.1163 | 2682360.9289 | 1251708.8594 | 2682441.6134 | 1251688.5995
63 | 2682348.0593 | 1251712.1163 | 2682346.5125 | 1251712.5074
64 | 2682357.8258 | 1251696.4292 | 2682365.1732 | 1251694.5855 | 2682384.0357 | 1251689.8315
65 | 2682410.538 | 1251683.1521 | 2682384.0357 | 1251689.8315
66 | 2682416.962 | 1251721.6257 | 2682444.1308 | 1251714.3426 | 2682441.6134 | 1251688.5995
67 | 2682346.2713 | 1251712.5683 | 2682346.5125 | 1251712.5074
68 | 2682311.5747 | 1251721.3394 | 2682291.7574 | 1251726.349
69 | 2682294.6907 | 1251855.451 | 2682305.0927 | 1251870.6942
70 | 2682317.1282 | 1251985.1113 | 2682333.4578 | 1251982.1276
71 | 2682357.355 | 1251855.8544 | 2682361.0172 | 1251855.0142 | 2682361.1654 | 1251854.9854
72 | 2682211.8029 | 1251808.2185 | 2682212.7332 | 1251822.2786
73 | 2682211.8029 | 1251808.2185 | 2682205.4539 | 1251808.766
74 | 2682277.644 | 1251957.5648 | 2682275.065 | 1251952.2198
75 | 2682310.256 | 1251797.0367 | 2682325.0098 | 1251793.3901 | 2682335.85 | 1251790.7908
76 | 2682252.545 | 1251853.1928 | 2682264.077 | 1251839.3153
77 | 2682150.4369 | 1251816.8809 | 2682148.6731 | 1251817.2315
78 | 2682203.5622 | 1251913.038 | 2682198.0573 | 1251919.9285
79 | 2682203.5622 | 1251913.038 | 2682220.3817 | 1251926.9254
80 | 2682203.5622 | 1251913.038 | 2682204.7911 | 1251911.5095 | 2682211.5777 | 1251903.0292
81 | 2682400.8786 | 1251643.9329 | 2682410.538 | 1251683.1521
82 | 2682346.2713 | 1251712.5683 | 2682337.8203 | 1251714.7047
83 | 2682427.1028 | 1251762.0302 | 2682428.3205 | 1251765.105 | 2682433.0582 | 1251776.9797
84 | 2682427.1028 | 1251762.0302 | 2682434.0136 | 1251759.0299
85 | 2682425.5027 | 1251763.1088 | 2682427.1028 | 1251762.0302
86 | 2682384.1438 | 1251849.4517 | 2682375.609 | 1251852.1815 | 2682371.5361 | 1251852.9722
87 | 2682361.1654 | 1251854.9854 | 2682371.5361 | 1251852.9722
88 | 2682434.0136 | 1251759.0299 | 2682439.4963 | 1251756.6497
89 | 2682344.0057 | 1251788.8352 | 2682335.85 | 1251790.7908
90 | 2682344.0057 | 1251788.8352 | 2682352.7548 | 1251786.7373
91 | 2682352.7548 | 1251786.7373 | 2682353.1714 | 1251786.6374
92 | 2682353.1714 | 1251786.6374 | 2682364.0534 | 1251784.028
93 | 2682374.4437 | 1251781.5366 | 2682364.0534 | 1251784.028
94 | 2682374.4437 | 1251781.5366 | 2682379.8857 | 1251780.2317 | 2682388.6371 | 1251777.2845 | 2682393.6274 | 1251775.3656
95 | 2682397.1318 | 1251774.0181 | 2682393.6274 | 1251775.3656
96 | 2682397.1318 | 1251774.0181 | 2682411.9191 | 1251768.332
97 | 2682425.5027 | 1251763.1088 | 2682411.9191 | 1251768.332
98 | 2682425.5027 | 1251763.1088 | 2682430.2444 | 1251774.9863
99 | 2682436.5446 | 1251790.7676 | 2682430.2444 | 1251774.9863
100 | 2682320.0216 | 1251719.2041 | 2682311.5747 | 1251721.3394
101 | 2682320.0216 | 1251719.2041 | 2682321.4051 | 1251718.8543
102 | 2682321.4051 | 1251718.8543 | 2682328.9055 | 1251716.9583
103 | 2682333.973 | 1251715.6772 | 2682328.9055 | 1251716.9583
104 | 2682205.4539 | 1251808.766 | 2682189.3661 | 1251810.1532 | 2682186.16 | 1251810.6437
105 | 2682186.16 | 1251810.6437 | 2682174.6174 | 1251812.4096
106 | 2682174.6174 | 1251812.4096 | 2682169.7914 | 1251813.1479
107 | 2682212.7332 | 1251822.2786 | 2682213.0157 | 1251826.549
108 | 2682163.4742 | 1251814.2899 | 2682167.3094 | 1251813.5276 | 2682169.7914 | 1251813.1479
109 | 2682199.4369 | 1251849.5376 | 2682207.1219 | 1251840.3887 | 2682211.9583 | 1251833.9955 | 2682213.1505 | 1251828.5857 | 2682213.0157 | 1251826.549
110 | 2682163.4742 | 1251814.2899 | 2682150.4369 | 1251816.8809
111 | 2682199.4369 | 1251849.5376 | 2682197.8324 | 1251851.4477
112 | 2682167.8704 | 1251887.1173 | 2682167.968 | 1251887.0011
113 | 2682167.968 | 1251887.0011 | 2682176.9257 | 1251876.337
114 | 2682181.0072 | 1251871.478 | 2682176.9257 | 1251876.337
115 | 2682193.4214 | 1251856.699 | 2682197.8324 | 1251851.4477
116 | 2682193.4214 | 1251856.699 | 2682185.629 | 1251865.9758
117 | 2682181.0072 | 1251871.478 | 2682185.629 | 1251865.9758
118 | 2682252.545 | 1251853.1928 | 2682246.7265 | 1251860.1948
119 | 2682238.1245 | 1251870.5465 | 2682246.7265 | 1251860.1948
120 | 2682238.1245 | 1251870.5465 | 2682224.942 | 1251886.4101
121 | 2682223.2027 | 1251888.5033 | 2682224.942 | 1251886.4101
122 | 2682223.2027 | 1251888.5033 | 2682211.5777 | 1251903.0292
123 | 2682223.2027 | 1251888.5033 | 2682232.6368 | 1251896.4379
124 | 2682232.6368 | 1251896.4379 | 2682241.1644 | 1251903.6101
125 | 2682247.228 | 1251910.1012 | 2682242.6006 | 1251904.8179 | 2682241.1644 | 1251903.6101
126 | 2682223.0022 | 1251930.8078 | 2682222.0538 | 1251928.3059 | 2682220.3817 | 1251926.9254
127 | 2682247.228 | 1251910.1012 | 2682250.8033 | 1251914.1832 | 2682252.6055 | 1251916.4875
128 | 2682263.9437 | 1251932.6453 | 2682258.9537 | 1251924.6041 | 2682252.6055 | 1251916.4875
129 | 2682265.5241 | 1251935.1921 | 2682263.9437 | 1251932.6453
130 | 2682265.5241 | 1251935.1921 | 2682269.175 | 1251941.0699
131 | 2682265.5241 | 1251935.1921 | 2682255.7746 | 1251941.3546
132 | 2682275.065 | 1251952.2198 | 2682271.4598 | 1251944.7483 | 2682269.175 | 1251941.0699
133 | 2682247.9826 | 1251946.2797 | 2682255.7746 | 1251941.3546
134 | 2682243.9899 | 1251948.8034 | 2682247.9826 | 1251946.2797
135 | 2682243.9899 | 1251948.8034 | 2682250.1895 | 1251963.5036
136 | 2682333.973 | 1251715.6772 | 2682337.8203 | 1251714.7047
137 | 2682400.8786 | 1251643.9329 | 2682387.6139 | 1251647.2066
138 | 2682363.4864 | 1251653.161 | 2682387.6139 | 1251647.2066

## bus_geodata
| x | y | coords
0 | 2682220.6354 | 1251755.5608
1 | 2682244.1542 | 1251780.6059
2 | 2682198.525 | 1251750.1021
3 | 2682255.0622 | 1251797.7554
4 | 2682159.7573 | 1251759.9608
5 | 2682235.1043 | 1251740.7581
6 | 2682261.775 | 1251793.223
7 | 2682254.1533 | 1251805.0482
8 | 2682137.1392 | 1251765.7071
9 | 2682162.5467 | 1251772.4341
10 | 2682235.6859 | 1251745.6254
11 | 2682271.4572 | 1251731.4808
12 | 2682331.1648 | 1251909.3288
13 | 2682322.2834 | 1251915.481
14 | 2682328.8203 | 1251905.8603
15 | 2682337.2467 | 1251903.4756
16 | 2682315.3342 | 1251885.8442
17 | 2682319.1209 | 1251912.1553
18 | 2682369.5456 | 1251975.5338
19 | 2682373.2924 | 1251974.7631
20 | 2682340.081 | 1251980.9175
21 | 2682263.3381 | 1251795.511
22 | 2682251.8986 | 1251778.721
23 | 2682315.6033 | 1251871.7068
24 | 2682343.0521 | 1251896.3398
25 | 2682349.3202 | 1251921.9293
26 | 2682284.2582 | 1251991.1162
27 | 2682286.8082 | 1251990.6513
28 | 2682275.0901 | 1251992.7999
29 | 2682244.2874 | 1251805.7868
30 | 2682280.4181 | 1251965.6662
31 | 2682297.68 | 1251988.6648
32 | 2682275.8158 | 1251815.39
33 | 2682275.8999 | 1251805.5283
34 | 2682274.8406 | 1251826.3624
35 | 2682307.8874 | 1251797.6221
36 | 2682266.2442 | 1251836.7073
37 | 2682355.2673 | 1251944.9903
38 | 2682352.2322 | 1251940.4966
39 | 2682355.9268 | 1251945.9655
40 | 2682354.678 | 1251928.2029
41 | 2682347.1174 | 1251932.9236
42 | 2682343.7912 | 1251928.004
43 | 2682098.6473 | 1251830.2774
44 | 2682118.8343 | 1251873.5584
45 | 2682142.4559 | 1251818.4671
46 | 2682345.2215 | 1251699.612
47 | 2682353.6627 | 1251697.272
48 | 2682348.0593 | 1251712.1163
49 | 2682335.6441 | 1251702.0214
50 | 2682357.8258 | 1251696.4292
51 | 2682384.0357 | 1251689.8315
52 | 2682140.2642 | 1251779.2637
53 | 2682441.6134 | 1251688.5995
54 | 2682346.5125 | 1251712.5074
55 | 2682416.962 | 1251721.6257
56 | 2682194.3584 | 1251776.6904
57 | 2682252.1047 | 1251741.052
58 | 2682291.7574 | 1251726.349
59 | 2682308.0953 | 1251925.3092
60 | 2682305.0927 | 1251870.6942
61 | 2682333.4578 | 1251982.1276
62 | 2682357.355 | 1251855.8544
63 | 2682307.6781 | 1251859.9025
64 | 2682211.8029 | 1251808.2185
65 | 2682277.644 | 1251957.5648
66 | 2682317.1282 | 1251985.1113
67 | 2682310.256 | 1251797.0367
68 | 2682264.077 | 1251839.3153
69 | 2682294.6907 | 1251855.451
70 | 2682148.6731 | 1251817.2315
71 | 2682350.5542 | 1251681.044
72 | 2682198.0573 | 1251919.9285
73 | 2682203.5622 | 1251913.038
74 | 2682410.538 | 1251683.1521
75 | 2682346.2713 | 1251712.5683
76 | 2682433.0582 | 1251776.9797
77 | 2682427.1028 | 1251762.0302
78 | 2682384.1438 | 1251849.4517
79 | 2682371.5361 | 1251852.9722
80 | 2682439.4963 | 1251756.6497
81 | 2682434.0136 | 1251759.0299
82 | 2682361.1654 | 1251854.9854
83 | 2682335.85 | 1251790.7908
84 | 2682344.0057 | 1251788.8352
85 | 2682352.7548 | 1251786.7373
86 | 2682353.1714 | 1251786.6374
87 | 2682364.0534 | 1251784.028
88 | 2682374.4437 | 1251781.5366
89 | 2682393.6274 | 1251775.3656
90 | 2682397.1318 | 1251774.0181
91 | 2682411.9191 | 1251768.332
92 | 2682425.5027 | 1251763.1088
93 | 2682430.2444 | 1251774.9863
94 | 2682436.5446 | 1251790.7676
95 | 2682311.5747 | 1251721.3394
96 | 2682320.0216 | 1251719.204
97 | 2682321.4051 | 1251718.8543
98 | 2682328.9055 | 1251716.9583
99 | 2682205.4539 | 1251808.766
100 | 2682186.16 | 1251810.6437
101 | 2682174.6174 | 1251812.4096
102 | 2682212.7332 | 1251822.2786
103 | 2682169.7914 | 1251813.1479
104 | 2682213.0157 | 1251826.549
105 | 2682163.4742 | 1251814.2899
106 | 2682199.4369 | 1251849.5376
107 | 2682150.4369 | 1251816.8809
108 | 2682167.8704 | 1251887.1173
109 | 2682167.968 | 1251887.0011
110 | 2682176.9257 | 1251876.337
111 | 2682197.8324 | 1251851.4477
112 | 2682193.4214 | 1251856.699
113 | 2682185.629 | 1251865.9758
114 | 2682181.0072 | 1251871.478
115 | 2682252.545 | 1251853.1928
116 | 2682246.7265 | 1251860.1948
117 | 2682238.1245 | 1251870.5465
118 | 2682224.942 | 1251886.4101
119 | 2682223.2027 | 1251888.5033
120 | 2682211.5777 | 1251903.0292
121 | 2682232.6368 | 1251896.4379
122 | 2682241.1644 | 1251903.6101
123 | 2682220.3817 | 1251926.9254
124 | 2682247.228 | 1251910.1012
125 | 2682223.0022 | 1251930.8078
126 | 2682252.6055 | 1251916.4875
127 | 2682263.9437 | 1251932.6453
128 | 2682265.5241 | 1251935.1921
129 | 2682269.175 | 1251941.0699
130 | 2682255.7746 | 1251941.3546
131 | 2682247.9826 | 1251946.2797
132 | 2682243.9899 | 1251948.8034
133 | 2682250.1895 | 1251963.5036
134 | 2682275.065 | 1251952.2198
135 | 2682333.973 | 1251715.6772
136 | 2682337.8203 | 1251714.7047
137 | 2682400.8786 | 1251643.9329
138 | 2682387.6139 | 1251647.2066
139 | 2682363.4864 | 1251653.161
140 | 2682275.8999 | 1251805.5283

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99284 | -0.13641 | 0.0088053 | 0.0022068
1 | 0.99429 | -0.10867 | 0.0067785 | 0.0016989
2 | 0.99195 | -0.15363 | 0 | 0
3 | 0.99516 | -0.091969 | 0 | 0
4 | 0.99147 | -0.1628 | 0 | 0
5 | 0.99058 | -0.17998 | 0 | 0
6 | 0.9956 | -0.083659 | 0 | 0
7 | 0.99484 | -0.09831 | 0 | 0
8 | 0.99141 | -0.1641 | 0 | 0
9 | 0.99136 | -0.16502 | 0.0040708 | 0.0010202
10 | 0.99056 | -0.18034 | 0 | 0
11 | 0.98925 | -0.20556 | 0.0022709 | 0.00056914
12 | 0.97458 | -0.48909 | 0 | 0
13 | 0.97452 | -0.4903 | 0.0028462 | 0.00071331
14 | 0.97453 | -0.49011 | 0 | 0
15 | 0.97474 | -0.48605 | 0 | 0
16 | 0.97432 | -0.49416 | 0.0033683 | 0.00084418
17 | 0.97448 | -0.49099 | 0.0041446 | 0.0010387
18 | 0.98201 | -0.34382 | 0 | 0
19 | 0.98169 | -0.35003 | 0 | 0
20 | 0.98453 | -0.2952 | 0.0026409 | 0.00066186
21 | 0.99575 | -0.08076 | 0.0031862 | 0.00079854
22 | 0.99552 | -0.085128 | 0.0047598 | 0.0011929
23 | 0.97302 | -0.51983 | 0 | 0
24 | 0.97467 | -0.48728 | 0.0073237 | 0.0018355
25 | 0.97627 | -0.45591 | 0.0075602 | 0.0018948
26 | 0.98942 | -0.20126 | 0 | 0
27 | 0.98942 | -0.2012 | 0 | 0
28 | 0.98941 | -0.20148 | 0.0013355 | 0.00033471
29 | 0.99441 | -0.10655 | 0.0028327 | 0.00070994
30 | 0.99064 | -0.17803 | 0.0017922 | 0.00044918
31 | 0.9884 | -0.22081 | 0.0012002 | 0.0003008
32 | 0.99637 | -0.068964 | 0 | 0
33 | 0.99674 | -0.061823 | 0 | 0
34 | 0.99584 | -0.078898 | 0 | 0
35 | 0.99975 | -0.004739 | 0.049448 | 0.012393
36 | 0.99536 | -0.088061 | 0.002847 | 0.00071353
37 | 0.97875 | -0.40734 | 0 | 0
38 | 0.97831 | -0.41598 | 0.0026828 | 0.00067238
39 | 0.97885 | -0.40547 | 0.0025446 | 0.00063774
40 | 0.9769 | -0.44347 | 0 | 0
41 | 0.97759 | -0.43011 | 0 | 0
42 | 0.97757 | -0.43039 | 0.0026356 | 0.00066053
43 | 0.9923 | -0.14724 | 0 | 0
44 | 0.99225 | -0.14839 | 0.0013635 | 0.00034172
45 | 0.99236 | -0.14614 | 0.001664 | 0.00041703
46 | 0.98414 | -0.30469 | 0 | 0
47 | 0.98393 | -0.30883 | 0 | 0
48 | 0.98449 | -0.29787 | 0 | 0
49 | 0.98411 | -0.30526 | 0.0032341 | 0.00081055
50 | 0.98385 | -0.31044 | 0 | 0
51 | 0.98332 | -0.32073 | 0.011866 | 0.0029739
52 | 0.99137 | -0.16488 | 0.0031632 | 0.00079278
53 | 0.98098 | -0.36636 | 0 | 0
54 | 0.98459 | -0.29589 | 0.016494 | 0.0041337
55 | 0.97901 | -0.40497 | 0.039451 | 0.0098873
56 | 0.99114 | -0.16926 | 0.0057326 | 0.0014367
57 | 0.9905 | -0.18159 | 0.0041263 | 0.0010342
58 | 0.98852 | -0.21965 | 0.0024497 | 0.00061395
59 | 0.97447 | -0.49134 | 0.0032853 | 0.00082338
60 | 0.97423 | -0.4961 | 0.0029507 | 0.0007395
61 | 0.98511 | -0.28398 | 0.0027379 | 0.00068618
62 | 0.97163 | -0.54728 | 0.0066693 | 0.0016715
63 | 0.97282 | -0.52371 | 0.014788 | 0.0037061
64 | 0.99309 | -0.1321 | 0 | 0
65 | 0.99084 | -0.17413 | 0.0013209 | 0.00033104
66 | 0.98659 | -0.25557 | 0.0029445 | 0.00073795
67 | 1 | 0 | -0.55368 | -0.14069
68 | 0.99524 | -0.09033 | 0.0036765 | 0.00092141
69 | 0.97418 | -0.49706 | 0.0028293 | 0.00070909
70 | 0.99238 | -0.1458 | 0.00148 | 0.00037092
71 | 0.98385 | -0.31039 | 0.0052222 | 0.0013088
72 | 0.99291 | -0.13472 | 0.0021579 | 0.00054083
73 | 0.99293 | -0.13439 | 0 | 0
74 | 0.98309 | -0.32529 | 0 | 0
75 | 0.98461 | -0.2955 | 0.0075607 | 0.0018949
76 | 0.99316 | -0.13159 | 0.0030155 | 0.00075575
77 | 0.99321 | -0.13073 | 0 | 0
78 | 0.97125 | -0.55484 | 0.0090751 | 0.0022744
79 | 0.97136 | -0.55264 | 0.0086517 | 0.0021683
80 | 0.99314 | -0.1321 | 0.0016644 | 0.00041714
81 | 0.99314 | -0.13192 | 0.0072717 | 0.0018225
82 | 0.97153 | -0.54918 | 0.0086805 | 0.0021755
83 | 0.99759 | -0.04621 | 0.0079583 | 0.0019945
84 | 0.99688 | -0.059797 | 0.0082857 | 0.0020766
85 | 0.99619 | -0.073085 | 0.0082653 | 0.0020715
86 | 0.99616 | -0.073656 | 0.0035836 | 0.00089814
87 | 0.99542 | -0.087877 | 0.013999 | 0.0035085
88 | 0.99486 | -0.09884 | 0.0090651 | 0.0022719
89 | 0.99395 | -0.11635 | 0.011457 | 0.0028715
90 | 0.99382 | -0.11885 | 0.01408 | 0.0035289
91 | 0.99348 | -0.12548 | 0.0048351 | 0.0012118
92 | 0.99323 | -0.13033 | 0 | 0
93 | 0.99315 | -0.13189 | 0.0034375 | 0.00086151
94 | 0.99309 | -0.13293 | 0.0034688 | 0.00086936
95 | 0.98782 | -0.2332 | 0.007614 | 0.0019082
96 | 0.98726 | -0.24418 | 0.0083223 | 0.0020858
97 | 0.98708 | -0.24756 | 0.016443 | 0.0041209
98 | 0.98625 | -0.26365 | 0.0089951 | 0.0022544
99 | 0.99298 | -0.13421 | 0.0031767 | 0.00079617
100 | 0.9927 | -0.13957 | 0.001961 | 0.00049148
101 | 0.99255 | -0.1424 | 0.0045899 | 0.0011503
102 | 0.99276 | -0.13848 | 0.0023689 | 0.0005937
103 | 0.99251 | -0.14318 | 0.0011866 | 0.00029738
104 | 0.99267 | -0.14024 | 0.0064712 | 0.0016218
105 | 0.99247 | -0.14408 | 0.0011955 | 0.00029961
106 | 0.99224 | -0.14842 | 0.0024188 | 0.00060621
107 | 0.99239 | -0.14565 | 0.0021847 | 0.00054754
108 | 0.99184 | -0.15618 | 0.002644 | 0.00066265
109 | 0.99184 | -0.15617 | 0.0025589 | 0.00064133
110 | 0.99191 | -0.15489 | 0.0013635 | 0.00034172
111 | 0.99221 | -0.14906 | 0.001264 | 0.00031679
112 | 0.99213 | -0.15065 | 0.0018998 | 0.00047612
113 | 0.992 | -0.15305 | 0.002573 | 0.00064485
114 | 0.99195 | -0.15415 | 0.0020618 | 0.00051673
115 | 0.99462 | -0.10212 | 0.0046829 | 0.0011736
116 | 0.99432 | -0.10789 | 0.0052027 | 0.0013039
117 | 0.99389 | -0.11611 | 0.0046353 | 0.0011617
118 | 0.99325 | -0.1283 | 0.0040367 | 0.0010117
119 | 0.99316 | -0.12986 | 0 | 0
120 | 0.99299 | -0.13317 | 0.0047148 | 0.0011816
121 | 0.99282 | -0.13639 | 0.0033133 | 0.00083039
122 | 0.99252 | -0.14213 | 0.0013313 | 0.00033364
123 | 0.99287 | -0.13562 | 0.0015689 | 0.0003932
124 | 0.99228 | -0.14666 | 0.001297 | 0.00032507
125 | 0.99286 | -0.13576 | 0.0016283 | 0.0004081
126 | 0.99206 | -0.15087 | 0.0013689 | 0.00034307
127 | 0.99154 | -0.16072 | 0.0012995 | 0.00032567
128 | 0.99147 | -0.1622 | 0 | 0
129 | 0.99129 | -0.16549 | 0.0018175 | 0.00045551
130 | 0.99142 | -0.16302 | 0.0013836 | 0.00034676
131 | 0.9914 | -0.16344 | 0.0013019 | 0.00032629
132 | 0.9914 | -0.16355 | 0 | 0
133 | 0.99138 | -0.16393 | 0.0013127 | 0.000329
134 | 0.99098 | -0.17139 | 0.0013414 | 0.00033618
135 | 0.98574 | -0.2737 | 0.0057195 | 0.0014334
136 | 0.98536 | -0.28093 | 0.0083883 | 0.0021023
137 | 0.98274 | -0.33203 | 0 | 0
138 | 0.98263 | -0.33431 | 0.0038849 | 0.00097365
139 | 0.9825 | -0.33672 | 0.0053662 | 0.0013449
140 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.1805 | -0.045738 | 0.18074 | 0.045891 | 0.00024084 | 0.00015232 | 0.2707 | 0.2707 | 0.2707 | 0.99284 | -0.13641 | 0.99429 | -0.10867 | 18.5921
1 | 0.1717 | 0.043531 | -0.17155 | -0.043442 | 0.00014198 | 8.9684e-05 | 0.2575 | 0.2575 | 0.2575 | 0.99284 | -0.13641 | 0.99195 | -0.15363 | 17.6858
2 | -0.18752 | -0.047589 | 0.18767 | 0.047685 | 0.00015081 | 9.5457e-05 | 0.28085 | 0.28084 | 0.28085 | 0.99429 | -0.10867 | 0.99516 | -0.091969 | 19.2888
3 | 0.012975 | 0.0032533 | -0.012969 | -0.0032502 | 5.6673e-06 | 3.1124e-06 | 0.019464 | 0.019464 | 0.019464 | 0.99195 | -0.15363 | 0.99147 | -0.1628 | 5.3473
4 | 0.15858 | 0.040188 | -0.15838 | -0.040062 | 0.00020056 | 0.00012641 | 0.23804 | 0.23804 | 0.23804 | 0.99195 | -0.15363 | 0.99058 | -0.17998 | 16.349
5 | -0.23505 | -0.059599 | 0.23514 | 0.059659 | 9.3926e-05 | 5.9691e-05 | 0.3517 | 0.3517 | 0.3517 | 0.99516 | -0.091969 | 0.9956 | -0.083659 | 24.1549
6 | 0.047375 | 0.011915 | -0.04736 | -0.011905 | 1.4344e-05 | 9.0815e-06 | 0.070851 | 0.070851 | 0.070851 | 0.99516 | -0.091969 | 0.99484 | -0.09831 | 19.4647
7 | 0.0031635 | 0.0007925 | -0.0031633 | -0.00079267 | 1.9672e-07 | -1.7421e-07 | 0.0047477 | 0.0047478 | 0.0047478 | 0.99147 | -0.1628 | 0.99141 | -0.1641 | 1.3044
8 | 0.0098056 | 0.0024577 | -0.0098046 | -0.0024572 | 1.038e-06 | 4.9953e-07 | 0.014716 | 0.014717 | 0.014717 | 0.99147 | -0.1628 | 0.99136 | -0.16502 | 4.043
9 | 0.0041266 | 0.0010341 | -0.0041266 | -0.0010341 | 7.0637e-08 | -1.7896e-08 | 0.0061989 | 0.0061989 | 0.0061989 | 0.99058 | -0.17998 | 0.99056 | -0.18034 | 1.703
10 | 0.15425 | 0.039028 | -0.15406 | -0.038909 | 0.00018906 | 0.00011907 | 0.23184 | 0.23184 | 0.23184 | 0.99058 | -0.17998 | 0.98925 | -0.20556 | 15.9233
11 | -0.2399 | -0.060852 | 0.23993 | 0.060873 | 3.3445e-05 | 2.1261e-05 | 0.35881 | 0.35881 | 0.35881 | 0.9956 | -0.083659 | 0.99575 | -0.08076 | 24.6436
12 | 0.0047601 | 0.0011929 | -0.0047598 | -0.0011929 | 3.3303e-07 | -1.501e-08 | 0.0071144 | 0.0071145 | 0.0071145 | 0.9956 | -0.083659 | 0.99552 | -0.085128 | 1.9545
13 | 0.04736 | 0.011905 | -0.047342 | -0.011894 | 1.8624e-05 | 1.1791e-05 | 0.070851 | 0.070852 | 0.070852 | 0.99484 | -0.09831 | 0.99441 | -0.10655 | 19.4647
14 | 0.0031633 | 0.00079267 | -0.0031632 | -0.00079278 | 1.1761e-07 | -1.0412e-07 | 0.0047478 | 0.0047479 | 0.0047479 | 0.99141 | -0.1641 | 0.99137 | -0.16488 | 1.3044
15 | 0.0057338 | 0.0014369 | -0.0057326 | -0.0014367 | 1.1601e-06 | 2.0406e-07 | 0.0086063 | 0.0086065 | 0.0086065 | 0.99136 | -0.16502 | 0.99114 | -0.16926 | 2.3644
16 | 0.0041266 | 0.0010341 | -0.0041263 | -0.0010342 | 2.4575e-07 | -6.2239e-08 | 0.0061989 | 0.006199 | 0.006199 | 0.99056 | -0.18034 | 0.9905 | -0.18159 | 1.703
17 | 0.15179 | 0.03834 | -0.15169 | -0.038275 | 0.00010243 | 6.4479e-05 | 0.22843 | 0.22843 | 0.22843 | 0.98925 | -0.20556 | 0.98852 | -0.21965 | 15.6887
18 | 0.006132 | 0.0015367 | -0.0061317 | -0.0015366 | 3.5514e-07 | 9.2672e-08 | 0.0093625 | 0.0093625 | 0.0093625 | 0.97458 | -0.48909 | 0.97452 | -0.4903 | 2.5721
19 | 0.013296 | 0.0033326 | -0.013296 | -0.0033323 | 6.4648e-07 | 3.6163e-07 | 0.020301 | 0.020301 | 0.020301 | 0.97458 | -0.48909 | 0.97453 | -0.49011 | 5.5772
20 | -0.019428 | -0.0048693 | 0.019431 | 0.004871 | 2.8125e-06 | 1.6937e-06 | 0.029664 | 0.029663 | 0.029664 | 0.97458 | -0.48909 | 0.97474 | -0.48605 | 8.1493
21 | 0.0032855 | 0.00082327 | -0.0032853 | -0.00082338 | 1.6289e-07 | -1.1078e-07 | 0.0050167 | 0.0050167 | 0.0050167 | 0.97452 | -0.4903 | 0.97447 | -0.49134 | 1.3782
22 | 0.0091507 | 0.0022936 | -0.0091489 | -0.0022927 | 1.767e-06 | 8.3021e-07 | 0.013972 | 0.013972 | 0.013972 | 0.97453 | -0.49011 | 0.97432 | -0.49416 | 3.8386
23 | 0.0041448 | 0.0010387 | -0.0041446 | -0.0010387 | 1.7368e-07 | -3.2911e-08 | 0.0063287 | 0.0063288 | 0.0063288 | 0.97453 | -0.49011 | 0.97448 | -0.49099 | 1.7387
24 | 0.047994 | 0.012077 | -0.047917 | -0.012028 | 7.7349e-05 | 4.9026e-05 | 0.073284 | 0.073285 | 0.073285 | 0.97474 | -0.48605 | 0.97302 | -0.51983 | 20.1331
25 | 0.0073242 | 0.0018357 | -0.0073237 | -0.0018355 | 4.3079e-07 | 1.6117e-07 | 0.011181 | 0.011181 | 0.011181 | 0.97474 | -0.48605 | 0.97467 | -0.48728 | 3.0717
26 | -0.074749 | -0.018784 | 0.074857 | 0.018853 | 0.00010772 | 6.8663e-05 | 0.11413 | 0.11413 | 0.11413 | 0.97474 | -0.48605 | 0.97627 | -0.45591 | 31.3541
27 | 0.0057806 | 0.0014486 | -0.0057801 | -0.0014484 | 5.3447e-07 | 1.1434e-07 | 0.0088283 | 0.0088283 | 0.0088283 | 0.97432 | -0.49416 | 0.97423 | -0.4961 | 2.4254
28 | 0.090752 | 0.023019 | -0.090725 | -0.023002 | 2.7085e-05 | 1.7286e-05 | 0.13761 | 0.13761 | 0.13761 | 0.98201 | -0.34382 | 0.98169 | -0.35003 | 37.8056
29 | -0.090752 | -0.023019 | 0.090965 | 0.023155 | 0.0002127 | 0.00013575 | 0.13761 | 0.13761 | 0.13761 | 0.98201 | -0.34382 | 0.98453 | -0.2952 | 37.8056
30 | 0.090725 | 0.023002 | -0.090484 | -0.022848 | 0.00024106 | 0.00015385 | 0.13761 | 0.13761 | 0.13761 | 0.98169 | -0.35003 | 0.97885 | -0.40547 | 37.8056
31 | -0.093605 | -0.023817 | 0.093656 | 0.023849 | 5.0626e-05 | 3.2315e-05 | 0.1416 | 0.1416 | 0.1416 | 0.98453 | -0.2952 | 0.98511 | -0.28398 | 38.9021
32 | -0.24312 | -0.061672 | 0.24334 | 0.061813 | 0.0002216 | 0.00014089 | 0.36357 | 0.36357 | 0.36357 | 0.99575 | -0.08076 | 0.99674 | -0.061823 | 24.9706
33 | 0.033126 | 0.0083206 | -0.033083 | -0.0082934 | 4.3317e-05 | 2.7165e-05 | 0.050666 | 0.050666 | 0.050666 | 0.97302 | -0.51983 | 0.97163 | -0.54728 | 13.9192
34 | 0.01479 | 0.0037077 | -0.014788 | -0.0037061 | 2.7278e-06 | 1.5692e-06 | 0.022619 | 0.022619 | 0.022619 | 0.97302 | -0.51983 | 0.97282 | -0.52371 | 6.214
35 | -0.082417 | -0.020747 | 0.082466 | 0.020779 | 4.9024e-05 | 3.1272e-05 | 0.12565 | 0.12565 | 0.12565 | 0.97627 | -0.45591 | 0.9769 | -0.44347 | 34.5198
36 | -0.0013355 | -0.0003346 | 0.0013355 | 0.00033457 | 3.9105e-09 | -3.0697e-08 | 0.0020085 | 0.0020085 | 0.0020085 | 0.98942 | -0.20126 | 0.98942 | -0.2012 | 0.55178
37 | 0.0013355 | 0.0003346 | -0.0013355 | -0.00033471 | 1.4101e-08 | -1.1069e-07 | 0.0020085 | 0.0020085 | 0.0020085 | 0.98942 | -0.20126 | 0.98941 | -0.20148 | 0.55179
38 | -0.10227 | -0.026161 | 0.10238 | 0.026234 | 0.00011481 | 7.2815e-05 | 0.154 | 0.15399 | 0.154 | 0.98942 | -0.2012 | 0.99064 | -0.17803 | 21.1532
39 | 0.10093 | 0.025826 | -0.10084 | -0.025765 | 9.5735e-05 | 6.1129e-05 | 0.15199 | 0.15199 | 0.15199 | 0.98942 | -0.2012 | 0.9884 | -0.22081 | 41.7546
40 | 0.044509 | 0.011184 | -0.044455 | -0.011149 | 5.4205e-05 | 3.4269e-05 | 0.066613 | 0.066613 | 0.066613 | 0.99441 | -0.10655 | 0.99309 | -0.1321 | 18.3002
41 | -0.10418 | -0.026683 | 0.1042 | 0.026695 | 1.9713e-05 | 1.2175e-05 | 0.15669 | 0.15669 | 0.15669 | 0.99064 | -0.17803 | 0.99084 | -0.17413 | 10.7615
42 | 0.099638 | 0.025464 | -0.099471 | -0.025358 | 0.00016721 | 0.00010676 | 0.15018 | 0.15018 | 0.15018 | 0.9884 | -0.22081 | 0.98659 | -0.25557 | 41.2582
43 | -0.15712 | -0.040213 | 0.15717 | 0.040247 | 5.4351e-05 | 3.4237e-05 | 0.23494 | 0.23494 | 0.23494 | 0.99637 | -0.068964 | 0.99674 | -0.061823 | 16.1361
44 | 0.15712 | 0.040213 | -0.15704 | -0.040165 | 7.5537e-05 | 4.7584e-05 | 0.23494 | 0.23494 | 0.23494 | 0.99637 | -0.068964 | 0.99584 | -0.078898 | 16.1361
45 | -0.40051 | -0.10206 | 0.40162 | 0.10277 | 0.0011066 | 0.00070647 | 0.59851 | 0.59851 | 0.59851 | 0.99674 | -0.061823 | 0.99975 | -0.004739 | 41.1066
46 | 0.15704 | 0.040165 | -0.15697 | -0.040121 | 6.9603e-05 | 4.3847e-05 | 0.23494 | 0.23494 | 0.23494 | 0.99584 | -0.078898 | 0.99536 | -0.088061 | 16.1362
47 | -0.45107 | -0.11516 | 0.45117 | 0.11522 | 0.00010333 | 6.6001e-05 | 0.67211 | 0.67211 | 0.67211 | 0.99975 | -0.004739 | 1 | 0 | 46.1613
48 | 0.15412 | 0.039408 | -0.15411 | -0.039397 | 1.6917e-05 | 1.0651e-05 | 0.23069 | 0.23069 | 0.23069 | 0.99536 | -0.088061 | 0.99524 | -0.09033 | 15.8438
49 | 0.087931 | 0.022205 | -0.087895 | -0.022182 | 3.6374e-05 | 2.3211e-05 | 0.13374 | 0.13374 | 0.13374 | 0.97875 | -0.40734 | 0.97831 | -0.41598 | 36.7429
50 | -0.087931 | -0.022205 | 0.087939 | 0.02221 | 7.8966e-06 | 5.039e-06 | 0.13374 | 0.13374 | 0.13374 | 0.97875 | -0.40734 | 0.97885 | -0.40547 | 36.7429
51 | 0.085212 | 0.02151 | -0.085154 | -0.021473 | 5.7616e-05 | 3.6759e-05 | 0.12966 | 0.12966 | 0.12966 | 0.97831 | -0.41598 | 0.97759 | -0.43011 | 35.6219
52 | -0.082466 | -0.020779 | 0.082519 | 0.020812 | 5.2773e-05 | 3.3663e-05 | 0.12565 | 0.12565 | 0.12565 | 0.9769 | -0.44347 | 0.97759 | -0.43011 | 34.5198
53 | 0.0026356 | 0.00066048 | -0.0026356 | -0.00066053 | 3.5841e-08 | -5.1518e-08 | 0.0040117 | 0.0040117 | 0.0040117 | 0.97759 | -0.43011 | 0.97757 | -0.43039 | 1.1021
54 | 0.0013636 | 0.00034115 | -0.0013635 | -0.00034172 | 7.4869e-08 | -5.6898e-07 | 0.0020445 | 0.0020447 | 0.0020447 | 0.9923 | -0.14724 | 0.99225 | -0.14839 | 0.56174
55 | -0.0013636 | -0.00034115 | 0.0013636 | 0.00034061 | 7.128e-08 | -5.4189e-07 | 0.0020445 | 0.0020443 | 0.0020445 | 0.9923 | -0.14724 | 0.99236 | -0.14614 | 0.56168
56 | -0.0030276 | -0.00075764 | 0.0030276 | 0.00075759 | 4.8981e-08 | -5.0548e-08 | 0.0045394 | 0.0045394 | 0.0045394 | 0.99236 | -0.14614 | 0.99238 | -0.1458 | 1.2471
57 | 0.026363 | 0.0066147 | -0.026358 | -0.0066114 | 5.206e-06 | 3.2209e-06 | 0.039864 | 0.039864 | 0.039864 | 0.98414 | -0.30469 | 0.98393 | -0.30883 | 10.9517
58 | -0.029598 | -0.0074251 | 0.029607 | 0.0074311 | 9.6308e-06 | 6.0007e-06 | 0.044754 | 0.044754 | 0.044754 | 0.98414 | -0.30469 | 0.98449 | -0.29787 | 12.2951
59 | 0.0032342 | 0.00081048 | -0.0032341 | -0.00081055 | 8.8561e-08 | -6.8805e-08 | 0.0048901 | 0.0048901 | 0.0048901 | 0.98414 | -0.30469 | 0.98411 | -0.30526 | 1.3434
60 | 0.0052226 | 0.0013088 | -0.0052222 | -0.0013088 | 3.8804e-07 | 3.7678e-08 | 0.0078981 | 0.0078982 | 0.0078982 | 0.98393 | -0.30883 | 0.98385 | -0.31039 | 2.1698
61 | 0.021136 | 0.0053026 | -0.021134 | -0.0053016 | 1.6232e-06 | 9.8503e-07 | 0.031966 | 0.031966 | 0.031966 | 0.98393 | -0.30883 | 0.98385 | -0.31044 | 8.7818
62 | 0.039653 | 0.010015 | -0.039524 | -0.0099332 | 0.0001297 | 8.1791e-05 | 0.059962 | 0.059962 | 0.059962 | 0.98449 | -0.29787 | 0.98098 | -0.36636 | 16.4731
63 | -0.069261 | -0.017446 | 0.069267 | 0.01745 | 6.5607e-06 | 4.1786e-06 | 0.10472 | 0.10472 | 0.10472 | 0.98449 | -0.29787 | 0.98459 | -0.29589 | 28.768
64 | 0.021134 | 0.0053016 | -0.021124 | -0.0052953 | 1.0357e-05 | 6.2851e-06 | 0.031966 | 0.031966 | 0.031966 | 0.98385 | -0.31044 | 0.98332 | -0.32073 | 8.7819
65 | 0.0092577 | 0.0023214 | -0.0092557 | -0.0023205 | 2.0116e-06 | 9.4082e-07 | 0.01401 | 0.01401 | 0.01401 | 0.98332 | -0.32073 | 0.98309 | -0.32529 | 3.8489
66 | 0.039524 | 0.0099332 | -0.039451 | -0.0098873 | 7.2699e-05 | 4.5848e-05 | 0.059962 | 0.059962 | 0.059962 | 0.98098 | -0.36636 | 0.97901 | -0.40497 | 16.4732
67 | -0.085761 | -0.021584 | 0.085762 | 0.021585 | 1.5679e-06 | 1.0003e-06 | 0.12964 | 0.12964 | 0.12964 | 0.98459 | -0.29589 | 0.98461 | -0.2955 | 35.616
68 | 0.14924 | 0.037661 | -0.14914 | -0.0376 | 9.679e-05 | 6.0898e-05 | 0.22474 | 0.22474 | 0.22474 | 0.98852 | -0.21965 | 0.98782 | -0.2332 | 15.4355
69 | 0.0028294 | 0.00070894 | -0.0028293 | -0.00070909 | 1.2925e-07 | -1.4706e-07 | 0.0043216 | 0.0043216 | 0.0043216 | 0.97423 | -0.4961 | 0.97418 | -0.49706 | 1.1873
70 | -0.096394 | -0.024535 | 0.096526 | 0.02462 | 0.00013222 | 8.4408e-05 | 0.14574 | 0.14574 | 0.14574 | 0.98511 | -0.28398 | 0.98659 | -0.25557 | 40.0382
71 | 0.026414 | 0.0066219 | -0.026411 | -0.0066205 | 2.3983e-06 | 1.4865e-06 | 0.040452 | 0.040452 | 0.040452 | 0.97163 | -0.54728 | 0.97153 | -0.54918 | 11.1132
72 | 0.025644 | 0.0064335 | -0.025636 | -0.0064287 | 7.8024e-06 | 4.8113e-06 | 0.038426 | 0.038427 | 0.038427 | 0.99309 | -0.1321 | 0.99276 | -0.13848 | 10.5567
73 | 0.018811 | 0.0047159 | -0.018809 | -0.0047148 | 1.8986e-06 | 1.1326e-06 | 0.028186 | 0.028186 | 0.028186 | 0.99309 | -0.1321 | 0.99298 | -0.13421 | 7.7435
74 | -0.10552 | -0.027026 | 0.10553 | 0.027035 | 1.4008e-05 | 8.6591e-06 | 0.15867 | 0.15867 | 0.15867 | 0.99084 | -0.17413 | 0.99098 | -0.17139 | 10.8977
75 | 0.10087 | 0.025463 | -0.10064 | -0.02532 | 0.00022274 | 0.00014221 | 0.15015 | 0.15015 | 0.15015 | 1 | 0 | 0.99759 | -0.04621 | 41.251
76 | 0.15043 | 0.038476 | -0.15035 | -0.038422 | 8.5781e-05 | 5.3963e-05 | 0.22519 | 0.22519 | 0.22519 | 0.99524 | -0.09033 | 0.99462 | -0.10212 | 15.4663
77 | -0.0045076 | -0.0011285 | 0.0045077 | 0.0011285 | 3.0802e-08 | -3.5204e-09 | 0.0067585 | 0.0067585 | 0.0067585 | 0.99238 | -0.1458 | 0.99239 | -0.14565 | 1.8567
78 | -0.0021579 | -0.00054083 | 0.002158 | 0.00054073 | 3.4588e-08 | -9.1936e-08 | 0.0032339 | 0.0032339 | 0.0032339 | 0.99291 | -0.13472 | 0.99293 | -0.13439 | 0.88845
79 | 0.0031974 | 0.00080108 | -0.0031972 | -0.00080124 | 1.878e-07 | -1.6191e-07 | 0.0047916 | 0.0047917 | 0.0047917 | 0.99293 | -0.13439 | 0.99287 | -0.13562 | 1.3164
80 | -0.0053554 | -0.0013418 | 0.0053557 | 0.0013418 | 3.0971e-07 | 3.2348e-08 | 0.0080255 | 0.0080254 | 0.0080255 | 0.99293 | -0.13439 | 0.99299 | -0.13317 | 2.2048
81 | 0.0092557 | 0.0023205 | -0.0092527 | -0.0023191 | 2.9727e-06 | 1.3906e-06 | 0.01401 | 0.01401 | 0.01401 | 0.98309 | -0.32529 | 0.98274 | -0.33203 | 3.8489
82 | -0.093323 | -0.02348 | 0.093388 | 0.023521 | 6.5051e-05 | 4.1521e-05 | 0.14107 | 0.14107 | 0.14107 | 0.98461 | -0.2955 | 0.98536 | -0.28093 | 38.7551
83 | -0.0030155 | -0.00075575 | 0.0030156 | 0.00075562 | 1.2318e-07 | -1.2942e-07 | 0.004518 | 0.0045179 | 0.004518 | 0.99316 | -0.13159 | 0.99321 | -0.13073 | 1.2412
84 | 0.0089366 | 0.0022398 | -0.0089361 | -0.0022395 | 5.0646e-07 | 2.2664e-07 | 0.013389 | 0.013389 | 0.013389 | 0.99321 | -0.13073 | 0.99314 | -0.13192 | 3.6783
85 | -0.011952 | -0.0029954 | 0.011952 | 0.0029955 | 2.3159e-07 | 1.2329e-07 | 0.017907 | 0.017907 | 0.017907 | 0.99321 | -0.13073 | 0.99323 | -0.13033 | 4.9194
86 | -0.0090751 | -0.0022744 | 0.009076 | 0.0022749 | 9.5033e-07 | 4.4595e-07 | 0.013904 | 0.013904 | 0.013904 | 0.97125 | -0.55484 | 0.97136 | -0.55264 | 3.8197
87 | -0.017728 | -0.0044432 | 0.017731 | 0.0044449 | 2.9217e-06 | 1.7391e-06 | 0.027157 | 0.027157 | 0.027157 | 0.97136 | -0.55264 | 0.97153 | -0.54918 | 7.4607
88 | -0.0016644 | -0.00041714 | 0.0016644 | 0.00041707 | 1.3939e-08 | -6.8422e-08 | 0.0024938 | 0.0024938 | 0.0024938 | 0.99314 | -0.1321 | 0.99314 | -0.13192 | 0.6851
89 | 0.092684 | 0.023326 | -0.092624 | -0.023287 | 6.014e-05 | 3.838e-05 | 0.13828 | 0.13828 | 0.13828 | 0.99759 | -0.04621 | 0.99688 | -0.059797 | 37.9898
90 | 0.084338 | 0.021211 | -0.084285 | -0.021177 | 5.3493e-05 | 3.4118e-05 | 0.12592 | 0.12592 | 0.12592 | 0.99688 | -0.059797 | 0.99619 | -0.073085 | 34.5921
91 | 0.076019 | 0.019105 | -0.076017 | -0.019104 | 2.0719e-06 | 1.3205e-06 | 0.11357 | 0.11357 | 0.11357 | 0.99619 | -0.073085 | 0.99616 | -0.073656 | 31.2003
92 | 0.072434 | 0.018206 | -0.072385 | -0.018175 | 4.9144e-05 | 3.1306e-05 | 0.10822 | 0.10822 | 0.10822 | 0.99616 | -0.073656 | 0.99542 | -0.087877 | 29.7297
93 | 0.058386 | 0.014666 | -0.058355 | -0.014647 | 3.053e-05 | 1.94e-05 | 0.08729 | 0.08729 | 0.08729 | 0.99542 | -0.087877 | 0.99486 | -0.09884 | 23.9807
94 | 0.04929 | 0.012375 | -0.049249 | -0.012349 | 4.1133e-05 | 2.6064e-05 | 0.073731 | 0.073731 | 0.073731 | 0.99486 | -0.09884 | 0.99395 | -0.11635 | 20.2558
95 | 0.037791 | 0.0094771 | -0.037787 | -0.0094743 | 4.507e-06 | 2.8359e-06 | 0.056578 | 0.056578 | 0.056578 | 0.99395 | -0.11635 | 0.99382 | -0.11885 | 15.5435
96 | 0.023706 | 0.0059454 | -0.023699 | -0.0059408 | 7.4856e-06 | 4.5856e-06 | 0.035496 | 0.035496 | 0.035496 | 0.99382 | -0.11885 | 0.99348 | -0.12548 | 9.7517
97 | 0.018864 | 0.004729 | -0.018859 | -0.0047264 | 4.3567e-06 | 2.5999e-06 | 0.028254 | 0.028254 | 0.028254 | 0.99348 | -0.12548 | 0.99323 | -0.13033 | 7.7622
98 | 0.006907 | 0.0017309 | -0.0069064 | -0.0017308 | 5.1352e-07 | 1.6315e-07 | 0.010348 | 0.010348 | 0.010348 | 0.99323 | -0.13033 | 0.99315 | -0.13189 | 2.8428
99 | 0.003469 | 0.00086925 | -0.0034688 | -0.00086936 | 1.7214e-07 | -1.097e-07 | 0.0051974 | 0.0051975 | 0.0051975 | 0.99315 | -0.13189 | 0.99309 | -0.13293 | 1.4279
100 | 0.14153 | 0.035692 | -0.14145 | -0.035645 | 7.4305e-05 | 4.7332e-05 | 0.21327 | 0.21327 | 0.21327 | 0.98782 | -0.2332 | 0.98726 | -0.24418 | 29.2956
101 | 0.13313 | 0.033559 | -0.13311 | -0.033545 | 2.1562e-05 | 1.3781e-05 | 0.20073 | 0.20073 | 0.20073 | 0.98726 | -0.24418 | 0.98708 | -0.24756 | 55.1451
102 | 0.11667 | 0.029424 | -0.11658 | -0.029367 | 8.9805e-05 | 5.7377e-05 | 0.17594 | 0.17594 | 0.17594 | 0.98708 | -0.24756 | 0.98625 | -0.26365 | 48.3355
103 | 0.10758 | 0.027113 | -0.10753 | -0.02708 | 5.1675e-05 | 3.3005e-05 | 0.16237 | 0.16237 | 0.16237 | 0.98625 | -0.26365 | 0.98574 | -0.2737 | 44.607
104 | 0.015632 | 0.0039186 | -0.015628 | -0.0039163 | 3.9905e-06 | 2.3032e-06 | 0.023426 | 0.023426 | 0.023426 | 0.99298 | -0.13421 | 0.9927 | -0.13957 | 6.4357
105 | 0.013667 | 0.0034248 | -0.013665 | -0.0034238 | 1.8378e-06 | 1.0253e-06 | 0.020487 | 0.020487 | 0.020487 | 0.9927 | -0.13957 | 0.99255 | -0.1424 | 5.6282
106 | 0.0090756 | 0.0022735 | -0.0090752 | -0.0022733 | 3.389e-07 | 1.538e-07 | 0.013606 | 0.013606 | 0.013606 | 0.99255 | -0.1424 | 0.99251 | -0.14318 | 3.7378
107 | 0.023267 | 0.005835 | -0.023265 | -0.0058338 | 1.9521e-06 | 1.194e-06 | 0.034876 | 0.034876 | 0.034876 | 0.99276 | -0.13848 | 0.99267 | -0.14024 | 9.5813
108 | 0.0078887 | 0.0019759 | -0.0078883 | -0.0019758 | 3.3679e-07 | 1.3257e-07 | 0.011827 | 0.011827 | 0.011827 | 0.99251 | -0.14318 | 0.99247 | -0.14408 | 3.2491
109 | 0.016794 | 0.004212 | -0.016787 | -0.0042081 | 6.547e-06 | 3.8341e-06 | 0.025175 | 0.025176 | 0.025176 | 0.99267 | -0.14024 | 0.99224 | -0.14842 | 6.9164
110 | 0.0066929 | 0.0016762 | -0.0066924 | -0.001676 | 5.0189e-07 | 1.4945e-07 | 0.010034 | 0.010034 | 0.010034 | 0.99247 | -0.14408 | 0.99239 | -0.14565 | 2.7567
111 | 0.014369 | 0.0036019 | -0.014368 | -0.0036017 | 4.3437e-07 | 2.4577e-07 | 0.021548 | 0.021548 | 0.021548 | 0.99224 | -0.14842 | 0.99221 | -0.14906 | 5.9198
112 | -0.002644 | -0.00066265 | 0.002644 | 0.00066264 | 8.9554e-10 | -1.3853e-09 | 0.0039667 | 0.0039667 | 0.0039667 | 0.99184 | -0.15618 | 0.99184 | -0.15617 | 1.0897
113 | -0.0052029 | -0.001304 | 0.0052033 | 0.001304 | 3.1821e-07 | 2.3898e-08 | 0.0078057 | 0.0078057 | 0.0078057 | 0.99184 | -0.15617 | 0.99191 | -0.15489 | 2.1444
114 | -0.0065667 | -0.0016457 | 0.006567 | 0.0016458 | 2.3093e-07 | 6.5882e-08 | 0.0098511 | 0.0098511 | 0.0098511 | 0.99191 | -0.15489 | 0.99195 | -0.15415 | 2.7063
115 | 0.013104 | 0.0032849 | -0.013103 | -0.0032844 | 9.9328e-07 | 5.4713e-07 | 0.019653 | 0.019653 | 0.019653 | 0.99221 | -0.14906 | 0.99213 | -0.15065 | 5.3991
116 | 0.011203 | 0.0028082 | -0.011202 | -0.0028076 | 1.2828e-06 | 6.6456e-07 | 0.016803 | 0.016803 | 0.016803 | 0.99213 | -0.15065 | 0.992 | -0.15305 | 4.6163
117 | 0.0086292 | 0.0021627 | -0.0086288 | -0.0021625 | 4.5148e-07 | 1.9618e-07 | 0.012944 | 0.012944 | 0.012944 | 0.992 | -0.15305 | 0.99195 | -0.15415 | 3.556
118 | 0.14566 | 0.037248 | -0.14562 | -0.037222 | 4.063e-05 | 2.5531e-05 | 0.21818 | 0.21818 | 0.21818 | 0.99462 | -0.10212 | 0.99432 | -0.10789 | 14.9852
119 | 0.14042 | 0.035918 | -0.14036 | -0.035883 | 5.5857e-05 | 3.5051e-05 | 0.2104 | 0.2104 | 0.2104 | 0.99432 | -0.10789 | 0.99389 | -0.11611 | 14.4505
120 | 0.13573 | 0.034722 | -0.13565 | -0.034672 | 8.0046e-05 | 5.0161e-05 | 0.20346 | 0.20346 | 0.20346 | 0.99389 | -0.11611 | 0.99325 | -0.1283 | 13.9739
121 | 0.13161 | 0.03366 | -0.1316 | -0.033654 | 9.9431e-06 | 6.2227e-06 | 0.19741 | 0.19741 | 0.19741 | 0.99325 | -0.1283 | 0.99316 | -0.12986 | 13.5585
122 | 0.010072 | 0.0025243 | -0.01007 | -0.0025235 | 1.5888e-06 | 7.7612e-07 | 0.015091 | 0.015091 | 0.015091 | 0.99316 | -0.12986 | 0.99299 | -0.13317 | 4.1458
123 | 0.12153 | 0.031129 | -0.12149 | -0.031105 | 3.8416e-05 | 2.3948e-05 | 0.18232 | 0.18232 | 0.18232 | 0.99316 | -0.12986 | 0.99282 | -0.13639 | 12.5221
124 | 0.11818 | 0.030275 | -0.11814 | -0.030255 | 3.2859e-05 | 2.0454e-05 | 0.17736 | 0.17736 | 0.17736 | 0.99282 | -0.13639 | 0.99252 | -0.14213 | 12.1811
125 | 0.11681 | 0.029921 | -0.11679 | -0.029905 | 2.5658e-05 | 1.5961e-05 | 0.17536 | 0.17536 | 0.17536 | 0.99252 | -0.14213 | 0.99228 | -0.14666 | 12.044
126 | 0.0016283 | 0.00040804 | -0.0016283 | -0.0004081 | 1.0818e-08 | -5.5721e-08 | 0.0024404 | 0.0024404 | 0.0024404 | 0.99287 | -0.13562 | 0.99286 | -0.13576 | 0.67044
127 | 0.11549 | 0.02958 | -0.11547 | -0.029565 | 2.3546e-05 | 1.4638e-05 | 0.17342 | 0.17342 | 0.17342 | 0.99228 | -0.14666 | 0.99206 | -0.15087 | 11.9104
128 | 0.1141 | 0.029222 | -0.11404 | -0.029188 | 5.4421e-05 | 3.3809e-05 | 0.17136 | 0.17136 | 0.17136 | 0.99206 | -0.15087 | 0.99154 | -0.16072 | 11.7694
129 | 0.11274 | 0.028863 | -0.11274 | -0.028858 | 8.065e-06 | 5.0069e-06 | 0.16941 | 0.16941 | 0.16941 | 0.99154 | -0.16072 | 0.99147 | -0.1622 | 11.6355
130 | 0.10874 | 0.027856 | -0.10872 | -0.027845 | 1.7322e-05 | 1.0729e-05 | 0.16341 | 0.16341 | 0.16341 | 0.99147 | -0.1622 | 0.99129 | -0.16549 | 11.2234
131 | 0.0039985 | 0.0010017 | -0.0039983 | -0.0010017 | 1.5575e-07 | -4.9056e-08 | 0.0060008 | 0.0060009 | 0.0060009 | 0.99147 | -0.1622 | 0.99142 | -0.16302 | 1.6486
132 | 0.1069 | 0.02739 | -0.10687 | -0.027371 | 3.0562e-05 | 1.8909e-05 | 0.16068 | 0.16068 | 0.16068 | 0.99129 | -0.16549 | 0.99098 | -0.17139 | 11.036
133 | 0.0026147 | 0.00065496 | -0.0026147 | -0.00065504 | 5.3234e-08 | -8.4796e-08 | 0.0039243 | 0.0039243 | 0.0039243 | 0.99142 | -0.16302 | 0.9914 | -0.16344 | 1.0781
134 | 0.0013127 | 0.00032875 | -0.0013127 | -0.00032881 | 6.8758e-09 | -5.6506e-08 | 0.0019702 | 0.0019703 | 0.0019703 | 0.9914 | -0.16344 | 0.9914 | -0.16355 | 0.54128
135 | 0.0013127 | 0.00032881 | -0.0013127 | -0.000329 | 2.3225e-08 | -1.9085e-07 | 0.0019703 | 0.0019703 | 0.0019703 | 0.9914 | -0.16355 | 0.99138 | -0.16393 | 0.5413
136 | 0.10181 | 0.025646 | -0.10178 | -0.025624 | 3.5171e-05 | 2.2459e-05 | 0.15374 | 0.15374 | 0.15374 | 0.98574 | -0.2737 | 0.98536 | -0.28093 | 42.2351
137 | 0.0092527 | 0.0023191 | -0.0092517 | -0.0023186 | 1.0057e-06 | 4.7052e-07 | 0.01401 | 0.01401 | 0.01401 | 0.98274 | -0.33203 | 0.98263 | -0.33431 | 3.8489
138 | 0.0053668 | 0.001345 | -0.0053662 | -0.0013449 | 6.1553e-07 | 7.9178e-08 | 0.008127 | 0.0081271 | 0.0081271 | 0.98263 | -0.33431 | 0.9825 | -0.33672 | 2.2327

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.57728 | 0.1466

## res_load
| p_mw | q_mvar
0 | 0.0088053 | 0.0022068
1 | 0.0067785 | 0.0016989
2 | 0.0040708 | 0.0010202
3 | 0.0022709 | 0.00056914
4 | 0.0028462 | 0.00071331
5 | 0.0033683 | 0.00084418
6 | 0.0041446 | 0.0010387
7 | 0.0026409 | 0.00066186
8 | 0.0031862 | 0.00079854
9 | 0.0047598 | 0.0011929
10 | 0.0073237 | 0.0018355
11 | 0.0075602 | 0.0018948
12 | 0.0013355 | 0.00033471
13 | 0.0028327 | 0.00070994
14 | 0.0017922 | 0.00044918
15 | 0.0012002 | 0.0003008
16 | 0.049448 | 0.012393
17 | 0.002847 | 0.00071353
18 | 0.0026828 | 0.00067238
19 | 0.0025446 | 0.00063774
20 | 0.0026356 | 0.00066053
21 | 0.0013635 | 0.00034172
22 | 0.001664 | 0.00041703
23 | 0.0032341 | 0.00081055
24 | 0.011866 | 0.0029739
25 | 0.0031632 | 0.00079278
26 | 0.016494 | 0.0041337
27 | 0.039451 | 0.0098873
28 | 0.0057326 | 0.0014367
29 | 0.0041263 | 0.0010342
30 | 0.0024497 | 0.00061395
31 | 0.0032853 | 0.00082338
32 | 0.0029507 | 0.0007395
33 | 0.0027379 | 0.00068618
34 | 0.0066693 | 0.0016715
35 | 0.014788 | 0.0037061
36 | 0.0013209 | 0.00033104
37 | 0.0029445 | 0.00073795
38 | 0.023592 | 0.0059126
39 | 0.0036765 | 0.00092141
40 | 0.0028293 | 0.00070909
41 | 0.00148 | 0.00037092
42 | 0.0052222 | 0.0013088
43 | 0.0021579 | 0.00054083
44 | 0.0075607 | 0.0018949
45 | 0.0030155 | 0.00075575
46 | 0.0090751 | 0.0022744
47 | 0.0086517 | 0.0021683
48 | 0.0016644 | 0.00041714
49 | 0.0072717 | 0.0018225
50 | 0.0086805 | 0.0021755
51 | 0.0079583 | 0.0019945
52 | 0.0082857 | 0.0020766
53 | 0.0082653 | 0.0020715
54 | 0.0035836 | 0.00089814
55 | 0.013999 | 0.0035085
56 | 0.0090651 | 0.0022719
57 | 0.011457 | 0.0028715
58 | 0.01408 | 0.0035289
59 | 0.0048351 | 0.0012118
60 | 0.0034375 | 0.00086151
61 | 0.0034688 | 0.00086936
62 | 0.007614 | 0.0019082
63 | 0.0083223 | 0.0020858
64 | 0.016443 | 0.0041209
65 | 0.0089951 | 0.0022544
66 | 0.0031767 | 0.00079617
67 | 0.001961 | 0.00049148
68 | 0.0045899 | 0.0011503
69 | 0.0023689 | 0.0005937
70 | 0.0011866 | 0.00029738
71 | 0.0064712 | 0.0016218
72 | 0.0011955 | 0.00029961
73 | 0.0024188 | 0.00060621
74 | 0.0021847 | 0.00054754
75 | 0.002644 | 0.00066265
76 | 0.0025589 | 0.00064133
77 | 0.0013635 | 0.00034172
78 | 0.001264 | 0.00031679
79 | 0.0018998 | 0.00047612
80 | 0.002573 | 0.00064485
81 | 0.0020618 | 0.00051673
82 | 0.0046829 | 0.0011736
83 | 0.0052027 | 0.0013039
84 | 0.0046353 | 0.0011617
85 | 0.0040367 | 0.0010117
86 | 0.0047148 | 0.0011816
87 | 0.0033133 | 0.00083039
88 | 0.0013313 | 0.00033364
89 | 0.0015689 | 0.0003932
90 | 0.001297 | 0.00032507
91 | 0.0016283 | 0.0004081
92 | 0.0013689 | 0.00034307
93 | 0.0012995 | 0.00032567
94 | 0.0018175 | 0.00045551
95 | 0.0013836 | 0.00034676
96 | 0.0013019 | 0.00032629
97 | 0.0013127 | 0.000329
98 | 0.0013414 | 0.00033618
99 | 0.0057195 | 0.0014334
100 | 0.0083883 | 0.0021023
101 | 0.0038849 | 0.00097365
102 | 0.0053662 | 0.0013449

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1