## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-386_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-386_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-386_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_261-386_0_3_node_9 | 0.4 | n |  | TRUE
4 | bus_LV_261-386_0_3_node_2 | 0.4 | n |  | TRUE
5 | bus_LV_261-386_0_3_node_12 | 0.4 | n |  | TRUE
6 | bus_LV_261-386_0_3_node_13 | 0.4 | n |  | TRUE
7 | bus_LV_261-386_0_3_node_24 | 0.4 | n |  | TRUE
8 | bus_LV_261-386_0_3_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_261-386_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_261-386_0_3_node_25 | 0.4 | n |  | TRUE
11 | bus_LV_261-386_0_3_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_261-386_0_3_node_23 | 0.4 | n |  | TRUE
13 | bus_LV_261-386_0_3_node_21 | 0.4 | n |  | TRUE
14 | bus_LV_261-386_0_3_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_261-386_0_3_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_261-386_0_3_node_19 | 0.4 | n |  | TRUE
17 | bus_LV_261-386_0_3_node_26 | 0.4 | n |  | TRUE
18 | bus_LV_261-386_0_3_node_22 | 0.4 | n |  | TRUE
19 | bus_LV_261-386_0_3_node_20 | 0.4 | n |  | TRUE
20 | bus_LV_261-386_0_3_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_261-386_0_3_node_15 | 0.4 | n |  | TRUE
22 | bus_MV_530_1_node_187 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-386_0_3_load_0 | 0 | 0.032213 | 0.0080733 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-386_0_3_load_3 | 2 | 0.017364 | 0.0043518 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-386_0_3_load_12 | 5 | 0.020173 | 0.0050559 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-386_0_3_load_13 | 6 | 0.0717 | 0.01797 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-386_0_3_load_24 | 7 | 0.014531 | 0.0036419 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-386_0_3_load_25 | 10 | 0.020006 | 0.005014 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-386_0_3_load_23 | 12 | 0.0050847 | 0.0012743 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-386_0_3_load_21 | 13 | 0.020344 | 0.0050986 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-386_0_3_load_14 | 14 | 0.057984 | 0.014532 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-386_0_3_load_26 | 17 | 0.010038 | 0.0025158 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-386_0_3_load_22 | 18 | 0.029242 | 0.0073288 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-386_0_3_load_20 | 19 | 0.029867 | 0.0074855 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-386_0_3_load_18 | 20 | 0.029554 | 0.0074071 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-386_0_3_load_15 | 21 | 0.0075044 | 0.0018808 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-386_0_3_line_0 |  | 0 | 1 | 0.025966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-386_0_3_line_1 |  | 1 | 2 | 0.014767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-386_0_3_line_2 |  | 1 | 3 | 0.055809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-386_0_3_line_3 |  | 2 | 7 | 0.019608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-386_0_3_line_4 |  | 3 | 14 | 0.062708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-386_0_3_line_5 |  | 4 | 5 | 0.016492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_261-386_0_3_line_6 |  | 4 | 6 | 0.020121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-386_0_3_line_7 |  | 5 | 18 | 0.0050417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_261-386_0_3_line_8 |  | 6 | 16 | 0.042907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-386_0_3_line_9 |  | 7 | 10 | 0.020897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-386_0_3_line_10 |  | 8 | 9 | 0.003577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_261-386_0_3_line_11 |  | 8 | 10 | 0.013352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_261-386_0_3_line_12 |  | 9 | 12 | 0.025759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_261-386_0_3_line_13 |  | 11 | 12 | 0.028538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_261-386_0_3_line_14 |  | 11 | 13 | 0.017414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_261-386_0_3_line_15 |  | 13 | 19 | 0.010475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_261-386_0_3_line_16 |  | 14 | 21 | 0.1378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-386_0_3_line_17 |  | 15 | 16 | 0.03996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-386_0_3_line_18 |  | 15 | 17 | 0.02254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-386_0_3_line_19 |  | 16 | 20 | 0.021668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-386_0_3_line_20 |  | 18 | 19 | 0.019438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-386_0_3_trafo_2 | 0.63 MVA 20/0.4 kV | 22 | 4 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2682351.6386 | 1249085.3491 | 2682369.8446 | 1249066.8352
1 | 2682351.6386 | 1249085.3491 | 2682340.7563 | 1249075.3664
2 | 2682351.6386 | 1249085.3491 | 2682352.9874 | 1249091.5391 | 2682364.5014 | 1249102.5405 | 2682360.9662 | 1249105.8827 | 2682356.7732 | 1249109.8274 | 2682357.2979 | 1249110.6464 | 2682357.8108 | 1249112.3214 | 2682357.7357 | 1249113.9216 | 2682357.0366 | 1249115.324 | 2682354.0823 | 1249118.1628 | 2682358.386 | 1249122.5481 | 2682363.144 | 1249127.3955
3 | 2682340.7563 | 1249075.3664 | 2682326.3066 | 1249062.1112
4 | 2682363.144 | 1249127.3955 | 2682399.1559 | 1249093.7822 | 2682409.0703 | 1249084.6986
5 | 2682392.5399 | 1249035.2025 | 2682380.3435 | 1249024.1017
6 | 2682392.5399 | 1249035.2025 | 2682406.3523 | 1249020.5708
7 | 2682380.3435 | 1249024.1017 | 2682376.6149 | 1249020.7082
8 | 2682435.806 | 1248989.37 | 2682406.3523 | 1249020.5708
9 | 2682310.9073 | 1249047.9849 | 2682326.3066 | 1249062.1112
10 | 2682302.8132 | 1249037.8916 | 2682301.8643 | 1249034.4426
11 | 2682302.8132 | 1249037.8916 | 2682303.7981 | 1249041.4635 | 2682310.9073 | 1249047.9849
12 | 2682301.8643 | 1249034.4426 | 2682319.6171 | 1249015.778
13 | 2682339.2851 | 1248995.0997 | 2682319.6171 | 1249015.778
14 | 2682339.2851 | 1248995.0997 | 2682348.2368 | 1248994.8795 | 2682354.4933 | 1249000.5739
15 | 2682362.2399 | 1249007.6245 | 2682354.4933 | 1249000.5739
16 | 2682409.0703 | 1249084.6986 | 2682536.1229 | 1249138.0413
17 | 2682465.0888 | 1249016.653 | 2682463.9259 | 1249015.5693 | 2682435.806 | 1248989.37
18 | 2682465.0888 | 1249016.653 | 2682482.1162 | 1249001.8838
19 | 2682435.806 | 1248989.37 | 2682419.9534 | 1248974.5984
20 | 2682362.2399 | 1249007.6245 | 2682376.6149 | 1249020.7082

## bus_geodata
| x | y | coords
0 | 2682369.8446 | 1249066.8352
1 | 2682351.6386 | 1249085.3491
2 | 2682340.7563 | 1249075.3664
3 | 2682363.144 | 1249127.3955
4 | 2682392.5399 | 1249035.2025
5 | 2682380.3435 | 1249024.1017
6 | 2682406.3523 | 1249020.5708
7 | 2682326.3066 | 1249062.1112
8 | 2682302.8132 | 1249037.8916
9 | 2682301.8643 | 1249034.4426
10 | 2682310.9073 | 1249047.9849
11 | 2682339.2851 | 1248995.0997
12 | 2682319.6171 | 1249015.778
13 | 2682354.4933 | 1249000.5739
14 | 2682409.0703 | 1249084.6986
15 | 2682465.0888 | 1249016.653
16 | 2682435.806 | 1248989.37
17 | 2682482.1162 | 1249001.8838
18 | 2682376.6149 | 1249020.7082
19 | 2682362.2399 | 1249007.6245
20 | 2682419.9534 | 1248974.5984
21 | 2682536.1229 | 1249138.0413
22 | 2682435.806 | 1248989.37

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98189 | -0.3477 | 0.032213 | 0.0080733
1 | 0.98266 | -0.33259 | 0 | 0
2 | 0.984 | -0.30658 | 0.017364 | 0.0043518
3 | 0.97926 | -0.39879 | 0 | 0
4 | 1 | 0 | -0.37061 | -0.093769
5 | 0.99807 | -0.036624 | 0.020173 | 0.0050559
6 | 0.99796 | -0.039112 | 0.0717 | 0.01797
7 | 0.98609 | -0.26605 | 0.014531 | 0.0036419
8 | 0.98952 | -0.19983 | 0 | 0
9 | 0.98977 | -0.19506 | 0 | 0
10 | 0.9886 | -0.21762 | 0.020006 | 0.005014
11 | 0.9936 | -0.12179 | 0 | 0
12 | 0.99156 | -0.16084 | 0.0050847 | 0.0012743
13 | 0.99484 | -0.098037 | 0.020344 | 0.0050986
14 | 0.97544 | -0.47373 | 0.057984 | 0.014532
15 | 0.99605 | -0.075936 | 0 | 0
16 | 0.99642 | -0.068891 | 0 | 0
17 | 0.99585 | -0.079912 | 0.010038 | 0.0025158
18 | 0.99753 | -0.046957 | 0.029242 | 0.0073288
19 | 0.99569 | -0.081906 | 0.029867 | 0.0074855
20 | 0.99583 | -0.08014 | 0.029554 | 0.0074071
21 | 0.97448 | -0.4927 | 0.0075044 | 0.0018808
22 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.032213 | -0.0080733 | 0.032236 | 0.0080878 | 2.3205e-05 | 1.4522e-05 | 0.048817 | 0.048817 | 0.048817 | 0.98189 | -0.3477 | 0.98266 | -0.33259 | 13.4113
1 | -0.098175 | -0.024786 | 0.098298 | 0.024864 | 0.0001225 | 7.8212e-05 | 0.14873 | 0.14873 | 0.14873 | 0.98266 | -0.33259 | 0.984 | -0.30658 | 40.8596
2 | 0.065939 | 0.016698 | -0.06573 | -0.016565 | 0.00020892 | 0.000133 | 0.099912 | 0.099912 | 0.099912 | 0.98266 | -0.33259 | 0.97926 | -0.39879 | 27.4484
3 | -0.11566 | -0.029216 | 0.11589 | 0.02936 | 0.00022516 | 0.00014385 | 0.17499 | 0.17499 | 0.17499 | 0.984 | -0.30658 | 0.98609 | -0.26605 | 48.0733
4 | 0.06573 | 0.016565 | -0.065496 | -0.016416 | 0.00023474 | 0.00014945 | 0.099912 | 0.099913 | 0.099913 | 0.97926 | -0.39879 | 0.97544 | -0.47373 | 27.4485
5 | 0.25739 | 0.065696 | -0.25693 | -0.065405 | 0.00045458 | 0.0002905 | 0.38342 | 0.38342 | 0.38342 | 1 | 0 | 0.99807 | -0.036624 | 52.667
6 | 0.11158 | 0.028073 | -0.11137 | -0.027941 | 0.0002081 | 0.00013292 | 0.16607 | 0.16607 | 0.16607 | 1 | 0 | 0.99796 | -0.039112 | 45.6233
7 | 0.23676 | 0.060349 | -0.23664 | -0.060274 | 0.00011802 | 7.5402e-05 | 0.35334 | 0.35334 | 0.35334 | 0.99807 | -0.036624 | 0.99753 | -0.046957 | 48.5357
8 | 0.03967 | 0.0099708 | -0.039614 | -0.0099353 | 5.6315e-05 | 3.5482e-05 | 0.05916 | 0.059161 | 0.059161 | 0.99796 | -0.039112 | 0.99642 | -0.068891 | 16.2529
9 | -0.13042 | -0.033002 | 0.13072 | 0.033196 | 0.00030386 | 0.0001942 | 0.19691 | 0.19691 | 0.19691 | 0.98609 | -0.26605 | 0.9886 | -0.21762 | 54.0974
10 | -0.15086 | -0.038292 | 0.15089 | 0.038314 | 3.4568e-05 | 2.2032e-05 | 0.22703 | 0.22703 | 0.22703 | 0.98952 | -0.19983 | 0.98977 | -0.19506 | 31.1851
11 | 0.15086 | 0.038292 | -0.15073 | -0.03821 | 0.00012904 | 8.2241e-05 | 0.22703 | 0.22703 | 0.22703 | 0.98952 | -0.19983 | 0.9886 | -0.21762 | 31.1851
12 | -0.15089 | -0.038314 | 0.15114 | 0.038473 | 0.00024893 | 0.00015865 | 0.22703 | 0.22703 | 0.22703 | 0.98977 | -0.19506 | 0.99156 | -0.16084 | 31.185
13 | 0.15652 | 0.039935 | -0.15623 | -0.039747 | 0.00029464 | 0.00018783 | 0.23466 | 0.23466 | 0.23466 | 0.9936 | -0.12179 | 0.99156 | -0.16084 | 32.2332
14 | -0.15652 | -0.039935 | 0.1567 | 0.04005 | 0.00017979 | 0.00011462 | 0.23466 | 0.23466 | 0.23466 | 0.9936 | -0.12179 | 0.99484 | -0.098037 | 32.2331
15 | -0.17704 | -0.045148 | 0.17718 | 0.045236 | 0.00013801 | 8.8055e-05 | 0.26509 | 0.26509 | 0.26509 | 0.99484 | -0.098037 | 0.99569 | -0.081906 | 36.4128
16 | 0.0075112 | 0.0018834 | -0.0075044 | -0.0018808 | 6.7849e-06 | 2.624e-06 | 0.011458 | 0.011459 | 0.011459 | 0.97544 | -0.47373 | 0.97448 | -0.4927 | 3.1481
17 | -0.01004 | -0.0025168 | 0.010044 | 0.0025184 | 3.3713e-06 | 1.6373e-06 | 0.014999 | 0.014999 | 0.014999 | 0.99605 | -0.075936 | 0.99642 | -0.068891 | 4.1207
18 | 0.01004 | 0.0025168 | -0.010038 | -0.0025158 | 1.9017e-06 | 9.2376e-07 | 0.014999 | 0.014999 | 0.014999 | 0.99605 | -0.075936 | 0.99585 | -0.079912 | 4.1207
19 | 0.02957 | 0.0074169 | -0.029554 | -0.0074071 | 1.5847e-05 | 9.8598e-06 | 0.044161 | 0.044162 | 0.044162 | 0.99642 | -0.068891 | 0.99583 | -0.08014 | 12.1323
20 | 0.2074 | 0.052945 | -0.20705 | -0.052722 | 0.00034961 | 0.00022324 | 0.30972 | 0.30972 | 0.30972 | 0.99753 | -0.046957 | 0.99569 | -0.081906 | 42.544

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.37061 | 0.093769

## res_load
| p_mw | q_mvar
0 | 0.032213 | 0.0080733
1 | 0.017364 | 0.0043518
2 | 0.020173 | 0.0050559
3 | 0.0717 | 0.01797
4 | 0.014531 | 0.0036419
5 | 0.020006 | 0.005014
6 | 0.0050847 | 0.0012743
7 | 0.020344 | 0.0050986
8 | 0.057984 | 0.014532
9 | 0.010038 | 0.0025158
10 | 0.029242 | 0.0073288
11 | 0.029867 | 0.0074855
12 | 0.029554 | 0.0074071
13 | 0.0075044 | 0.0018808

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1