## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-389_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-389_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-389_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-389_0_5_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_261-389_0_5_node_19 | 0.4 | n |  | TRUE
5 | bus_LV_261-389_0_5_node_20 | 0.4 | n |  | TRUE
6 | bus_LV_261-389_0_5_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_261-389_0_5_node_24 | 0.4 | n |  | TRUE
8 | bus_LV_261-389_0_5_node_53 | 0.4 | n |  | TRUE
9 | bus_LV_261-389_0_5_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_261-389_0_5_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_261-389_0_5_node_43 | 0.4 | n |  | TRUE
12 | bus_LV_261-389_0_5_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_261-389_0_5_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_261-389_0_5_node_36 | 0.4 | n |  | TRUE
15 | bus_LV_261-389_0_5_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_261-389_0_5_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_261-389_0_5_node_26 | 0.4 | n |  | TRUE
18 | bus_LV_261-389_0_5_node_50 | 0.4 | n |  | TRUE
19 | bus_LV_261-389_0_5_node_54 | 0.4 | n |  | TRUE
20 | bus_LV_261-389_0_5_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_261-389_0_5_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_261-389_0_5_node_39 | 0.4 | n |  | TRUE
23 | bus_LV_261-389_0_5_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_261-389_0_5_node_40 | 0.4 | n |  | TRUE
25 | bus_LV_261-389_0_5_node_32 | 0.4 | n |  | TRUE
26 | bus_LV_261-389_0_5_node_38 | 0.4 | n |  | TRUE
27 | bus_LV_261-389_0_5_node_31 | 0.4 | n |  | TRUE
28 | bus_LV_261-389_0_5_node_42 | 0.4 | n |  | TRUE
29 | bus_LV_261-389_0_5_node_48 | 0.4 | n |  | TRUE
30 | bus_LV_261-389_0_5_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_261-389_0_5_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_261-389_0_5_node_51 | 0.4 | n |  | TRUE
33 | bus_LV_261-389_0_5_node_41 | 0.4 | n |  | TRUE
34 | bus_LV_261-389_0_5_node_30 | 0.4 | n |  | TRUE
35 | bus_LV_261-389_0_5_node_37 | 0.4 | n |  | TRUE
36 | bus_LV_261-389_0_5_node_33 | 0.4 | n |  | TRUE
37 | bus_LV_261-389_0_5_node_34 | 0.4 | n |  | TRUE
38 | bus_LV_261-389_0_5_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_261-389_0_5_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_261-389_0_5_node_46 | 0.4 | n |  | TRUE
41 | bus_LV_261-389_0_5_node_52 | 0.4 | n |  | TRUE
42 | bus_LV_261-389_0_5_node_35 | 0.4 | n |  | TRUE
43 | bus_LV_261-389_0_5_node_44 | 0.4 | n |  | TRUE
44 | bus_LV_261-389_0_5_node_45 | 0.4 | n |  | TRUE
45 | bus_LV_261-389_0_5_node_47 | 0.4 | n |  | TRUE
46 | bus_LV_261-389_0_5_node_49 | 0.4 | n |  | TRUE
47 | bus_MV_530_1_node_148 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-389_0_5_load_0 | 0 | 0.012108 | 0.0030346 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-389_0_5_load_1 | 1 | 0.055966 | 0.014026 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-389_0_5_load_3 | 6 | 0.04819 | 0.012077 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-389_0_5_load_53 | 8 | 0.0079746 | 0.0019986 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-389_0_5_load_43 | 11 | 0.020066 | 0.0050289 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-389_0_5_load_36 | 14 | 0.012613 | 0.003161 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-389_0_5_load_26 | 17 | 0.0061711 | 0.0015466 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-389_0_5_load_50 | 18 | 0.013245 | 0.0033195 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-389_0_5_load_54 | 19 | 0.0068019 | 0.0017047 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-389_0_5_load_39 | 22 | 0.011121 | 0.0027872 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-389_0_5_load_40 | 24 | 0.011921 | 0.0029878 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-389_0_5_load_32 | 25 | 0.010062 | 0.0025218 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-389_0_5_load_38 | 26 | 0.0061084 | 0.0015309 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-389_0_5_load_31 | 27 | 0.0076996 | 0.0019297 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-389_0_5_load_42 | 28 | 0.0073564 | 0.0018437 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-389_0_5_load_48 | 29 | 0.0071952 | 0.0018033 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-389_0_5_load_25 | 30 | 0.016606 | 0.0041619 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-389_0_5_load_27 | 31 | 0.013504 | 0.0033844 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-389_0_5_load_51 | 32 | 0.02092 | 0.005243 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-389_0_5_load_41 | 33 | 0.012053 | 0.0030209 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-389_0_5_load_30 | 34 | 0.0078304 | 0.0019625 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-389_0_5_load_37 | 35 | 0.010847 | 0.0027185 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-389_0_5_load_33 | 36 | 0.013439 | 0.0033681 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-389_0_5_load_34 | 37 | 0.0076232 | 0.0019106 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-389_0_5_load_29 | 38 | 0.0050902 | 0.0012757 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-389_0_5_load_28 | 39 | 0.013845 | 0.0034698 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-389_0_5_load_46 | 40 | 0.0063536 | 0.0015924 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-389_0_5_load_52 | 41 | 0.062213 | 0.015592 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-389_0_5_load_35 | 42 | 0.0049853 | 0.0012494 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-389_0_5_load_44 | 43 | 0.013915 | 0.0034874 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-389_0_5_load_45 | 44 | 0.014346 | 0.0035954 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-389_0_5_load_47 | 45 | 0.014759 | 0.003699 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-389_0_5_load_49 | 46 | 0.0070856 | 0.0017758 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 9 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-389_0_5_line_0 |  | 0 | 1 | 0.024815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-389_0_5_line_1 |  | 0 | 2 | 0.0073241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-389_0_5_line_2 |  | 2 | 3 | 0.018002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-389_0_5_line_3 |  | 2 | 4 | 0.075578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-389_0_5_line_4 |  | 2 | 5 | 0.012029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_261-389_0_5_line_5 |  | 3 | 8 | 0.010136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-389_0_5_line_6 |  | 4 | 28 | 0.017119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-389_0_5_line_7 |  | 5 | 29 | 0.0065337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-389_0_5_line_8 |  | 5 | 9 | 0.002316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_261-389_0_5_line_9 |  | 6 | 7 | 0.04338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-389_0_5_line_10 |  | 7 | 30 | 0.0212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-389_0_5_line_11 |  | 8 | 30 | 0.017875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-389_0_5_line_12 |  | 9 | 10 | 0.010761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_261-389_0_5_line_13 |  | 9 | 11 | 0.019897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-389_0_5_line_14 |  | 10 | 15 | 0.004138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-389_0_5_line_15 |  | 10 | 16 | 0.039859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-389_0_5_line_16 |  | 10 | 17 | 0.014418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-389_0_5_line_17 |  | 12 | 13 | 0.00216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-389_0_5_line_18 |  | 12 | 14 | 0.014176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-389_0_5_line_19 |  | 13 | 15 | 0.011844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-389_0_5_line_20 |  | 13 | 19 | 0.01788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-389_0_5_line_21 |  | 15 | 27 | 0.0064877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-389_0_5_line_22 |  | 16 | 18 | 0.012715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-389_0_5_line_23 |  | 17 | 31 | 0.015368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-389_0_5_line_24 |  | 18 | 32 | 0.014753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-389_0_5_line_25 |  | 20 | 21 | 0.085508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-389_0_5_line_26 |  | 20 | 22 | 0.03282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-389_0_5_line_27 |  | 21 | 23 | 0.0092299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-389_0_5_line_28 |  | 21 | 24 | 0.032018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-389_0_5_line_29 |  | 23 | 25 | 0.011754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-389_0_5_line_30 |  | 23 | 26 | 0.017249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-389_0_5_line_31 |  | 24 | 33 | 0.016461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-389_0_5_line_32 |  | 25 | 34 | 0.0142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-389_0_5_line_33 |  | 26 | 35 | 0.019931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-389_0_5_line_34 |  | 27 | 38 | 0.01331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-389_0_5_line_35 |  | 29 | 40 | 0.012259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-389_0_5_line_36 |  | 31 | 39 | 0.014363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-389_0_5_line_37 |  | 32 | 41 | 0.015735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-389_0_5_line_38 |  | 34 | 38 | 0.0030197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-389_0_5_line_39 |  | 35 | 42 | 0.0039386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-389_0_5_line_40 |  | 36 | 37 | 0.0051694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-389_0_5_line_41 |  | 37 | 42 | 0.0093062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-389_0_5_line_42 |  | 40 | 43 | 0.0091824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-389_0_5_line_43 |  | 43 | 44 | 0.0084053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-389_0_5_line_44 |  | 44 | 45 | 0.0085195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-389_0_5_line_45 |  | 45 | 46 | 0.013007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-389_0_5_trafo_6 | 0.63 MVA 20/0.4 kV | 47 | 9 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2682224.5192 | 1248773.9714 | 2682203.7337 | 1248787.5272
1 | 2682230.654 | 1248769.9705 | 2682224.5192 | 1248773.9714
2 | 2682228.3795 | 1248753.2043 | 2682232.4793 | 1248762.5125 | 2682232.5192 | 1248764.5368 | 2682232.0755 | 1248767.1214 | 2682230.654 | 1248769.9705
3 | 2682174.1132 | 1248811.9064 | 2682183.6691 | 1248806.2569 | 2682233.4727 | 1248774.7353 | 2682230.654 | 1248769.9705
4 | 2682236.786 | 1248780.3187 | 2682233.4727 | 1248774.7353 | 2682230.654 | 1248769.9705
5 | 2682228.3795 | 1248753.2043 | 2682224.0291 | 1248744.0496
6 | 2682174.1132 | 1248811.9064 | 2682172.673 | 1248828.9647
7 | 2682236.786 | 1248780.3187 | 2682231.1887 | 1248783.6892
8 | 2682239.052 | 1248780.8283 | 2682236.786 | 1248780.3187
9 | 2682203.015 | 1248714.9355 | 2682200.9291 | 1248716.6857 | 2682197.4808 | 1248723.5541 | 2682190.0283 | 1248750.6819 | 2682188.9473 | 1248755.3987
10 | 2682203.015 | 1248714.9355 | 2682205.3079 | 1248714.6004 | 2682207.5424 | 1248714.6648 | 2682209.8824 | 1248715.2866 | 2682211.0553 | 1248716.7483 | 2682216.3568 | 1248727.9045
11 | 2682216.3568 | 1248727.9045 | 2682224.0291 | 1248744.0496
12 | 2682239.052 | 1248780.8283 | 2682244.2678 | 1248778.2877 | 2682248.7308 | 1248776.1257
13 | 2682239.052 | 1248780.8283 | 2682241.0274 | 1248782.1456 | 2682242.9049 | 1248784.5289 | 2682249.0013 | 1248797.6724
14 | 2682248.69 | 1248771.9888 | 2682248.7308 | 1248776.1257
15 | 2682248.7308 | 1248776.1257 | 2682244.2678 | 1248778.2877 | 2682244.735 | 1248779.4505 | 2682258.9014 | 1248809.9696
16 | 2682248.7308 | 1248776.1257 | 2682249.8682 | 1248778.5099 | 2682254.8913 | 1248789.1615
17 | 2682243.0575 | 1248761.5696 | 2682241.1768 | 1248760.4983
18 | 2682241.1768 | 1248760.4983 | 2682235.1202 | 1248747.681
19 | 2682243.0575 | 1248761.5696 | 2682245.3253 | 1248765.7597 | 2682248.69 | 1248771.9888
20 | 2682243.0575 | 1248761.5696 | 2682257.5442 | 1248751.0901
21 | 2682248.69 | 1248771.9888 | 2682253.9061 | 1248768.131
22 | 2682258.9014 | 1248809.9696 | 2682251.6501 | 1248813.8941 | 2682247.5655 | 1248815.7088
23 | 2682254.8913 | 1248789.1615 | 2682261.446 | 1248803.061
24 | 2682247.5655 | 1248815.7088 | 2682241.2627 | 1248818.509 | 2682234.0308 | 1248821.5776 | 2682234.0308 | 1248821.5776
25 | 2682296.8827 | 1248740.69 | 2682296.737 | 1248737.0408 | 2682326.0532 | 1248715.3206 | 2682329.0869 | 1248714.9291 | 2682353.1317 | 1248749.7443
26 | 2682353.1317 | 1248749.7443 | 2682350.6404 | 1248751.3108 | 2682341.6299 | 1248757.3679 | 2682335.5779 | 1248761.3869 | 2682342.1832 | 1248771.1104
27 | 2682288.602 | 1248744.7669 | 2682292.5788 | 1248742.8096 | 2682296.8827 | 1248740.69
28 | 2682296.8827 | 1248740.69 | 2682310.3718 | 1248769.7278
29 | 2682288.602 | 1248744.7669 | 2682284.9336 | 1248745.183 | 2682278.4517 | 1248749.977
30 | 2682288.602 | 1248744.7669 | 2682295.9759 | 1248760.3608
31 | 2682310.3718 | 1248769.7278 | 2682317.3068 | 1248784.6567
32 | 2682278.4517 | 1248749.977 | 2682267.0349 | 1248758.4209
33 | 2682304.4961 | 1248778.3788 | 2682295.9759 | 1248760.3608
34 | 2682264.607 | 1248760.2165 | 2682253.9061 | 1248768.131
35 | 2682220.687 | 1248790.0129 | 2682231.1887 | 1248783.6892
36 | 2682267.5722 | 1248816.0517 | 2682261.446 | 1248803.061
37 | 2682240.503 | 1248835.9203 | 2682234.0308 | 1248821.5776
38 | 2682264.607 | 1248760.2165 | 2682267.0349 | 1248758.4209
39 | 2682304.4961 | 1248778.3788 | 2682306.1797 | 1248781.9393
40 | 2682310.158 | 1248790.3524 | 2682312.3678 | 1248795.0256
41 | 2682310.158 | 1248790.3524 | 2682306.1797 | 1248781.9393
42 | 2682212.8206 | 1248794.7498 | 2682220.687 | 1248790.0129
43 | 2682212.8206 | 1248794.7498 | 2682205.62 | 1248799.0857
44 | 2682198.3216 | 1248803.4805 | 2682205.62 | 1248799.0857
45 | 2682198.3216 | 1248803.4805 | 2682187.1788 | 1248810.1903

## bus_geodata
| x | y | coords
0 | 2682224.5192 | 1248773.9714
1 | 2682203.7337 | 1248787.5272
2 | 2682230.654 | 1248769.9705
3 | 2682228.3795 | 1248753.2043
4 | 2682174.1132 | 1248811.9064
5 | 2682236.786 | 1248780.3187
6 | 2682188.9473 | 1248755.3987
7 | 2682203.015 | 1248714.9355
8 | 2682224.0291 | 1248744.0496
9 | 2682239.052 | 1248780.8283
10 | 2682248.7308 | 1248776.1257
11 | 2682249.0013 | 1248797.6724
12 | 2682241.1768 | 1248760.4983
13 | 2682243.0575 | 1248761.5696
14 | 2682235.1202 | 1248747.681
15 | 2682248.69 | 1248771.9888
16 | 2682258.9014 | 1248809.9696
17 | 2682254.8913 | 1248789.1615
18 | 2682247.5655 | 1248815.7088
19 | 2682257.5442 | 1248751.0901
20 | 2682353.1317 | 1248749.7443
21 | 2682296.8827 | 1248740.69
22 | 2682342.1832 | 1248771.1104
23 | 2682288.602 | 1248744.7669
24 | 2682310.3718 | 1248769.7278
25 | 2682278.4517 | 1248749.977
26 | 2682295.9759 | 1248760.3608
27 | 2682253.9061 | 1248768.131
28 | 2682172.673 | 1248828.9647
29 | 2682231.1887 | 1248783.6892
30 | 2682216.3568 | 1248727.9045
31 | 2682261.446 | 1248803.061
32 | 2682234.0308 | 1248821.5776
33 | 2682317.3068 | 1248784.6567
34 | 2682267.0349 | 1248758.4209
35 | 2682304.4961 | 1248778.3788
36 | 2682312.3678 | 1248795.0256
37 | 2682310.158 | 1248790.3524
38 | 2682264.607 | 1248760.2165
39 | 2682267.5722 | 1248816.0517
40 | 2682220.687 | 1248790.0129
41 | 2682240.503 | 1248835.9203
42 | 2682306.1797 | 1248781.9393
43 | 2682212.8206 | 1248794.7498
44 | 2682205.62 | 1248799.0857
45 | 2682198.3216 | 1248803.4805
46 | 2682187.1788 | 1248810.1903
47 | 2682236.786 | 1248780.3187

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99851 | -0.028545 | 0.012108 | 0.0030346
1 | 0.99725 | -0.052854 | 0.055966 | 0.014026
2 | 0.99897 | -0.019833 | 0 | 0
3 | 0.99777 | -0.042742 | 0 | 0
4 | 0.99846 | -0.029551 | 0 | 0
5 | 0.99978 | -0.0042771 | 0 | 0
6 | 0.9932 | -0.13082 | 0.04819 | 0.012077
7 | 0.99511 | -0.093957 | 0 | 0
8 | 0.9971 | -0.055664 | 0.0079746 | 0.0019986
9 | 1 | 0 | -0.49371 | -0.12411
10 | 0.99873 | -0.024235 | 0 | 0
11 | 0.99964 | -0.0069612 | 0.020066 | 0.0050289
12 | 0.99802 | -0.03801 | 0 | 0
13 | 0.99804 | -0.037533 | 0 | 0
14 | 0.99785 | -0.041139 | 0.012613 | 0.003161
15 | 0.99825 | -0.03351 | 0 | 0
16 | 0.99522 | -0.091599 | 0 | 0
17 | 0.99829 | -0.032684 | 0.0061711 | 0.0015466
18 | 0.9941 | -0.11319 | 0.013245 | 0.0033195
19 | 0.99793 | -0.039661 | 0.0068019 | 0.0017047
20 | 0.99297 | -0.13526 | 0 | 0
21 | 0.99383 | -0.11846 | 0 | 0
22 | 0.99263 | -0.14171 | 0.011121 | 0.0027872
23 | 0.99413 | -0.11274 | 0 | 0
24 | 0.99313 | -0.13201 | 0.011921 | 0.0029878
25 | 0.99497 | -0.096564 | 0.010062 | 0.0025218
26 | 0.99345 | -0.12583 | 0.0061084 | 0.0015309
27 | 0.99761 | -0.045863 | 0.0076996 | 0.0019297
28 | 0.99835 | -0.031753 | 0.0073564 | 0.0018437
29 | 0.9994 | -0.011532 | 0.0071952 | 0.0018033
30 | 0.99604 | -0.075992 | 0.016606 | 0.0041619
31 | 0.99791 | -0.040038 | 0.013504 | 0.0033844
32 | 0.99298 | -0.13484 | 0.02092 | 0.005243
33 | 0.99295 | -0.13552 | 0.012053 | 0.0030209
34 | 0.99611 | -0.074546 | 0.0078304 | 0.0019625
35 | 0.99278 | -0.13883 | 0.010847 | 0.0027185
36 | 0.99245 | -0.14534 | 0.013439 | 0.0033681
37 | 0.99251 | -0.14411 | 0.0076232 | 0.0019106
38 | 0.99638 | -0.069455 | 0.0050902 | 0.0012757
39 | 0.99773 | -0.043519 | 0.013845 | 0.0034698
40 | 0.99877 | -0.023618 | 0.0063536 | 0.0015924
41 | 0.99209 | -0.15216 | 0.062213 | 0.015592
42 | 0.99269 | -0.14064 | 0.0049853 | 0.0012494
43 | 0.99835 | -0.03166 | 0.013915 | 0.0034874
44 | 0.99808 | -0.036981 | 0.014346 | 0.0035954
45 | 0.99791 | -0.040238 | 0.014759 | 0.003699
46 | 0.99782 | -0.041851 | 0.0070856 | 0.0017758
47 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.056031 | 0.014068 | -0.055966 | -0.014026 | 6.4894e-05 | 4.1208e-05 | 0.083508 | 0.083508 | 0.083508 | 0.99851 | -0.028545 | 0.99725 | -0.052854 | 22.9418
1 | -0.068139 | -0.017102 | 0.068167 | 0.01712 | 2.8325e-05 | 1.8032e-05 | 0.10155 | 0.10155 | 0.10155 | 0.99851 | -0.028545 | 0.99897 | -0.019833 | 27.8988
2 | 0.073085 | 0.018438 | -0.073005 | -0.018387 | 8.007e-05 | 5.1009e-05 | 0.10891 | 0.10891 | 0.10891 | 0.99897 | -0.019833 | 0.99777 | -0.042742 | 29.9195
3 | 0.0073606 | 0.0018452 | -0.0073572 | -0.001844 | 3.4071e-06 | 1.1916e-06 | 0.010964 | 0.010965 | 0.010965 | 0.99897 | -0.019833 | 0.99846 | -0.029551 | 3.0122
4 | -0.14861 | -0.037403 | 0.14872 | 0.037474 | 0.00011058 | 7.0453e-05 | 0.22142 | 0.22142 | 0.22142 | 0.99897 | -0.019833 | 0.99978 | -0.0042771 | 30.4152
5 | 0.073005 | 0.018387 | -0.07296 | -0.018358 | 4.5082e-05 | 2.872e-05 | 0.10891 | 0.10891 | 0.10891 | 0.99777 | -0.042742 | 0.9971 | -0.055664 | 29.9195
6 | 0.0073572 | 0.001844 | -0.0073564 | -0.0018437 | 7.7177e-07 | 2.7006e-07 | 0.010965 | 0.010965 | 0.010965 | 0.99846 | -0.029551 | 0.99835 | -0.031753 | 3.0123
7 | 0.063741 | 0.016008 | -0.063719 | -0.015994 | 2.2057e-05 | 1.4031e-05 | 0.094881 | 0.094881 | 0.094881 | 0.99978 | -0.0042771 | 0.9994 | -0.011532 | 26.0661
8 | -0.21246 | -0.053482 | 0.21251 | 0.05351 | 4.3446e-05 | 2.7745e-05 | 0.3163 | 0.3163 | 0.3163 | 0.99978 | -0.0042771 | 1 | 0 | 43.4482
9 | -0.04819 | -0.012077 | 0.048274 | 0.012131 | 8.4795e-05 | 5.3706e-05 | 0.072198 | 0.072198 | 0.072198 | 0.9932 | -0.13082 | 0.99511 | -0.093957 | 19.8346
10 | -0.048274 | -0.012131 | 0.048316 | 0.012157 | 4.1439e-05 | 2.6245e-05 | 0.072198 | 0.072198 | 0.072198 | 0.99511 | -0.093957 | 0.99604 | -0.075992 | 19.8345
11 | 0.064985 | 0.016359 | -0.064922 | -0.016319 | 6.3079e-05 | 4.0137e-05 | 0.097006 | 0.097006 | 0.097006 | 0.9971 | -0.055664 | 0.99604 | -0.075992 | 26.65
12 | 0.25948 | 0.065568 | -0.25918 | -0.065376 | 0.00030109 | 0.00019242 | 0.3863 | 0.3863 | 0.3863 | 1 | 0 | 0.99873 | -0.024235 | 53.0639
13 | 0.020072 | 0.0050329 | -0.020066 | -0.0050289 | 6.6565e-06 | 3.9992e-06 | 0.029869 | 0.029869 | 0.029869 | 1 | 0 | 0.99964 | -0.0069612 | 8.2057
14 | 0.12871 | 0.032454 | -0.12865 | -0.032418 | 5.7106e-05 | 3.6494e-05 | 0.19184 | 0.19184 | 0.19184 | 0.99873 | -0.024235 | 0.99825 | -0.03351 | 52.7021
15 | 0.096927 | 0.024505 | -0.096615 | -0.024306 | 0.00031204 | 0.00019919 | 0.14449 | 0.14449 | 0.14449 | 0.99873 | -0.024235 | 0.99522 | -0.091599 | 39.6942
16 | 0.033545 | 0.0084166 | -0.033532 | -0.0084081 | 1.3508e-05 | 8.4563e-06 | 0.049983 | 0.049983 | 0.049983 | 0.99873 | -0.024235 | 0.99829 | -0.032684 | 13.7315
17 | -0.012615 | -0.0031621 | 0.012615 | 0.0031622 | 2.8654e-07 | 1.5516e-07 | 0.018808 | 0.018808 | 0.018808 | 0.99802 | -0.03801 | 0.99804 | -0.037533 | 5.1671
18 | 0.012615 | 0.0031621 | -0.012613 | -0.003161 | 1.8806e-06 | 1.0183e-06 | 0.018808 | 0.018808 | 0.018808 | 0.99802 | -0.03801 | 0.99785 | -0.041139 | 5.1671
19 | -0.019417 | -0.0048671 | 0.019421 | 0.0048694 | 3.7226e-06 | 2.2276e-06 | 0.02895 | 0.02895 | 0.02895 | 0.99804 | -0.037533 | 0.99825 | -0.03351 | 7.9534
20 | 0.0068026 | 0.0017049 | -0.0068019 | -0.0017047 | 6.8971e-07 | 2.0779e-07 | 0.010142 | 0.010142 | 0.010142 | 0.99804 | -0.037533 | 0.99793 | -0.039661 | 2.7864
21 | 0.10923 | 0.027548 | -0.10917 | -0.027507 | 6.4548e-05 | 4.1226e-05 | 0.16289 | 0.16289 | 0.16289 | 0.99825 | -0.03351 | 0.99761 | -0.045863 | 44.7487
22 | 0.096615 | 0.024306 | -0.096515 | -0.024242 | 9.954e-05 | 6.3541e-05 | 0.14449 | 0.14449 | 0.14449 | 0.99522 | -0.091599 | 0.9941 | -0.11319 | 39.6942
23 | 0.027361 | 0.0068615 | -0.027351 | -0.0068556 | 9.5857e-06 | 5.934e-06 | 0.040784 | 0.040784 | 0.040784 | 0.99829 | -0.032684 | 0.99791 | -0.040038 | 11.2045
24 | 0.08327 | 0.020923 | -0.083184 | -0.020868 | 8.5974e-05 | 5.4832e-05 | 0.12466 | 0.12466 | 0.12466 | 0.9941 | -0.11319 | 0.99298 | -0.13484 | 34.2476
25 | -0.011124 | -0.0027889 | 0.011133 | 0.0027935 | 8.9113e-06 | 4.5962e-06 | 0.016671 | 0.01667 | 0.016671 | 0.99297 | -0.13526 | 0.99383 | -0.11846 | 4.5799
26 | 0.011124 | 0.0027889 | -0.011121 | -0.0027872 | 3.4205e-06 | 1.7647e-06 | 0.016671 | 0.016671 | 0.016671 | 0.99297 | -0.13526 | 0.99263 | -0.14171 | 4.5799
27 | -0.035126 | -0.0088128 | 0.035135 | 0.0088188 | 9.5745e-06 | 6.0081e-06 | 0.052595 | 0.052595 | 0.052595 | 0.99383 | -0.11846 | 0.99413 | -0.11274 | 14.4492
28 | 0.023992 | 0.0060192 | -0.023977 | -0.0060097 | 1.5496e-05 | 9.5027e-06 | 0.035925 | 0.035925 | 0.035925 | 0.99383 | -0.11846 | 0.99313 | -0.13201 | 9.8694
29 | -0.078194 | -0.019632 | 0.078255 | 0.01967 | 6.0393e-05 | 3.8499e-05 | 0.11705 | 0.11705 | 0.11705 | 0.99413 | -0.11274 | 0.99497 | -0.096564 | 32.1576
30 | 0.043059 | 0.010813 | -0.043032 | -0.010796 | 2.6876e-05 | 1.6977e-05 | 0.064458 | 0.064459 | 0.064459 | 0.99413 | -0.11274 | 0.99345 | -0.12583 | 17.7084
31 | 0.012055 | 0.003022 | -0.012053 | -0.0030209 | 2.014e-06 | 1.076e-06 | 0.018063 | 0.018063 | 0.018063 | 0.99313 | -0.13201 | 0.99295 | -0.13552 | 4.9624
32 | -0.088317 | -0.022192 | 0.08841 | 0.022251 | 9.2927e-05 | 5.9289e-05 | 0.1321 | 0.1321 | 0.1321 | 0.99497 | -0.096564 | 0.99611 | -0.074546 | 36.2917
33 | 0.036924 | 0.0092649 | -0.036901 | -0.0092506 | 2.2864e-05 | 1.4375e-05 | 0.055309 | 0.055309 | 0.055309 | 0.99345 | -0.12583 | 0.99278 | -0.13883 | 15.1949
34 | 0.10147 | 0.025577 | -0.10135 | -0.025504 | 0.00011441 | 7.3048e-05 | 0.1514 | 0.1514 | 0.1514 | 0.99761 | -0.045863 | 0.99638 | -0.069455 | 41.5937
35 | 0.056524 | 0.014191 | -0.056491 | -0.01417 | 3.2566e-05 | 2.0682e-05 | 0.084168 | 0.084168 | 0.084168 | 0.9994 | -0.011532 | 0.99877 | -0.023618 | 23.123
36 | 0.013847 | 0.0034711 | -0.013845 | -0.0034698 | 2.2963e-06 | 1.282e-06 | 0.020648 | 0.020648 | 0.020648 | 0.99791 | -0.040038 | 0.99773 | -0.043519 | 5.6726
37 | 0.062264 | 0.015625 | -0.062213 | -0.015592 | 5.1379e-05 | 3.2679e-05 | 0.093312 | 0.093312 | 0.093312 | 0.99298 | -0.13484 | 0.99209 | -0.15216 | 25.6352
38 | -0.09624 | -0.024214 | 0.096264 | 0.024229 | 2.3416e-05 | 1.4947e-05 | 0.1438 | 0.1438 | 0.1438 | 0.99611 | -0.074546 | 0.99638 | -0.069455 | 39.5053
39 | 0.026054 | 0.0065321 | -0.026052 | -0.0065307 | 2.2524e-06 | 1.3906e-06 | 0.039052 | 0.039052 | 0.039052 | 0.99278 | -0.13883 | 0.99269 | -0.14064 | 10.7284
40 | -0.013439 | -0.0033681 | 0.01344 | 0.0033686 | 7.8706e-07 | 4.3692e-07 | 0.02015 | 0.02015 | 0.02015 | 0.99245 | -0.14534 | 0.99251 | -0.14411 | 5.5356
41 | -0.021063 | -0.0052791 | 0.021066 | 0.0052812 | 3.4801e-06 | 2.107e-06 | 0.031579 | 0.031579 | 0.031579 | 0.99251 | -0.14411 | 0.99269 | -0.14064 | 8.6755
42 | 0.050138 | 0.012578 | -0.050118 | -0.012566 | 1.9215e-05 | 1.2178e-05 | 0.074702 | 0.074702 | 0.074702 | 0.99877 | -0.023618 | 0.99835 | -0.03166 | 20.5225
43 | 0.036204 | 0.0090782 | -0.036194 | -0.0090724 | 9.1783e-06 | 5.7642e-06 | 0.053962 | 0.053962 | 0.053962 | 0.99835 | -0.03166 | 0.99808 | -0.036981 | 14.8247
44 | 0.021849 | 0.005477 | -0.021845 | -0.005475 | 3.39e-06 | 2.0583e-06 | 0.032574 | 0.032574 | 0.032574 | 0.99808 | -0.036981 | 0.99791 | -0.040238 | 8.949
45 | 0.0070862 | 0.001776 | -0.0070856 | -0.0017758 | 5.4459e-07 | 1.7863e-07 | 0.010566 | 0.010567 | 0.010567 | 0.99791 | -0.040238 | 0.99782 | -0.041851 | 2.9029

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.49371 | 0.12411

## res_load
| p_mw | q_mvar
0 | 0.012108 | 0.0030346
1 | 0.055966 | 0.014026
2 | 0.04819 | 0.012077
3 | 0.0079746 | 0.0019986
4 | 0.020066 | 0.0050289
5 | 0.012613 | 0.003161
6 | 0.0061711 | 0.0015466
7 | 0.013245 | 0.0033195
8 | 0.0068019 | 0.0017047
9 | 0.011121 | 0.0027872
10 | 0.011921 | 0.0029878
11 | 0.010062 | 0.0025218
12 | 0.0061084 | 0.0015309
13 | 0.0076996 | 0.0019297
14 | 0.0073564 | 0.0018437
15 | 0.0071952 | 0.0018033
16 | 0.016606 | 0.0041619
17 | 0.013504 | 0.0033844
18 | 0.02092 | 0.005243
19 | 0.012053 | 0.0030209
20 | 0.0078304 | 0.0019625
21 | 0.010847 | 0.0027185
22 | 0.013439 | 0.0033681
23 | 0.0076232 | 0.0019106
24 | 0.0050902 | 0.0012757
25 | 0.013845 | 0.0034698
26 | 0.0063536 | 0.0015924
27 | 0.062213 | 0.015592
28 | 0.0049853 | 0.0012494
29 | 0.013915 | 0.0034874
30 | 0.014346 | 0.0035954
31 | 0.014759 | 0.003699
32 | 0.0070856 | 0.0017758

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1