## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-423_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-423_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-423_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-423_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_261-423_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_261-423_0_4_node_11 | 0.4 | n |  | TRUE
6 | bus_LV_261-423_0_4_node_23 | 0.4 | n |  | TRUE
7 | bus_LV_261-423_0_4_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_261-423_0_4_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_261-423_0_4_node_15 | 0.4 | n |  | TRUE
10 | bus_LV_261-423_0_4_node_12 | 0.4 | n |  | TRUE
11 | bus_LV_261-423_0_4_node_21 | 0.4 | n |  | TRUE
12 | bus_LV_261-423_0_4_node_22 | 0.4 | n |  | TRUE
13 | bus_LV_261-423_0_4_node_16 | 0.4 | n |  | TRUE
14 | bus_LV_261-423_0_4_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_261-423_0_4_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_261-423_0_4_node_20 | 0.4 | n |  | TRUE
17 | bus_LV_261-423_0_4_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_261-423_0_4_node_27 | 0.4 | n |  | TRUE
19 | bus_LV_261-423_0_4_node_26 | 0.4 | n |  | TRUE
20 | bus_LV_261-423_0_4_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_261-423_0_4_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_261-423_0_4_node_29 | 0.4 | n |  | TRUE
23 | bus_LV_261-423_0_4_node_25 | 0.4 | n |  | TRUE
24 | bus_LV_261-423_0_4_node_24 | 0.4 | n |  | TRUE
25 | bus_MV_530_1_node_36 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-423_0_4_load_0 | 0 | 0.083539 | 0.020937 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-423_0_4_load_1 | 1 | 0.0063561 | 0.001593 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-423_0_4_load_11 | 5 | 0.019882 | 0.0049829 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-423_0_4_load_23 | 6 | 0.011244 | 0.0028179 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-423_0_4_load_15 | 9 | 0.012032 | 0.0030156 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-423_0_4_load_12 | 10 | 0.011136 | 0.0027909 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-423_0_4_load_21 | 11 | 0.01086 | 0.0027218 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-423_0_4_load_22 | 12 | 0.008889 | 0.0022278 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-423_0_4_load_16 | 13 | 0.078623 | 0.019705 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-423_0_4_load_13 | 15 | 0.017503 | 0.0043866 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-423_0_4_load_20 | 16 | 0.011677 | 0.0029265 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-423_0_4_load_14 | 17 | 0.011207 | 0.0028087 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-423_0_4_load_27 | 18 | 0.0047422 | 0.0011885 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-423_0_4_load_26 | 19 | 0.011117 | 0.0027863 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-423_0_4_load_19 | 21 | 0.013835 | 0.0034674 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-423_0_4_load_29 | 22 | 0.029333 | 0.0073514 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-423_0_4_load_25 | 23 | 0.0067383 | 0.0016888 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-423_0_4_load_24 | 24 | 0.055547 | 0.013921 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-423_0_4_line_0 |  | 0 | 1 | 0.032404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-423_0_4_line_1 |  | 0 | 2 | 0.095707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-423_0_4_line_2 |  | 2 | 3 | 0.065207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-423_0_4_line_3 |  | 3 | 4 | 0.084949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_261-423_0_4_line_4 |  | 3 | 5 | 0.023026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-423_0_4_line_5 |  | 4 | 6 | 0.0081748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_261-423_0_4_line_6 |  | 6 | 12 | 0.014051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_261-423_0_4_line_7 |  | 7 | 8 | 0.016143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_261-423_0_4_line_8 |  | 7 | 9 | 0.010258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-423_0_4_line_9 |  | 7 | 10 | 0.024991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_261-423_0_4_line_10 |  | 8 | 11 | 0.00077304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_261-423_0_4_line_11 |  | 10 | 15 | 0.014679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_261-423_0_4_line_12 |  | 11 | 16 | 0.017534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_261-423_0_4_line_13 |  | 12 | 16 | 0.016333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_261-423_0_4_line_14 |  | 13 | 14 | 0.045991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-423_0_4_line_15 |  | 14 | 20 | 0.009131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-423_0_4_line_16 |  | 14 | 21 | 0.028723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-423_0_4_line_17 |  | 15 | 17 | 0.0018683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_261-423_0_4_line_18 |  | 17 | 18 | 0.0066344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_261-423_0_4_line_19 |  | 18 | 19 | 0.0098905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_261-423_0_4_line_20 |  | 19 | 24 | 0.0022922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_261-423_0_4_line_21 |  | 20 | 22 | 0.017076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-423_0_4_line_22 |  | 21 | 23 | 0.012622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-423_0_4_line_23 |  | 23 | 24 | 0.0039962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-423_0_4_trafo_26 | 0.63 MVA 20/0.4 kV | 25 | 19 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2682126.8971 | 1249102.5947 | 2682098.0342 | 1249087.8662
1 | 2682212.2987 | 1249145.7933 | 2682201.1412 | 1249140.1011 | 2682191.2961 | 1249135.072 | 2682168.2334 | 1249123.6884 | 2682126.8971 | 1249102.5947
2 | 2682212.2987 | 1249145.7933 | 2682214.3712 | 1249141.7413 | 2682196.8478 | 1249132.7917 | 2682204.0568 | 1249124.2632 | 2682201.6957 | 1249121.9065 | 2682196.8696 | 1249126.3206 | 2682181.7749 | 1249139.3432
3 | 2682121.0428 | 1249164.6871 | 2682120.282 | 1249167.2784 | 2682123.0204 | 1249170.1963 | 2682125.5059 | 1249172.8438 | 2682127.6935 | 1249175.1869 | 2682130.1344 | 1249177.7782 | 2682131.3371 | 1249180.3523 | 2682132.6904 | 1249179.148 | 2682149.1734 | 1249165.6441 | 2682167.446 | 1249151.0643 | 2682178.8494 | 1249141.7488 | 2682181.7749 | 1249139.3432
4 | 2682181.7749 | 1249139.3432 | 2682184.9057 | 1249141.1991 | 2682196.5899 | 1249148.1106 | 2682201.7144 | 1249150.8516
5 | 2682121.0428 | 1249164.6871 | 2682119.3681 | 1249166.1983 | 2682114.7331 | 1249169.8795
6 | 2682114.7331 | 1249169.8795 | 2682106.6399 | 1249176.3073 | 2682103.7364 | 1249178.6262
7 | 2682076.6694 | 1249200.2433 | 2682064.3293 | 1249210.6913
8 | 2682064.3293 | 1249210.6913 | 2682056.5196 | 1249217.3426
9 | 2682064.3293 | 1249210.6913 | 2682050.1468 | 1249190.1148
10 | 2682076.6694 | 1249200.2433 | 2682077.2734 | 1249199.7609
11 | 2682041.8161 | 1249178.0281 | 2682050.1468 | 1249190.1148
12 | 2682090.9744 | 1249188.8186 | 2682077.2734 | 1249199.7609
13 | 2682090.9744 | 1249188.8186 | 2682103.7364 | 1249178.6262
14 | 2682004.3458 | 1249123.6638 | 2682008.8371 | 1249120.5236 | 2682024.6215 | 1249109.4671 | 2682041.9892 | 1249097.242
15 | 2682004.3458 | 1249123.6638 | 2681996.8502 | 1249128.9084
16 | 2682004.3458 | 1249123.6638 | 2682010.342 | 1249132.3643 | 2682020.646 | 1249147.3137
17 | 2682040.7558 | 1249176.4899 | 2682041.8161 | 1249178.0281
18 | 2682040.7558 | 1249176.4899 | 2682036.9907 | 1249171.0273
19 | 2682031.3778 | 1249162.8838 | 2682036.9907 | 1249171.0273
20 | 2682031.3778 | 1249162.8838 | 2682030.0769 | 1249160.9965
21 | 2681996.8502 | 1249128.9084 | 2681982.8624 | 1249138.702
22 | 2682027.8091 | 1249157.7062 | 2682020.646 | 1249147.3137
23 | 2682027.8091 | 1249157.7062 | 2682030.0769 | 1249160.9965

## bus_geodata
| x | y | coords
0 | 2682126.8971 | 1249102.5947
1 | 2682098.0342 | 1249087.8662
2 | 2682212.2987 | 1249145.7933
3 | 2682181.7749 | 1249139.3432
4 | 2682121.0428 | 1249164.6871
5 | 2682201.7144 | 1249150.8516
6 | 2682114.7331 | 1249169.8795
7 | 2682064.3293 | 1249210.6913
8 | 2682076.6694 | 1249200.2433
9 | 2682056.5196 | 1249217.3426
10 | 2682050.1468 | 1249190.1148
11 | 2682077.2734 | 1249199.7609
12 | 2682103.7364 | 1249178.6262
13 | 2682041.9892 | 1249097.242
14 | 2682004.3458 | 1249123.6638
15 | 2682041.8161 | 1249178.0281
16 | 2682090.9744 | 1249188.8186
17 | 2682040.7558 | 1249176.4899
18 | 2682036.9907 | 1249171.0273
19 | 2682031.3778 | 1249162.8838
20 | 2681996.8502 | 1249128.9084
21 | 2682020.646 | 1249147.3137
22 | 2681982.8624 | 1249138.702
23 | 2682027.8091 | 1249157.7062
24 | 2682030.0769 | 1249160.9965
25 | 2682004.3458 | 1249123.6638

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97279 | -0.52417 | 0.083539 | 0.020937
1 | 0.9726 | -0.52797 | 0.0063561 | 0.001593
2 | 0.98081 | -0.367 | 0 | 0
3 | 0.98628 | -0.26138 | 0 | 0
4 | 0.99062 | -0.17819 | 0 | 0
5 | 0.98586 | -0.26958 | 0.019882 | 0.0049829
6 | 0.99104 | -0.17022 | 0.011244 | 0.0028179
7 | 0.99516 | -0.091718 | 0 | 0
8 | 0.99402 | -0.1134 | 0 | 0
9 | 0.99505 | -0.093891 | 0.012032 | 0.0030156
10 | 0.99706 | -0.055613 | 0.011136 | 0.0027909
11 | 0.99397 | -0.11444 | 0.01086 | 0.0027218
12 | 0.99183 | -0.15515 | 0.008889 | 0.0022278
13 | 0.9918 | -0.15779 | 0.078623 | 0.019705
14 | 0.9951 | -0.09393 | 0 | 0
15 | 0.99825 | -0.033039 | 0.017503 | 0.0043866
16 | 0.99281 | -0.13637 | 0.011677 | 0.0029265
17 | 0.99842 | -0.029884 | 0.011207 | 0.0028087
18 | 0.99905 | -0.018039 | 0.0047422 | 0.0011885
19 | 1 | 0 | -0.39857 | -0.10094
20 | 0.99486 | -0.098646 | 0 | 0
21 | 0.99793 | -0.039505 | 0.013835 | 0.0034674
22 | 0.9944 | -0.10747 | 0.029333 | 0.0073514
23 | 0.99934 | -0.012638 | 0.0067383 | 0.0016888
24 | 0.99981 | -0.0036778 | 0.055547 | 0.013921
25 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0063572 | 0.0015933 | -0.0063561 | -0.001593 | 1.1491e-06 | 3.3319e-07 | 0.0097243 | 0.0097244 | 0.0097244 | 0.97279 | -0.52417 | 0.9726 | -0.52797 | 2.6715
1 | -0.089896 | -0.02253 | 0.090575 | 0.022963 | 0.00067863 | 0.00043313 | 0.13751 | 0.13751 | 0.13751 | 0.97279 | -0.52417 | 0.98081 | -0.367 | 37.7771
2 | -0.090575 | -0.022963 | 0.091037 | 0.023258 | 0.00046236 | 0.00029508 | 0.13751 | 0.13751 | 0.13751 | 0.98081 | -0.367 | 0.98628 | -0.26138 | 37.7769
3 | -0.11093 | -0.028246 | 0.11137 | 0.02853 | 0.00044696 | 0.00028388 | 0.16752 | 0.16752 | 0.16752 | 0.98628 | -0.26138 | 0.99062 | -0.17819 | 23.0105
4 | 0.01989 | 0.0049876 | -0.019882 | -0.0049829 | 7.776e-06 | 4.6829e-06 | 0.030009 | 0.030009 | 0.030009 | 0.98628 | -0.26138 | 0.98586 | -0.26958 | 8.2442
5 | -0.11137 | -0.02853 | 0.11142 | 0.028557 | 4.3012e-05 | 2.7317e-05 | 0.16752 | 0.16752 | 0.16752 | 0.99062 | -0.17819 | 0.99104 | -0.17022 | 23.0104
6 | -0.12266 | -0.031375 | 0.12275 | 0.031432 | 8.9582e-05 | 5.697e-05 | 0.1844 | 0.1844 | 0.1844 | 0.99104 | -0.17022 | 0.99183 | -0.15515 | 25.3293
7 | 0.15462 | 0.03959 | -0.15446 | -0.039486 | 0.0001622 | 0.00010339 | 0.23149 | 0.23149 | 0.23149 | 0.99516 | -0.091718 | 0.99402 | -0.1134 | 31.7983
8 | 0.012034 | 0.0030162 | -0.012032 | -0.0030156 | 1.2455e-06 | 6.6383e-07 | 0.017993 | 0.017993 | 0.017993 | 0.99516 | -0.091718 | 0.99505 | -0.093891 | 4.9432
9 | -0.16665 | -0.042606 | 0.16694 | 0.042792 | 0.00029165 | 0.00018601 | 0.24948 | 0.24948 | 0.24948 | 0.99516 | -0.091718 | 0.99706 | -0.055613 | 34.2698
10 | 0.15446 | 0.039486 | -0.15445 | -0.039481 | 7.7674e-06 | 4.9511e-06 | 0.23149 | 0.23149 | 0.23149 | 0.99402 | -0.1134 | 0.99397 | -0.11444 | 31.7983
11 | -0.17808 | -0.045583 | 0.17827 | 0.045707 | 0.0001949 | 0.00012435 | 0.2661 | 0.2661 | 0.2661 | 0.99706 | -0.055613 | 0.99825 | -0.033039 | 36.5526
12 | 0.14359 | 0.036759 | -0.14344 | -0.036662 | 0.0001523 | 9.702e-05 | 0.21523 | 0.21523 | 0.21523 | 0.99397 | -0.11444 | 0.99281 | -0.13637 | 29.565
13 | -0.13164 | -0.03366 | 0.13176 | 0.033736 | 0.00011973 | 7.6207e-05 | 0.19773 | 0.19773 | 0.19773 | 0.99183 | -0.15515 | 0.99281 | -0.13637 | 27.1611
14 | -0.078623 | -0.019705 | 0.078863 | 0.019858 | 0.00023998 | 0.00015299 | 0.11796 | 0.11796 | 0.11796 | 0.9918 | -0.15779 | 0.9951 | -0.09393 | 32.4067
15 | 0.029352 | 0.0073632 | -0.029345 | -0.0073591 | 6.5969e-06 | 4.1034e-06 | 0.043893 | 0.043893 | 0.043893 | 0.9951 | -0.09393 | 0.99486 | -0.098646 | 12.0585
16 | -0.10821 | -0.027221 | 0.1085 | 0.027401 | 0.00028217 | 0.00018021 | 0.16185 | 0.16185 | 0.16185 | 0.9951 | -0.09393 | 0.99793 | -0.039505 | 44.4652
17 | -0.19578 | -0.050094 | 0.19581 | 0.050113 | 2.9908e-05 | 1.9092e-05 | 0.29219 | 0.29219 | 0.29219 | 0.99825 | -0.033039 | 0.99842 | -0.029884 | 40.1363
18 | -0.20701 | -0.052921 | 0.20713 | 0.052997 | 0.00011869 | 7.579e-05 | 0.30889 | 0.30889 | 0.30889 | 0.99842 | -0.029884 | 0.99905 | -0.018039 | 42.4306
19 | -0.21187 | -0.054186 | 0.21206 | 0.054304 | 0.00018513 | 0.00011822 | 0.31596 | 0.31596 | 0.31596 | 0.99905 | -0.018039 | 1 | 0 | 43.4008
20 | 0.18486 | 0.046636 | -0.18483 | -0.046615 | 3.2547e-05 | 2.077e-05 | 0.27519 | 0.27519 | 0.27519 | 1 | 0 | 0.99981 | -0.0036778 | 37.8003
21 | 0.029345 | 0.0073591 | -0.029333 | -0.0073514 | 1.2337e-05 | 7.6739e-06 | 0.043893 | 0.043893 | 0.043893 | 0.99486 | -0.098646 | 0.9944 | -0.10747 | 12.0586
22 | -0.12233 | -0.030869 | 0.12249 | 0.030969 | 0.00015761 | 0.00010071 | 0.18248 | 0.18248 | 0.18248 | 0.99793 | -0.039505 | 0.99934 | -0.012638 | 50.1325
23 | -0.12923 | -0.032658 | 0.12928 | 0.032694 | 5.554e-05 | 3.5493e-05 | 0.19252 | 0.19252 | 0.19252 | 0.99934 | -0.012638 | 0.99981 | -0.0036778 | 52.8889

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.40969 | 0.10373

## res_load
| p_mw | q_mvar
0 | 0.083539 | 0.020937
1 | 0.0063561 | 0.001593
2 | 0.019882 | 0.0049829
3 | 0.011244 | 0.0028179
4 | 0.012032 | 0.0030156
5 | 0.011136 | 0.0027909
6 | 0.01086 | 0.0027218
7 | 0.008889 | 0.0022278
8 | 0.078623 | 0.019705
9 | 0.017503 | 0.0043866
10 | 0.011677 | 0.0029265
11 | 0.011207 | 0.0028087
12 | 0.0047422 | 0.0011885
13 | 0.011117 | 0.0027863
14 | 0.013835 | 0.0034674
15 | 0.029333 | 0.0073514
16 | 0.0067383 | 0.0016888
17 | 0.055547 | 0.013921

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1