## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-439_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-439_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-439_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-439_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-439_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-439_0_5_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_261-439_0_5_node_18 | 0.4 | n |  | TRUE
7 | bus_LV_261-439_0_5_node_17 | 0.4 | n |  | TRUE
8 | bus_LV_261-439_0_5_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_261-439_0_5_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_261-439_0_5_node_23 | 0.4 | n |  | TRUE
11 | bus_LV_261-439_0_5_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_261-439_0_5_node_21 | 0.4 | n |  | TRUE
13 | bus_LV_261-439_0_5_node_22 | 0.4 | n |  | TRUE
14 | bus_LV_261-439_0_5_node_28 | 0.4 | n |  | TRUE
15 | bus_LV_261-439_0_5_node_26 | 0.4 | n |  | TRUE
16 | bus_LV_261-439_0_5_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_261-439_0_5_node_36 | 0.4 | n |  | TRUE
18 | bus_LV_261-439_0_5_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_261-439_0_5_node_33 | 0.4 | n |  | TRUE
20 | bus_LV_261-439_0_5_node_31 | 0.4 | n |  | TRUE
21 | bus_LV_261-439_0_5_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_261-439_0_5_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_261-439_0_5_node_27 | 0.4 | n |  | TRUE
24 | bus_LV_261-439_0_5_node_34 | 0.4 | n |  | TRUE
25 | bus_LV_261-439_0_5_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_261-439_0_5_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_261-439_0_5_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_261-439_0_5_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_261-439_0_5_node_32 | 0.4 | n |  | TRUE
30 | bus_LV_261-439_0_5_node_35 | 0.4 | n |  | TRUE
31 | bus_LV_261-439_0_5_node_30 | 0.4 | n |  | TRUE
32 | bus_MV_529_1_node_133 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-439_0_5_load_0 | 0 | 0.010724 | 0.0026877 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-439_0_5_load_1 | 1 | 0.010802 | 0.0027073 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-439_0_5_load_3 | 3 | 0.024317 | 0.0060944 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-439_0_5_load_4 | 4 | 0.032143 | 0.0080557 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-439_0_5_load_18 | 6 | 0.004168 | 0.0010446 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-439_0_5_load_17 | 7 | 0.032183 | 0.0080658 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-439_0_5_load_23 | 10 | 0.025746 | 0.0064526 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-439_0_5_load_21 | 12 | 0.026385 | 0.0066128 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-439_0_5_load_22 | 13 | 0.076087 | 0.019069 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-439_0_5_load_28 | 14 | 0.011528 | 0.0028892 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-439_0_5_load_26 | 15 | 0.033146 | 0.0083072 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-439_0_5_load_36 | 17 | 0.019451 | 0.004875 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-439_0_5_load_33 | 19 | 0.03157 | 0.0079123 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-439_0_5_load_31 | 20 | 0.0039482 | 0.00098951 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-439_0_5_load_20 | 21 | 0.0040286 | 0.0010097 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-439_0_5_load_27 | 23 | 0.03339 | 0.0083684 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-439_0_5_load_34 | 24 | 0.0036166 | 0.00090641 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-439_0_5_load_24 | 26 | 0.0030361 | 0.00076092 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-439_0_5_load_25 | 27 | 0.0059434 | 0.0014896 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-439_0_5_load_19 | 28 | 0.027829 | 0.0069747 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-439_0_5_load_32 | 29 | 0.0089872 | 0.0022524 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-439_0_5_load_35 | 30 | 0.019841 | 0.0049725 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-439_0_5_load_30 | 31 | 0.0030606 | 0.00076706 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-439_0_5_line_0 |  | 0 | 1 | 0.012602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-439_0_5_line_1 |  | 0 | 2 | 0.016246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-439_0_5_line_2 |  | 1 | 3 | 0.022363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-439_0_5_line_3 |  | 2 | 4 | 0.016126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-439_0_5_line_4 |  | 2 | 5 | 0.025025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-439_0_5_line_5 |  | 3 | 6 | 0.0075443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-439_0_5_line_6 |  | 4 | 7 | 0.018494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_261-439_0_5_line_7 |  | 5 | 13 | 0.020191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-439_0_5_line_8 |  | 7 | 11 | 0.029613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_261-439_0_5_line_9 |  | 8 | 9 | 0.017273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-439_0_5_line_10 |  | 8 | 10 | 0.026358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-439_0_5_line_11 |  | 9 | 14 | 0.026461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-439_0_5_line_12 |  | 9 | 15 | 0.019712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-439_0_5_line_13 |  | 9 | 11 | 0.022956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_261-439_0_5_line_14 |  | 10 | 25 | 0.019571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-439_0_5_line_15 |  | 11 | 12 | 0.015595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-439_0_5_line_16 |  | 12 | 28 | 0.01767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-439_0_5_line_17 |  | 14 | 29 | 0.010475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-439_0_5_line_18 |  | 15 | 23 | 0.020575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-439_0_5_line_19 |  | 16 | 17 | 0.054803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-439_0_5_line_20 |  | 16 | 18 | 0.011613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-439_0_5_line_21 |  | 16 | 19 | 0.030406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-439_0_5_line_22 |  | 18 | 20 | 0.020048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-439_0_5_line_23 |  | 18 | 21 | 0.015244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-439_0_5_line_24 |  | 19 | 29 | 0.013371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-439_0_5_line_25 |  | 22 | 23 | 0.01326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-439_0_5_line_26 |  | 22 | 24 | 0.033666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-439_0_5_line_27 |  | 24 | 30 | 0.0032851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-439_0_5_line_28 |  | 25 | 26 | 0.028927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-439_0_5_line_29 |  | 25 | 27 | 0.011917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-439_0_5_line_30 |  | 26 | 31 | 0.0048451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-439_0_5_trafo_6 | 0.63 MVA 20/0.4 kV | 32 | 11 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2679812.807 | 1247438.4821 | 2679811.7469 | 1247429.3722 | 2679810.3463 | 1247426.24
1 | 2679814.6851 | 1247454.6191 | 2679812.807 | 1247438.4821
2 | 2679810.3463 | 1247426.24 | 2679810.3463 | 1247426.24 | 2679808.2112 | 1247423.8095 | 2679803.6955 | 1247419.7903 | 2679798.1807 | 1247418.1593 | 2679796.3838 | 1247417.5347 | 2679794.7943 | 1247412.3438
3 | 2679814.6851 | 1247454.6191 | 2679798.6481 | 1247456.3085
4 | 2679798.02 | 1247464.313 | 2679797.6411 | 1247460.4829 | 2679815.0981 | 1247458.1605 | 2679814.6851 | 1247454.6191
5 | 2679792.5853 | 1247405.1301 | 2679794.7943 | 1247412.3438
6 | 2679798.6481 | 1247456.3085 | 2679789.0425 | 1247457.3204 | 2679780.2798 | 1247458.452
7 | 2679798.02 | 1247464.313 | 2679799.9904 | 1247484.4075
8 | 2679751.0532 | 1247462.0351 | 2679755.1817 | 1247462.2797 | 2679760.7036 | 1247462.254 | 2679775.241 | 1247459.1027 | 2679780.2798 | 1247458.452
9 | 2679742.564 | 1247466.4687 | 2679745.0024 | 1247471.6163 | 2679747.0691 | 1247475.7693 | 2679750.1579 | 1247481.9821
10 | 2679750.1579 | 1247481.9821 | 2679763.8562 | 1247504.5006
11 | 2679742.564 | 1247466.4687 | 2679741.3227 | 1247463.8501 | 2679738.5197 | 1247457.719 | 2679731.8235 | 1247442.2879
12 | 2679742.564 | 1247466.4687 | 2679739.2302 | 1247468.9145 | 2679725.0024 | 1247475.2573
13 | 2679742.564 | 1247466.4687 | 2679745.0024 | 1247471.6163 | 2679749.2685 | 1247470.0503 | 2679754.4638 | 1247468.4746 | 2679751.0532 | 1247462.0351
14 | 2679774.0272 | 1247521.2205 | 2679763.8562 | 1247504.5006
15 | 2679751.0532 | 1247462.0351 | 2679747.7337 | 1247455.0076 | 2679744.5881 | 1247447.8454
16 | 2679744.5881 | 1247447.8454 | 2679742.7573 | 1247443.6769 | 2679738.4856 | 1247433.8679 | 2679737.6615 | 1247431.5947
17 | 2679727.0799 | 1247432.9524 | 2679731.2008 | 1247440.8528 | 2679731.8235 | 1247442.2879
18 | 2679706.2105 | 1247483.6347 | 2679725.0024 | 1247475.2573
19 | 2679711.6293 | 1247392.0319 | 2679709.099 | 1247393.1432 | 2679668.2537 | 1247411.3743 | 2679661.6822 | 1247414.5772
20 | 2679711.6293 | 1247392.0319 | 2679716.7736 | 1247389.755 | 2679722.4275 | 1247387.7851
21 | 2679711.6293 | 1247392.0319 | 2679719.5613 | 1247414.9886 | 2679721.8917 | 1247420.6452
22 | 2679722.4275 | 1247387.7851 | 2679727.0872 | 1247386.1577 | 2679732.1049 | 1247382.6337 | 2679737.4632 | 1247375.4261
23 | 2679722.4275 | 1247387.7851 | 2679725.1209 | 1247395.8827 | 2679727.3111 | 1247402.2252
24 | 2679727.0799 | 1247432.9524 | 2679725.5235 | 1247429.9685 | 2679722.4726 | 1247422.0551 | 2679721.8917 | 1247420.6452
25 | 2679694.0999 | 1247489.0337 | 2679706.2105 | 1247483.6347
26 | 2679694.0999 | 1247489.0337 | 2679689.6452 | 1247481.0346 | 2679679.6554 | 1247458.6527
27 | 2679678.3164 | 1247455.6528 | 2679679.6554 | 1247458.6527
28 | 2679774.0272 | 1247521.2205 | 2679789.0589 | 1247545.935
29 | 2679774.0272 | 1247521.2205 | 2679763.7922 | 1247527.3243
30 | 2679791.5766 | 1247550.0746 | 2679789.0589 | 1247545.935

## bus_geodata
| x | y | coords
0 | 2679812.807 | 1247438.4821
1 | 2679810.3463 | 1247426.24
2 | 2679814.6851 | 1247454.6191
3 | 2679794.7943 | 1247412.3438
4 | 2679798.6481 | 1247456.3085
5 | 2679798.02 | 1247464.313
6 | 2679792.5853 | 1247405.1301
7 | 2679780.2798 | 1247458.452
8 | 2679750.1579 | 1247481.9821
9 | 2679742.564 | 1247466.4687
10 | 2679763.8562 | 1247504.5006
11 | 2679751.0532 | 1247462.0351
12 | 2679744.5881 | 1247447.8454
13 | 2679799.9904 | 1247484.4075
14 | 2679731.8235 | 1247442.2879
15 | 2679725.0024 | 1247475.2573
16 | 2679711.6293 | 1247392.0319
17 | 2679661.6822 | 1247414.5772
18 | 2679722.4275 | 1247387.7851
19 | 2679721.8917 | 1247420.6452
20 | 2679737.4632 | 1247375.4261
21 | 2679727.3111 | 1247402.2252
22 | 2679694.0999 | 1247489.0337
23 | 2679706.2105 | 1247483.6347
24 | 2679679.6554 | 1247458.6527
25 | 2679774.0272 | 1247521.2205
26 | 2679789.0589 | 1247545.935
27 | 2679763.7922 | 1247527.3243
28 | 2679737.6615 | 1247431.5947
29 | 2679727.0799 | 1247432.9524
30 | 2679678.3164 | 1247455.6528
31 | 2679791.5766 | 1247550.0746
32 | 2679754.4638 | 1247468.4746

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99349 | -0.12507 | 0.010724 | 0.0026877
1 | 0.99303 | -0.13381 | 0.010802 | 0.0027073
2 | 0.99423 | -0.11073 | 0 | 0
3 | 0.99245 | -0.14508 | 0.024317 | 0.0060944
4 | 0.99609 | -0.074942 | 0.032143 | 0.0080557
5 | 0.99249 | -0.14436 | 0 | 0
6 | 0.99242 | -0.14564 | 0.004168 | 0.0010446
7 | 0.99743 | -0.049271 | 0.032183 | 0.0080658
8 | 0.99724 | -0.052997 | 0 | 0
9 | 0.99783 | -0.041563 | 0 | 0
10 | 0.99633 | -0.070469 | 0.025746 | 0.0064526
11 | 1 | 0 | -0.45572 | -0.11463
12 | 0.99923 | -0.014747 | 0.026385 | 0.0066128
13 | 0.99108 | -0.17158 | 0.076087 | 0.019069
14 | 0.99591 | -0.078468 | 0.011528 | 0.0028892
15 | 0.99622 | -0.072669 | 0.033146 | 0.0083072
16 | 0.99378 | -0.11959 | 0 | 0
17 | 0.99281 | -0.13842 | 0.019451 | 0.004875
18 | 0.9937 | -0.12123 | 0 | 0
19 | 0.99454 | -0.10488 | 0.03157 | 0.0079123
20 | 0.99363 | -0.12263 | 0.0039482 | 0.00098951
21 | 0.99364 | -0.12231 | 0.0040286 | 0.0010097
22 | 0.99487 | -0.098708 | 0 | 0
23 | 0.99515 | -0.093232 | 0.03339 | 0.0083684
24 | 0.99415 | -0.11263 | 0.0036166 | 0.00090641
25 | 0.99612 | -0.074608 | 0 | 0
26 | 0.99596 | -0.077706 | 0.0030361 | 0.00076092
27 | 0.99605 | -0.075852 | 0.0059434 | 0.0014896
28 | 0.99879 | -0.023335 | 0.027829 | 0.0069747
29 | 0.99526 | -0.090991 | 0.0089872 | 0.0022524
30 | 0.99409 | -0.11377 | 0.019841 | 0.0049725
31 | 0.99594 | -0.077967 | 0.0030606 | 0.00076706
32 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.039319 | 0.0098662 | -0.039303 | -0.0098558 | 1.6393e-05 | 1.0328e-05 | 0.058895 | 0.058895 | 0.058895 | 0.99349 | -0.12507 | 0.99303 | -0.13381 | 16.1801
1 | -0.050043 | -0.012554 | 0.050078 | 0.012576 | 3.423e-05 | 2.1697e-05 | 0.074958 | 0.074958 | 0.074958 | 0.99349 | -0.12507 | 0.99423 | -0.11073 | 20.5928
2 | 0.0285 | 0.0071485 | -0.028485 | -0.007139 | 1.5296e-05 | 9.5004e-06 | 0.042709 | 0.042709 | 0.042709 | 0.99303 | -0.13381 | 0.99245 | -0.14508 | 11.7332
3 | -0.12639 | -0.031786 | 0.1266 | 0.031924 | 0.00021645 | 0.00013832 | 0.18919 | 0.18919 | 0.18919 | 0.99423 | -0.11073 | 0.99609 | -0.074942 | 51.9766
4 | 0.076308 | 0.01921 | -0.076186 | -0.019132 | 0.00012247 | 7.8055e-05 | 0.11424 | 0.11424 | 0.11424 | 0.99423 | -0.11073 | 0.99249 | -0.14436 | 31.3838
5 | 0.0041682 | 0.0010446 | -0.004168 | -0.0010446 | 1.1049e-07 | -2.6769e-08 | 0.0062494 | 0.0062495 | 0.0062495 | 0.99245 | -0.14508 | 0.99242 | -0.14564 | 1.7169
6 | -0.15874 | -0.03998 | 0.15894 | 0.040104 | 0.00019512 | 0.0001244 | 0.23721 | 0.23721 | 0.23721 | 0.99609 | -0.074942 | 0.99743 | -0.049271 | 32.584
7 | 0.076186 | 0.019132 | -0.076087 | -0.019069 | 9.881e-05 | 6.2978e-05 | 0.11424 | 0.11424 | 0.11424 | 0.99249 | -0.14436 | 0.99108 | -0.17158 | 31.3838
8 | -0.19112 | -0.04817 | 0.19157 | 0.048458 | 0.00045171 | 0.00028832 | 0.28522 | 0.28522 | 0.28522 | 0.99743 | -0.049271 | 1 | 0 | 39.179
9 | -0.037821 | -0.0094914 | 0.037842 | 0.0095044 | 2.0633e-05 | 1.298e-05 | 0.056439 | 0.056439 | 0.056439 | 0.99724 | -0.052997 | 0.99783 | -0.041563 | 15.5053
10 | 0.037821 | 0.0094914 | -0.03779 | -0.0094716 | 3.1485e-05 | 1.9807e-05 | 0.056439 | 0.056439 | 0.056439 | 0.99724 | -0.052997 | 0.99633 | -0.070469 | 15.5053
11 | 0.079772 | 0.020091 | -0.079631 | -0.020001 | 0.0001405 | 8.9576e-05 | 0.11899 | 0.11899 | 0.11899 | 0.99783 | -0.041563 | 0.99591 | -0.078468 | 32.6907
12 | 0.090206 | 0.022689 | -0.090072 | -0.022604 | 0.00013382 | 8.5389e-05 | 0.13455 | 0.13455 | 0.13455 | 0.99783 | -0.041563 | 0.99622 | -0.072669 | 36.9639
13 | -0.20782 | -0.052285 | 0.20823 | 0.052549 | 0.00041359 | 0.0002641 | 0.30998 | 0.30998 | 0.30998 | 0.99783 | -0.041563 | 1 | 0 | 42.5799
14 | 0.012044 | 0.003019 | -0.012041 | -0.0030178 | 2.3746e-06 | 1.2649e-06 | 0.017988 | 0.017988 | 0.017988 | 0.99633 | -0.070469 | 0.99612 | -0.074608 | 4.9417
15 | 0.054264 | 0.013619 | -0.054226 | -0.013595 | 3.8135e-05 | 2.4202e-05 | 0.080753 | 0.080753 | 0.080753 | 1 | 0 | 0.99923 | -0.014747 | 22.1849
16 | 0.027841 | 0.0069818 | -0.027829 | -0.0069747 | 1.139e-05 | 7.0584e-06 | 0.041461 | 0.041461 | 0.041461 | 0.99923 | -0.014747 | 0.99879 | -0.023335 | 11.3904
17 | 0.068103 | 0.017112 | -0.068063 | -0.017086 | 4.0684e-05 | 2.5902e-05 | 0.10177 | 0.10177 | 0.10177 | 0.99591 | -0.078468 | 0.99526 | -0.090991 | 27.9588
18 | 0.056926 | 0.014297 | -0.05687 | -0.014261 | 5.5796e-05 | 3.5442e-05 | 0.085039 | 0.085039 | 0.085039 | 0.99622 | -0.072669 | 0.99515 | -0.093232 | 23.3624
19 | 0.019469 | 0.0048854 | -0.019451 | -0.004875 | 1.7467e-05 | 1.0469e-05 | 0.029153 | 0.029153 | 0.029153 | 0.99378 | -0.11959 | 0.99281 | -0.13842 | 8.0092
20 | 0.0079778 | 0.0019993 | -0.0079772 | -0.001999 | 6.2141e-07 | 2.4725e-07 | 0.011945 | 0.011945 | 0.011945 | 0.99378 | -0.11959 | 0.9937 | -0.12123 | 3.2817
21 | -0.027447 | -0.0068847 | 0.027466 | 0.0068966 | 1.926e-05 | 1.1932e-05 | 0.041099 | 0.041098 | 0.041099 | 0.99378 | -0.11959 | 0.99454 | -0.10488 | 11.2908
22 | 0.0039485 | 0.00098942 | -0.0039482 | -0.00098951 | 2.6283e-07 | -9.1487e-08 | 0.0059126 | 0.0059127 | 0.0059127 | 0.9937 | -0.12123 | 0.99363 | -0.12263 | 1.6244
23 | 0.0040288 | 0.0010096 | -0.0040286 | -0.0010097 | 2.0805e-07 | -6.4309e-08 | 0.0060329 | 0.0060329 | 0.0060329 | 0.9937 | -0.12123 | 0.99364 | -0.12231 | 1.6574
24 | -0.059036 | -0.014809 | 0.059075 | 0.014834 | 3.9125e-05 | 2.4867e-05 | 0.088333 | 0.088333 | 0.088333 | 0.99454 | -0.10488 | 0.99526 | -0.090991 | 24.2674
25 | -0.023474 | -0.0058891 | 0.02348 | 0.0058929 | 6.1301e-06 | 3.751e-06 | 0.035112 | 0.035112 | 0.035112 | 0.99487 | -0.098708 | 0.99515 | -0.093232 | 9.6461
26 | 0.023474 | 0.0058891 | -0.023458 | -0.0058796 | 1.5564e-05 | 9.5244e-06 | 0.035112 | 0.035112 | 0.035112 | 0.99487 | -0.098708 | 0.99415 | -0.11263 | 9.6462
27 | 0.019842 | 0.0049732 | -0.019841 | -0.0049725 | 1.0866e-06 | 6.5281e-07 | 0.029699 | 0.029699 | 0.029699 | 0.99415 | -0.11263 | 0.99409 | -0.11377 | 8.159
28 | 0.0060976 | 0.0015281 | -0.0060967 | -0.0015279 | 9.0002e-07 | 1.9952e-07 | 0.0091087 | 0.0091089 | 0.0091089 | 0.99612 | -0.074608 | 0.99596 | -0.077706 | 2.5024
29 | 0.0059438 | 0.0014896 | -0.0059434 | -0.0014896 | 3.523e-07 | 7.0355e-08 | 0.0088789 | 0.008879 | 0.008879 | 0.99612 | -0.074608 | 0.99605 | -0.075852 | 2.4393
30 | 0.0030606 | 0.00076702 | -0.0030606 | -0.00076706 | 3.7992e-08 | -3.8735e-08 | 0.0045727 | 0.0045728 | 0.0045728 | 0.99596 | -0.077706 | 0.99594 | -0.077967 | 1.2563

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.45572 | 0.11463

## res_load
| p_mw | q_mvar
0 | 0.010724 | 0.0026877
1 | 0.010802 | 0.0027073
2 | 0.024317 | 0.0060944
3 | 0.032143 | 0.0080557
4 | 0.004168 | 0.0010446
5 | 0.032183 | 0.0080658
6 | 0.025746 | 0.0064526
7 | 0.026385 | 0.0066128
8 | 0.076087 | 0.019069
9 | 0.011528 | 0.0028892
10 | 0.033146 | 0.0083072
11 | 0.019451 | 0.004875
12 | 0.03157 | 0.0079123
13 | 0.0039482 | 0.00098951
14 | 0.0040286 | 0.0010097
15 | 0.03339 | 0.0083684
16 | 0.0036166 | 0.00090641
17 | 0.0030361 | 0.00076092
18 | 0.0059434 | 0.0014896
19 | 0.027829 | 0.0069747
20 | 0.0089872 | 0.0022524
21 | 0.019841 | 0.0049725
22 | 0.0030606 | 0.00076706

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1