## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-444_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-444_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-444_0_5_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_261-444_0_5_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_261-444_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-444_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-444_0_5_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_261-444_0_5_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_261-444_0_5_node_36 | 0.4 | n |  | TRUE
9 | bus_LV_261-444_0_5_node_48 | 0.4 | n |  | TRUE
10 | bus_LV_261-444_0_5_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_261-444_0_5_node_77 | 0.4 | n |  | TRUE
12 | bus_LV_261-444_0_5_node_147 | 0.4 | n |  | TRUE
13 | bus_LV_261-444_0_5_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_261-444_0_5_node_35 | 0.4 | n |  | TRUE
15 | bus_LV_261-444_0_5_node_47 | 0.4 | n |  | TRUE
16 | bus_LV_261-444_0_5_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_261-444_0_5_node_7 | 0.4 | n |  | TRUE
18 | bus_LV_261-444_0_5_node_78 | 0.4 | n |  | TRUE
19 | bus_LV_261-444_0_5_node_8 | 0.4 | n |  | TRUE
20 | bus_LV_261-444_0_5_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_261-444_0_5_node_76 | 0.4 | n |  | TRUE
22 | bus_LV_261-444_0_5_node_79 | 0.4 | n |  | TRUE
23 | bus_LV_261-444_0_5_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_261-444_0_5_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_261-444_0_5_node_149 | 0.4 | n |  | TRUE
26 | bus_LV_261-444_0_5_node_75 | 0.4 | n |  | TRUE
27 | bus_LV_261-444_0_5_node_80 | 0.4 | n |  | TRUE
28 | bus_LV_261-444_0_5_node_33 | 0.4 | n |  | TRUE
29 | bus_LV_261-444_0_5_node_150 | 0.4 | n |  | TRUE
30 | bus_LV_261-444_0_5_node_15 | 0.4 | n |  | TRUE
31 | bus_LV_261-444_0_5_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_261-444_0_5_node_17 | 0.4 | n |  | TRUE
33 | bus_LV_261-444_0_5_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_261-444_0_5_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_261-444_0_5_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_261-444_0_5_node_34 | 0.4 | n |  | TRUE
37 | bus_LV_261-444_0_5_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_261-444_0_5_node_21 | 0.4 | n |  | TRUE
39 | bus_LV_261-444_0_5_node_115 | 0.4 | n |  | TRUE
40 | bus_LV_261-444_0_5_node_83 | 0.4 | n |  | TRUE
41 | bus_LV_261-444_0_5_node_82 | 0.4 | n |  | TRUE
42 | bus_LV_261-444_0_5_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_261-444_0_5_node_87 | 0.4 | n |  | TRUE
44 | bus_LV_261-444_0_5_node_105 | 0.4 | n |  | TRUE
45 | bus_LV_261-444_0_5_node_25 | 0.4 | n |  | TRUE
46 | bus_LV_261-444_0_5_node_27 | 0.4 | n |  | TRUE
47 | bus_LV_261-444_0_5_node_117 | 0.4 | n |  | TRUE
48 | bus_LV_261-444_0_5_node_26 | 0.4 | n |  | TRUE
49 | bus_LV_261-444_0_5_node_100 | 0.4 | n |  | TRUE
50 | bus_LV_261-444_0_5_node_97 | 0.4 | n |  | TRUE
51 | bus_LV_261-444_0_5_node_107 | 0.4 | n |  | TRUE
52 | bus_LV_261-444_0_5_node_106 | 0.4 | n |  | TRUE
53 | bus_LV_261-444_0_5_node_28 | 0.4 | n |  | TRUE
54 | bus_LV_261-444_0_5_node_31 | 0.4 | n |  | TRUE
55 | bus_LV_261-444_0_5_node_110 | 0.4 | n |  | TRUE
56 | bus_LV_261-444_0_5_node_29 | 0.4 | n |  | TRUE
57 | bus_LV_261-444_0_5_node_119 | 0.4 | n |  | TRUE
58 | bus_LV_261-444_0_5_node_30 | 0.4 | n |  | TRUE
59 | bus_LV_261-444_0_5_node_108 | 0.4 | n |  | TRUE
60 | bus_LV_261-444_0_5_node_84 | 0.4 | n |  | TRUE
61 | bus_LV_261-444_0_5_node_104 | 0.4 | n |  | TRUE
62 | bus_LV_261-444_0_5_node_102 | 0.4 | n |  | TRUE
63 | bus_LV_261-444_0_5_node_123 | 0.4 | n |  | TRUE
64 | bus_LV_261-444_0_5_node_122 | 0.4 | n |  | TRUE
65 | bus_LV_261-444_0_5_node_98 | 0.4 | n |  | TRUE
66 | bus_LV_261-444_0_5_node_93 | 0.4 | n |  | TRUE
67 | bus_LV_261-444_0_5_node_152 | 0.4 | n |  | TRUE
68 | bus_LV_261-444_0_5_node_136 | 0.4 | n |  | TRUE
69 | bus_LV_261-444_0_5_node_111 | 0.4 | n |  | TRUE
70 | bus_LV_261-444_0_5_node_120 | 0.4 | n |  | TRUE
71 | bus_LV_261-444_0_5_node_133 | 0.4 | n |  | TRUE
72 | bus_LV_261-444_0_5_node_118 | 0.4 | n |  | TRUE
73 | bus_LV_261-444_0_5_node_81 | 0.4 | n |  | TRUE
74 | bus_LV_261-444_0_5_node_37 | 0.4 | n |  | TRUE
75 | bus_LV_261-444_0_5_node_38 | 0.4 | n |  | TRUE
76 | bus_LV_261-444_0_5_node_39 | 0.4 | n |  | TRUE
77 | bus_LV_261-444_0_5_node_42 | 0.4 | n |  | TRUE
78 | bus_LV_261-444_0_5_node_151 | 0.4 | n |  | TRUE
79 | bus_LV_261-444_0_5_node_40 | 0.4 | n |  | TRUE
80 | bus_LV_261-444_0_5_node_128 | 0.4 | n |  | TRUE
81 | bus_LV_261-444_0_5_node_43 | 0.4 | n |  | TRUE
82 | bus_LV_261-444_0_5_node_129 | 0.4 | n |  | TRUE
83 | bus_LV_261-444_0_5_node_127 | 0.4 | n |  | TRUE
84 | bus_LV_261-444_0_5_node_45 | 0.4 | n |  | TRUE
85 | bus_LV_261-444_0_5_node_46 | 0.4 | n |  | TRUE
86 | bus_LV_261-444_0_5_node_132 | 0.4 | n |  | TRUE
87 | bus_LV_261-444_0_5_node_124 | 0.4 | n |  | TRUE
88 | bus_LV_261-444_0_5_node_113 | 0.4 | n |  | TRUE
89 | bus_LV_261-444_0_5_node_114 | 0.4 | n |  | TRUE
90 | bus_LV_261-444_0_5_node_130 | 0.4 | n |  | TRUE
91 | bus_LV_261-444_0_5_node_126 | 0.4 | n |  | TRUE
92 | bus_LV_261-444_0_5_node_125 | 0.4 | n |  | TRUE
93 | bus_LV_261-444_0_5_node_49 | 0.4 | n |  | TRUE
94 | bus_LV_261-444_0_5_node_50 | 0.4 | n |  | TRUE
95 | bus_LV_261-444_0_5_node_51 | 0.4 | n |  | TRUE
96 | bus_LV_261-444_0_5_node_52 | 0.4 | n |  | TRUE
97 | bus_LV_261-444_0_5_node_53 | 0.4 | n |  | TRUE
98 | bus_LV_261-444_0_5_node_54 | 0.4 | n |  | TRUE
99 | bus_LV_261-444_0_5_node_56 | 0.4 | n |  | TRUE
100 | bus_LV_261-444_0_5_node_55 | 0.4 | n |  | TRUE
101 | bus_LV_261-444_0_5_node_59 | 0.4 | n |  | TRUE
102 | bus_LV_261-444_0_5_node_57 | 0.4 | n |  | TRUE
103 | bus_LV_261-444_0_5_node_148 | 0.4 | n |  | TRUE
104 | bus_LV_261-444_0_5_node_58 | 0.4 | n |  | TRUE
105 | bus_LV_261-444_0_5_node_60 | 0.4 | n |  | TRUE
106 | bus_LV_261-444_0_5_node_61 | 0.4 | n |  | TRUE
107 | bus_LV_261-444_0_5_node_140 | 0.4 | n |  | TRUE
108 | bus_LV_261-444_0_5_node_139 | 0.4 | n |  | TRUE
109 | bus_LV_261-444_0_5_node_70 | 0.4 | n |  | TRUE
110 | bus_LV_261-444_0_5_node_73 | 0.4 | n |  | TRUE
111 | bus_LV_261-444_0_5_node_137 | 0.4 | n |  | TRUE
112 | bus_LV_261-444_0_5_node_69 | 0.4 | n |  | TRUE
113 | bus_LV_261-444_0_5_node_71 | 0.4 | n |  | TRUE
114 | bus_LV_261-444_0_5_node_62 | 0.4 | n |  | TRUE
115 | bus_LV_261-444_0_5_node_63 | 0.4 | n |  | TRUE
116 | bus_LV_261-444_0_5_node_64 | 0.4 | n |  | TRUE
117 | bus_LV_261-444_0_5_node_65 | 0.4 | n |  | TRUE
118 | bus_LV_261-444_0_5_node_66 | 0.4 | n |  | TRUE
119 | bus_LV_261-444_0_5_node_67 | 0.4 | n |  | TRUE
120 | bus_LV_261-444_0_5_node_68 | 0.4 | n |  | TRUE
121 | bus_LV_261-444_0_5_node_72 | 0.4 | n |  | TRUE
122 | bus_LV_261-444_0_5_node_74 | 0.4 | n |  | TRUE
123 | bus_LV_261-444_0_5_node_141 | 0.4 | n |  | TRUE
124 | bus_LV_261-444_0_5_node_144 | 0.4 | n |  | TRUE
125 | bus_LV_261-444_0_5_node_146 | 0.4 | n |  | TRUE
126 | bus_LV_261-444_0_5_node_142 | 0.4 | n |  | TRUE
127 | bus_LV_261-444_0_5_node_145 | 0.4 | n |  | TRUE
128 | bus_LV_261-444_0_5_node_85 | 0.4 | n |  | TRUE
129 | bus_LV_261-444_0_5_node_86 | 0.4 | n |  | TRUE
130 | bus_LV_261-444_0_5_node_88 | 0.4 | n |  | TRUE
131 | bus_LV_261-444_0_5_node_90 | 0.4 | n |  | TRUE
132 | bus_LV_261-444_0_5_node_91 | 0.4 | n |  | TRUE
133 | bus_LV_261-444_0_5_node_92 | 0.4 | n |  | TRUE
134 | bus_LV_261-444_0_5_node_94 | 0.4 | n |  | TRUE
135 | bus_LV_261-444_0_5_node_95 | 0.4 | n |  | TRUE
136 | bus_LV_261-444_0_5_node_138 | 0.4 | n |  | TRUE
137 | bus_LV_261-444_0_5_node_134 | 0.4 | n |  | TRUE
138 | bus_LV_261-444_0_5_node_96 | 0.4 | n |  | TRUE
139 | bus_LV_261-444_0_5_node_103 | 0.4 | n |  | TRUE
140 | bus_LV_261-444_0_5_node_99 | 0.4 | n |  | TRUE
141 | bus_LV_261-444_0_5_node_109 | 0.4 | n |  | TRUE
142 | bus_LV_261-444_0_5_node_112 | 0.4 | n |  | TRUE
143 | bus_LV_261-444_0_5_node_121 | 0.4 | n |  | TRUE
144 | bus_LV_261-444_0_5_node_131 | 0.4 | n |  | TRUE
145 | bus_LV_261-444_0_5_node_135 | 0.4 | n |  | TRUE
146 | bus_LV_261-444_0_5_node_143 | 0.4 | n |  | TRUE
147 | bus_MV_529_1_node_47 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-444_0_5_load_0 | 0 | 0.0043617 | 0.0010931 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-444_0_5_load_1 | 1 | 0.0021879 | 0.00054833 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-444_0_5_load_4 | 4 | 0.0021461 | 0.00053787 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-444_0_5_load_5 | 5 | 0.0018612 | 0.00046646 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-444_0_5_load_6 | 6 | 0.0021505 | 0.00053898 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-444_0_5_load_36 | 8 | 0.002489 | 0.00062381 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-444_0_5_load_48 | 9 | 0.0021398 | 0.00053627 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-444_0_5_load_147 | 12 | 0.001189 | 0.00029799 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-444_0_5_load_35 | 14 | 0.0015512 | 0.00038876 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-444_0_5_load_47 | 15 | 0.0036588 | 0.00091699 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-444_0_5_load_7 | 17 | 0.0052003 | 0.0013033 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-444_0_5_load_78 | 18 | 0.010269 | 0.0025737 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-444_0_5_load_8 | 19 | 0.0041597 | 0.0010425 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-444_0_5_load_14 | 20 | 0.015206 | 0.003811 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-444_0_5_load_76 | 21 | 0.010358 | 0.0025961 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-444_0_5_load_79 | 22 | 0.0069104 | 0.0017319 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-444_0_5_load_149 | 25 | 0.0051972 | 0.0013026 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-444_0_5_load_75 | 26 | 0.0071395 | 0.0017893 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-444_0_5_load_80 | 27 | 0.0064786 | 0.0016237 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-444_0_5_load_150 | 29 | 0.0052284 | 0.0013104 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-444_0_5_load_15 | 30 | 0.0037721 | 0.00094538 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-444_0_5_load_16 | 31 | 0.0015862 | 0.00039754 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-444_0_5_load_18 | 33 | 0.0043342 | 0.0010863 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-444_0_5_load_20 | 35 | 0.0016117 | 0.00040393 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-444_0_5_load_34 | 36 | 0.0021342 | 0.00053487 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-444_0_5_load_21 | 38 | 0.0043555 | 0.0010916 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-444_0_5_load_115 | 39 | 0.002086 | 0.00052281 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-444_0_5_load_83 | 40 | 0.0056088 | 0.0014057 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-444_0_5_load_82 | 41 | 0.0068045 | 0.0017054 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-444_0_5_load_87 | 43 | 0.0013737 | 0.00034428 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-444_0_5_load_117 | 47 | 0.0081016 | 0.0020305 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-444_0_5_load_100 | 49 | 0.0047331 | 0.0011862 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-444_0_5_load_97 | 50 | 0.0040634 | 0.0010184 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-444_0_5_load_107 | 51 | 0.0013235 | 0.00033171 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-444_0_5_load_106 | 52 | 0.0012821 | 0.00032132 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-444_0_5_load_110 | 55 | 0.0066953 | 0.001678 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-444_0_5_load_119 | 57 | 0.0086662 | 0.002172 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-444_0_5_load_108 | 59 | 0.0012575 | 0.00031515 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-444_0_5_load_84 | 60 | 0.0057447 | 0.0014398 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-444_0_5_load_104 | 61 | 0.0015923 | 0.00039907 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-444_0_5_load_122 | 64 | 0.0042066 | 0.0010543 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-444_0_5_load_98 | 65 | 0.0048996 | 0.001228 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-444_0_5_load_152 | 67 | 0.0096138 | 0.0024094 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-444_0_5_load_111 | 69 | 0.0055244 | 0.0013846 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-444_0_5_load_120 | 70 | 0.0040088 | 0.0010047 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-444_0_5_load_133 | 71 | 0.019269 | 0.0048292 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-444_0_5_load_81 | 73 | 0.0068994 | 0.0017291 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-444_0_5_load_38 | 75 | 0.0063794 | 0.0015988 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-444_0_5_load_151 | 78 | 0.0056002 | 0.0014036 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-444_0_5_load_128 | 80 | 0.0054601 | 0.0013684 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-444_0_5_load_129 | 82 | 0.00246 | 0.00061654 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-444_0_5_load_127 | 83 | 0.00068085 | 0.00017064 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-444_0_5_load_132 | 86 | 0.00018703 | 4.6875e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-444_0_5_load_124 | 87 | 0.00031356 | 7.8585e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-444_0_5_load_113 | 88 | 0.0024898 | 0.00062401 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-444_0_5_load_114 | 89 | 0.0018283 | 0.00045821 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-444_0_5_load_130 | 90 | 0.000991 | 0.00024837 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-444_0_5_load_126 | 91 | 0.0011756 | 0.00029462 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-444_0_5_load_125 | 92 | 0.00019893 | 4.9856e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-444_0_5_load_50 | 94 | 0.0033518 | 0.00084004 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-444_0_5_load_51 | 95 | 0.0033469 | 0.00083881 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-444_0_5_load_52 | 96 | 0.0023254 | 0.00058279 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-444_0_5_load_53 | 97 | 0.0031267 | 0.00078362 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-444_0_5_load_54 | 98 | 0.0028701 | 0.00071933 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-444_0_5_load_56 | 99 | 0.0056351 | 0.0014123 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-444_0_5_load_57 | 102 | 0.010916 | 0.0027359 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-444_0_5_load_148 | 103 | 0.016584 | 0.0041563 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-444_0_5_load_140 | 107 | 0.017176 | 0.0043047 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-444_0_5_load_139 | 108 | 0.016804 | 0.0042115 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-444_0_5_load_70 | 109 | 0.002677 | 0.00067091 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-444_0_5_load_69 | 112 | 0.0025633 | 0.00064243 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-444_0_5_load_71 | 113 | 0.0025052 | 0.00062786 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-444_0_5_load_62 | 114 | 0.008774 | 0.002199 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-444_0_5_load_63 | 115 | 0.0026088 | 0.00065382 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-444_0_5_load_64 | 116 | 0.0018358 | 0.00046011 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-444_0_5_load_65 | 117 | 0.0026764 | 0.00067077 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-444_0_5_load_66 | 118 | 0.00179 | 0.00044863 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-444_0_5_load_67 | 119 | 0.0058956 | 0.0014776 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-444_0_5_load_68 | 120 | 0.0058508 | 0.0014663 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-444_0_5_load_141 | 123 | 0.0045612 | 0.0011432 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-444_0_5_load_142 | 126 | 0.0021151 | 0.00053009 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-444_0_5_load_145 | 127 | 0.0040694 | 0.0010199 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_261-444_0_5_load_85 | 128 | 0.0076166 | 0.0019089 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_261-444_0_5_load_86 | 129 | 0.0038772 | 0.00097172 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_261-444_0_5_load_88 | 130 | 0.003327 | 0.00083381 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_261-444_0_5_load_90 | 131 | 0.0045534 | 0.0011412 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_261-444_0_5_load_91 | 132 | 0.0044271 | 0.0011095 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_261-444_0_5_load_92 | 133 | 0.0051912 | 0.001301 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_261-444_0_5_load_94 | 134 | 0.0045633 | 0.0011437 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_261-444_0_5_load_95 | 135 | 0.0077344 | 0.0019384 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_261-444_0_5_load_138 | 136 | 0.014059 | 0.0035235 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_261-444_0_5_load_134 | 137 | 0.0049824 | 0.0012487 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_261-444_0_5_load_96 | 138 | 0.0073432 | 0.0018404 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_261-444_0_5_load_103 | 139 | 0.0058141 | 0.0014572 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_261-444_0_5_load_99 | 140 | 0.0031149 | 0.00078068 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_261-444_0_5_load_109 | 141 | 0.0039541 | 0.000991 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_261-444_0_5_load_112 | 142 | 0.0063195 | 0.0015838 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_261-444_0_5_load_121 | 143 | 0.003061 | 0.00076716 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_261-444_0_5_load_131 | 144 | 0.0019989 | 0.00050097 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_261-444_0_5_load_135 | 145 | 0.0049827 | 0.0012488 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_261-444_0_5_load_143 | 146 | 0.0021151 | 0.00053009 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 18 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-444_0_5_line_0 |  | 0 | 1 | 0.0054865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-444_0_5_line_1 |  | 1 | 2 | 0.010289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-444_0_5_line_2 |  | 2 | 7 | 0.027774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-444_0_5_line_3 |  | 2 | 8 | 0.014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-444_0_5_line_4 |  | 3 | 4 | 0.016622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_261-444_0_5_line_5 |  | 3 | 5 | 0.017712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_261-444_0_5_line_6 |  | 3 | 6 | 0.022405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_261-444_0_5_line_7 |  | 4 | 9 | 0.020238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_261-444_0_5_line_8 |  | 5 | 10 | 0.021343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_261-444_0_5_line_9 |  | 6 | 11 | 0.0015099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_261-444_0_5_line_10 |  | 7 | 12 | 0.012558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-444_0_5_line_11 |  | 7 | 13 | 0.004131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-444_0_5_line_12 |  | 8 | 14 | 0.00030844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-444_0_5_line_13 |  | 9 | 15 | 0.010668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_261-444_0_5_line_14 |  | 10 | 16 | 0.021222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_261-444_0_5_line_15 |  | 10 | 17 | 0.0172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-444_0_5_line_16 |  | 11 | 18 | 0.017679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_261-444_0_5_line_17 |  | 13 | 20 | 0.006531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-444_0_5_line_18 |  | 13 | 19 | 0.017256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-444_0_5_line_19 |  | 14 | 74 | 0.011648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-444_0_5_line_20 |  | 15 | 93 | 0.023133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_261-444_0_5_line_21 |  | 16 | 21 | 0.016842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-444_0_5_line_22 |  | 16 | 22 | 0.011176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_261-444_0_5_line_23 |  | 17 | 19 | 0.017252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-444_0_5_line_24 |  | 18 | 128 | 0.032918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-444_0_5_line_25 |  | 21 | 26 | 0.0095334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-444_0_5_line_26 |  | 22 | 27 | 0.0028106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_261-444_0_5_line_27 |  | 23 | 24 | 0.014071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-444_0_5_line_28 |  | 23 | 25 | 0.017271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-444_0_5_line_29 |  | 24 | 28 | 0.021406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-444_0_5_line_30 |  | 25 | 29 | 0.017257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-444_0_5_line_31 |  | 27 | 73 | 0.018443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_261-444_0_5_line_32 |  | 28 | 60 | 0.00026726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_261-444_0_5_line_33 |  | 28 | 41 | 0.023903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_261-444_0_5_line_34 |  | 30 | 31 | 0.027008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-444_0_5_line_35 |  | 30 | 32 | 0.0055706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-444_0_5_line_36 |  | 31 | 33 | 0.001424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-444_0_5_line_37 |  | 32 | 34 | 0.038595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-444_0_5_line_38 |  | 32 | 35 | 0.014483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-444_0_5_line_39 |  | 33 | 36 | 0.0015134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-444_0_5_line_40 |  | 34 | 37 | 0.01327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-444_0_5_line_41 |  | 34 | 38 | 0.024009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-444_0_5_line_42 |  | 35 | 39 | 0.0091853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-444_0_5_line_43 |  | 37 | 40 | 0.01793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_261-444_0_5_line_44 |  | 37 | 41 | 0.022606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_261-444_0_5_line_45 |  | 40 | 43 | 0.02135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_261-444_0_5_line_46 |  | 42 | 43 | 0.01108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_261-444_0_5_line_47 |  | 42 | 44 | 0.015028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_261-444_0_5_line_48 |  | 44 | 61 | 0.025129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-444_0_5_line_49 |  | 44 | 58 | 0.030881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_261-444_0_5_line_50 |  | 45 | 46 | 0.070807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-444_0_5_line_51 |  | 45 | 47 | 0.018973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-444_0_5_line_52 |  | 46 | 51 | 0.01327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_261-444_0_5_line_53 |  | 46 | 52 | 0.0059562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_261-444_0_5_line_54 |  | 48 | 49 | 0.0076646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-444_0_5_line_55 |  | 48 | 50 | 0.0093654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-444_0_5_line_56 |  | 49 | 52 | 0.015198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_261-444_0_5_line_57 |  | 50 | 65 | 0.015968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-444_0_5_line_58 |  | 51 | 59 | 0.017749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_261-444_0_5_line_59 |  | 53 | 54 | 0.008859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-444_0_5_line_60 |  | 53 | 55 | 0.031393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-444_0_5_line_61 |  | 54 | 56 | 0.011286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-444_0_5_line_62 |  | 55 | 69 | 0.023212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-444_0_5_line_63 |  | 56 | 57 | 0.016241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-444_0_5_line_64 |  | 57 | 70 | 0.029736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-444_0_5_line_65 |  | 58 | 59 | 0.031208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_261-444_0_5_line_66 |  | 60 | 73 | 0.013167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_261-444_0_5_line_67 |  | 61 | 139 | 0.02247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-444_0_5_line_68 |  | 62 | 63 | 0.013914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-444_0_5_line_69 |  | 62 | 64 | 0.049882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-444_0_5_line_70 |  | 63 | 127 | 0.048057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-444_0_5_line_71 |  | 65 | 140 | 0.020924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-444_0_5_line_72 |  | 66 | 67 | 0.006223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-444_0_5_line_73 |  | 66 | 68 | 0.016533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-444_0_5_line_74 |  | 68 | 136 | 0.004572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-444_0_5_line_75 |  | 68 | 137 | 0.0063054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-444_0_5_line_76 |  | 69 | 142 | 0.017682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-444_0_5_line_77 |  | 70 | 143 | 0.028106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-444_0_5_line_78 |  | 71 | 72 | 0.027158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-444_0_5_line_79 |  | 72 | 143 | 0.011669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-444_0_5_line_80 |  | 74 | 75 | 0.01916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_261-444_0_5_line_81 |  | 74 | 76 | 0.056463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-444_0_5_line_82 |  | 76 | 77 | 0.16617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_261-444_0_5_line_83 |  | 76 | 78 | 0.068038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_261-444_0_5_line_84 |  | 77 | 81 | 0.28457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_261-444_0_5_line_85 |  | 77 | 82 | 0.038153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_261-444_0_5_line_86 |  | 77 | 79 | 0.014469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_261-444_0_5_line_87 |  | 79 | 80 | 0.00098882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_261-444_0_5_line_88 |  | 81 | 83 | 0.26368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_261-444_0_5_line_89 |  | 82 | 90 | 1.1003e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_261-444_0_5_line_90 |  | 83 | 91 | 0.049772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_261-444_0_5_line_91 |  | 84 | 85 | 0.21861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_261-444_0_5_line_92 |  | 84 | 86 | 0.065423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_261-444_0_5_line_93 |  | 85 | 87 | 0.046749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_261-444_0_5_line_94 |  | 87 | 92 | 0.017944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_261-444_0_5_line_95 |  | 88 | 89 | 0.050938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_261-444_0_5_line_96 |  | 89 | 101 | 0.033725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_261-444_0_5_line_97 |  | 90 | 144 | 0.0041163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_261-444_0_5_line_98 |  | 91 | 92 | 0.010072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_261-444_0_5_line_99 |  | 93 | 94 | 0.022411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_261-444_0_5_line_100 |  | 93 | 95 | 0.012923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_261-444_0_5_line_101 |  | 93 | 96 | 0.013067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_261-444_0_5_line_102 |  | 94 | 97 | 0.0041711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_261-444_0_5_line_103 |  | 95 | 98 | 0.031216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
104 | LV_261-444_0_5_line_104 |  | 96 | 99 | 0.016402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_261-444_0_5_line_105 |  | 98 | 100 | 0.024103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
106 | LV_261-444_0_5_line_106 |  | 100 | 101 | 0.005326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_261-444_0_5_line_107 |  | 100 | 102 | 0.011609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_261-444_0_5_line_108 |  | 101 | 103 | 0.007653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_261-444_0_5_line_109 |  | 102 | 104 | 0.011517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-444_0_5_line_110 |  | 104 | 105 | 0.013082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_261-444_0_5_line_111 |  | 104 | 106 | 0.029756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_261-444_0_5_line_112 |  | 105 | 107 | 0.009591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_261-444_0_5_line_113 |  | 105 | 108 | 0.031533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_261-444_0_5_line_114 |  | 106 | 109 | 0.011758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_261-444_0_5_line_115 |  | 106 | 110 | 0.002696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_261-444_0_5_line_116 |  | 108 | 111 | 0.018737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_261-444_0_5_line_117 |  | 109 | 112 | 0.0068059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_261-444_0_5_line_118 |  | 110 | 113 | 0.015168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_261-444_0_5_line_119 |  | 111 | 145 | 0.014475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_261-444_0_5_line_120 |  | 112 | 117 | 0.013319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_261-444_0_5_line_121 |  | 113 | 121 | 0.0072613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_261-444_0_5_line_122 |  | 114 | 115 | 0.0077026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_261-444_0_5_line_123 |  | 114 | 116 | 0.0060927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_261-444_0_5_line_124 |  | 115 | 117 | 0.0066943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_261-444_0_5_line_125 |  | 116 | 118 | 0.0064893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_261-444_0_5_line_126 |  | 118 | 119 | 0.012982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_261-444_0_5_line_127 |  | 119 | 120 | 0.0016021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_261-444_0_5_line_128 |  | 121 | 122 | 0.004961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_261-444_0_5_line_129 |  | 122 | 123 | 0.022102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_261-444_0_5_line_130 |  | 122 | 124 | 0.01691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_261-444_0_5_line_131 |  | 122 | 125 | 0.02101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_261-444_0_5_line_132 |  | 124 | 126 | 0.0030223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_261-444_0_5_line_133 |  | 125 | 127 | 0.0069338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_261-444_0_5_line_134 |  | 126 | 146 | 0.005523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_261-444_0_5_line_135 |  | 128 | 129 | 0.0021696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_261-444_0_5_line_136 |  | 129 | 130 | 0.02768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_261-444_0_5_line_137 |  | 131 | 132 | 0.015164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_261-444_0_5_line_138 |  | 132 | 133 | 0.016868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_261-444_0_5_line_139 |  | 133 | 134 | 0.018212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_261-444_0_5_line_140 |  | 134 | 135 | 0.020065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_261-444_0_5_line_141 |  | 135 | 138 | 0.012022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_261-444_0_5_line_142 |  | 137 | 145 | 0.011547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_261-444_0_5_line_143 |  | 138 | 139 | 0.023863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_261-444_0_5_line_144 |  | 140 | 141 | 0.016215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_261-444_0_5_line_145 |  | 141 | 142 | 0.017461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-444_0_5_trafo_78 | 0.63 MVA 20/0.4 kV | 147 | 18 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22
0 | 2679063.2673 | 1247247.4914 | 2679060.6709 | 1247242.6582
1 | 2679055.8018 | 1247233.5942 | 2679060.6709 | 1247242.6582
2 | 2679079.5627 | 1247219.1005 | 2679055.8018 | 1247233.5942
3 | 2679055.8018 | 1247233.5942 | 2679049.0719 | 1247221.3179
4 | 2679080.1617 | 1247278.9408 | 2679072.3775 | 1247280.3714 | 2679064.1077 | 1247283.0965 | 2679064.1077 | 1247283.0965
5 | 2679080.1617 | 1247278.9408 | 2679088.9154 | 1247275.6218 | 2679095.5762 | 1247270.5857
6 | 2679080.1617 | 1247278.9408 | 2679081.3846 | 1247286.9296 | 2679081.3574 | 1247301.2531
7 | 2679064.1077 | 1247283.0965 | 2679046.2412 | 1247292.6023
8 | 2679112.6009 | 1247257.7136 | 2679095.5762 | 1247270.5857
9 | 2679081.3546 | 1247302.7629 | 2679081.3574 | 1247301.2531
10 | 2679079.5627 | 1247219.1005 | 2679073.0905 | 1247208.3385
11 | 2679079.5627 | 1247219.1005 | 2679082.1813 | 1247215.8997
12 | 2679049.0719 | 1247221.3179 | 2679048.9236 | 1247221.0474
13 | 2679046.2412 | 1247292.6023 | 2679036.8228 | 1247297.6134
14 | 2679125.9695 | 1247274.2261 | 2679112.6009 | 1247257.7136
15 | 2679112.6009 | 1247257.7136 | 2679102.4821 | 1247243.8046
16 | 2679081.3546 | 1247302.7629 | 2679080.754 | 1247318.9 | 2679080.6594 | 1247320.4279
17 | 2679087.8376 | 1247212.6061 | 2679082.1813 | 1247215.8997
18 | 2679082.1813 | 1247215.8997 | 2679092.3331 | 1247229.8541
19 | 2679043.3245 | 1247210.8336 | 2679048.9236 | 1247221.0474
20 | 2679016.4004 | 1247308.4791 | 2679036.8228 | 1247297.6134
21 | 2679125.9695 | 1247274.2261 | 2679115.386 | 1247286.1714 | 2679114.659 | 1247286.6716
22 | 2679125.9695 | 1247274.2261 | 2679130.0092 | 1247270.9443 | 2679134.8055 | 1247267.3882
23 | 2679102.4821 | 1247243.8046 | 2679092.3331 | 1247229.8541
24 | 2679080.6594 | 1247320.4279 | 2679078.9344 | 1247348.2748 | 2679078.0686 | 1247353.2171
25 | 2679106.805 | 1247292.0752 | 2679114.659 | 1247286.6716
26 | 2679134.8055 | 1247267.3882 | 2679137.0633 | 1247265.7143
27 | 2679149.4648 | 1247229.8518 | 2679138.4028 | 1247238.5883
28 | 2679138.4028 | 1247238.5883 | 2679128.4928 | 1247224.4428
29 | 2679162.6699 | 1247246.7292 | 2679149.4648 | 1247229.8518
30 | 2679128.4928 | 1247224.4428 | 2679118.5913 | 1247210.3094
31 | 2679137.0633 | 1247265.7143 | 2679151.8782 | 1247254.7303
32 | 2679162.6699 | 1247246.7292 | 2679162.4552 | 1247246.8884
33 | 2679162.6699 | 1247246.7292 | 2679181.0884 | 1247231.4945
34 | 2679139.4264 | 1247157.1031 | 2679158.7978 | 1247175.9228
35 | 2679162.7933 | 1247179.8045 | 2679158.7978 | 1247175.9228
36 | 2679139.4264 | 1247157.1031 | 2679138.405 | 1247156.1108
37 | 2679190.2929 | 1247206.6466 | 2679182.7744 | 1247201.7538 | 2679162.7933 | 1247179.8045
38 | 2679162.7933 | 1247179.8045 | 2679171.8351 | 1247168.4905
39 | 2679137.3195 | 1247155.0563 | 2679138.405 | 1247156.1108
40 | 2679190.2929 | 1247206.6466 | 2679198.5079 | 1247217.0861
41 | 2679190.2929 | 1247206.6466 | 2679182.5371 | 1247207.0767 | 2679174.9744 | 1247209.4442 | 2679168.4804 | 1247214.6393
42 | 2679171.8351 | 1247168.4905 | 2679177.5696 | 1247161.3151
43 | 2679198.5079 | 1247217.0861 | 2679210.4836 | 1247230.4297
44 | 2679198.5079 | 1247217.0861 | 2679181.0884 | 1247231.4945
45 | 2679210.4836 | 1247230.4297 | 2679216.3857 | 1247237.006 | 2679224.8602 | 1247246.2131
46 | 2679232.3638 | 1247254.3654 | 2679224.8602 | 1247246.2131
47 | 2679232.3638 | 1247254.3654 | 2679241.9684 | 1247265.9466
48 | 2679241.9684 | 1247265.9466 | 2679222.3696 | 1247281.6735
49 | 2679241.9684 | 1247265.9466 | 2679262.3698 | 1247289.1805
50 | 2679214.822 | 1247329.1299 | 2679217.7595 | 1247333.7169 | 2679215.8234 | 1247335.0253 | 2679219.2899 | 1247340.7202 | 2679224.6847 | 1247348.509 | 2679254.7885 | 1247384.4484
51 | 2679254.7885 | 1247384.4484 | 2679240.6586 | 1247397.1105
52 | 2679214.822 | 1247329.1299 | 2679225.6539 | 1247321.4638
53 | 2679214.822 | 1247329.1299 | 2679209.9595 | 1247332.5697
54 | 2679191.1412 | 1247345.5478 | 2679197.3592 | 1247341.4834 | 2679197.5519 | 1247341.3471
55 | 2679191.1412 | 1247345.5478 | 2679183.2995 | 1247350.668
56 | 2679197.5519 | 1247341.3471 | 2679209.9595 | 1247332.5697
57 | 2679183.2995 | 1247350.668 | 2679170.8491 | 1247358.7976 | 2679169.9323 | 1247359.4024
58 | 2679225.6539 | 1247321.4638 | 2679232.9712 | 1247316.2852 | 2679239.4549 | 1247310.3586
59 | 2679053.0558 | 1247428.1323 | 2679061.002 | 1247424.1687
60 | 2679061.002 | 1247424.1687 | 2679089.0973 | 1247410.1625
61 | 2679053.0558 | 1247428.1323 | 2679055.2427 | 1247432.3645 | 2679058.2473 | 1247438.1532
62 | 2679089.0973 | 1247410.1625 | 2679091.7832 | 1247408.8235 | 2679109.1974 | 1247398.5661
63 | 2679058.2473 | 1247438.1532 | 2679072.7702 | 1247430.8818
64 | 2679072.7702 | 1247430.8818 | 2679079.5544 | 1247427.4851 | 2679099.1114 | 1247417.0886
65 | 2679262.3698 | 1247289.1805 | 2679260.7378 | 1247290.9044 | 2679239.4549 | 1247310.3586
66 | 2679162.4552 | 1247246.8884 | 2679151.8782 | 1247254.7303
67 | 2679204.844 | 1247295.7367 | 2679222.3696 | 1247281.6735
68 | 2678971.1278 | 1247488.4624 | 2678969.9654 | 1247487.2683 | 2678965.6335 | 1247482.4516 | 2678961.7708 | 1247478.1415
69 | 2678971.1278 | 1247488.4624 | 2678984.891 | 1247475.3584 | 2679009.1504 | 1247456.2543
70 | 2678961.7708 | 1247478.1415 | 2678959.3153 | 1247472.5158 | 2678951.7565 | 1247431.2838
71 | 2679169.9323 | 1247359.4024 | 2679152.4672 | 1247370.9248
72 | 2679027.4587 | 1247401.961 | 2679027.6855 | 1247408.1797
73 | 2679015.2208 | 1247392.9915 | 2679017.228 | 1247393.1405 | 2679022.5306 | 1247401.0725 | 2679027.4587 | 1247401.961
74 | 2679010.6479 | 1247392.6525 | 2679015.2208 | 1247392.9915
75 | 2679015.2208 | 1247392.9915 | 2679016.4767 | 1247387.7377 | 2679016.2975 | 1247386.8521
76 | 2679109.1974 | 1247398.5661 | 2679122.0006 | 1247391.0247 | 2679124.3571 | 1247389.47
77 | 2679099.1114 | 1247417.0886 | 2679107.6715 | 1247412.5381 | 2679123.5881 | 1247403.2838
78 | 2679133.676 | 1247397.4184 | 2679156.2536 | 1247382.3253
79 | 2679133.676 | 1247397.4184 | 2679123.5881 | 1247403.2838
80 | 2679043.3245 | 1247210.8336 | 2679032.9048 | 1247214.4641 | 2679029.1175 | 1247215.8146 | 2679025.0174 | 1247215.1261
81 | 2679016.1111 | 1247163.0363 | 2679021.3795 | 1247171.2792 | 2679034.743 | 1247192.1724 | 2679038.7737 | 1247200.332 | 2679038.5861 | 1247207.0344 | 2679043.3245 | 1247210.8336
82 | 2678962.0929 | 1247021.3697 | 2678975.5733 | 1247025.5967 | 2678979.7003 | 1247028.8095 | 2678983.8172 | 1247035.0467 | 2678982.9295 | 1247041.5729 | 2678982.6008 | 1247050.9309 | 2678982.1446 | 1247060.7875 | 2678981.6089 | 1247073.2116 | 2678981.2514 | 1247084.7374 | 2678981.0003 | 1247094.5078 | 2678981.1909 | 1247098.3465 | 2678982.0225 | 1247103.9617 | 2678982.899 | 1247108.4766 | 2678983.9296 | 1247111.6371 | 2678985.9469 | 1247117.268 | 2678988.5236 | 1247124.0072 | 2678989.1394 | 1247125.4164 | 2678990.9057 | 1247129.4762 | 2678992.3894 | 1247132.0757 | 2678995.2004 | 1247133.7032 | 2678997.1895 | 1247134.6526 | 2679001.314 | 1247136.9092 | 2679016.1111 | 1247163.0363
83 | 2679016.1111 | 1247163.0363 | 2679026.1588 | 1247156.7212 | 2679073.7285 | 1247126.8513
84 | 2678962.0929 | 1247021.3697 | 2678948.877 | 1246994.452 | 2678991.0684 | 1246982.9388 | 2679004.2135 | 1246981.157 | 2679034.8286 | 1246978.4296 | 2679065.7872 | 1246967.5009 | 2679071.2853 | 1246961.9368 | 2679091.6822 | 1246947.1425 | 2679156.4178 | 1246875.5097 | 2679157.9636 | 1246873.4621 | 2679158.4562 | 1246871.6452
85 | 2678962.0929 | 1247021.3697 | 2678947.9211 | 1247035.0243 | 2678932.1161 | 1247044.5883
86 | 2678962.0929 | 1247021.3697 | 2678963.7946 | 1247026.3182 | 2678964.2609 | 1247035.5422
87 | 2678963.55 | 1247036.2295 | 2678964.2609 | 1247035.5422
88 | 2679158.4562 | 1246871.6452 | 2679126.4017 | 1246881.4246 | 2678955.9299 | 1246932.2675 | 2678939.3489 | 1246937.3505 | 2678907.0416 | 1246950.6302
89 | 2678932.1151 | 1247044.5889 | 2678932.1161 | 1247044.5883
90 | 2678862.251 | 1246972.3279 | 2678905.7838 | 1246951.1472 | 2678907.0416 | 1246950.6302
91 | 2678795.2335 | 1247005.4502 | 2678795.7044 | 1247008.67 | 2678793.1569 | 1247014.4848 | 2678788.2809 | 1247018.7453 | 2678779.9543 | 1247024.0163 | 2678776.5521 | 1247018.556 | 2678766.364 | 1247004.177 | 2678764.309 | 1247001.3588 | 2678777.8986 | 1246991.1318 | 2678782.1438 | 1246990.5767 | 2678788.7985 | 1246992.8779 | 2678794.3152 | 1246989.8601 | 2678801.5338 | 1246985.5417 | 2678857.3995 | 1246959.1429 | 2678887.3994 | 1246943.0412 | 2678880.9004 | 1246935.8496 | 2678866.7454 | 1246927.2329
92 | 2678866.7454 | 1246927.2329 | 2678821.5142 | 1246950.8932 | 2678808.036 | 1246955.8964
93 | 2678795.2335 | 1247005.4502 | 2678814.662 | 1246996.3907 | 2678837.2273 | 1246984.9238
94 | 2678837.2273 | 1246984.9238 | 2678853.224 | 1246976.7949
95 | 2678991.7542 | 1247240.9008 | 2678987.6234 | 1247253.9006 | 2678984.2291 | 1247264.3074 | 2678979.8466 | 1247275.1792 | 2678974.2208 | 1247284.6889 | 2678972.1708 | 1247287.6241
96 | 2678953.7676 | 1247315.7281 | 2678954.8695 | 1247312.3959 | 2678972.1708 | 1247287.6241
97 | 2678928.5934 | 1247046.72 | 2678932.1151 | 1247044.5889
98 | 2678862.251 | 1246972.3279 | 2678856.6895 | 1246975.0338 | 2678853.224 | 1246976.7949
99 | 2679016.4004 | 1247308.4791 | 2679016.9121 | 1247310.8877 | 2679018.1758 | 1247320.9229 | 2679022.6972 | 1247329.6562
100 | 2679016.4004 | 1247308.4791 | 2679004.8227 | 1247314.2203
101 | 2679016.4004 | 1247308.4791 | 2679011.4858 | 1247296.3715
102 | 2679022.6972 | 1247329.6562 | 2679022.6972 | 1247329.6562 | 2679023.4218 | 1247333.7639
103 | 2679004.8227 | 1247314.2203 | 2678997.3375 | 1247317.932 | 2678989.3148 | 1247321.3944 | 2678983.3697 | 1247318.0239 | 2678976.1086 | 1247318.6661
104 | 2679003.4657 | 1247282.0654 | 2679006.4346 | 1247287.142 | 2679011.4858 | 1247296.3715
105 | 2678952.0988 | 1247320.7873 | 2678955.5095 | 1247320.488 | 2678976.1086 | 1247318.6661
106 | 2678952.0988 | 1247320.7873 | 2678953.7676 | 1247315.7281
107 | 2678952.0988 | 1247320.7873 | 2678950.1551 | 1247329.4788 | 2678950.1147 | 1247332.1817
108 | 2678953.7676 | 1247315.7281 | 2678946.1164 | 1247315.1146
109 | 2678949.943 | 1247343.6975 | 2678950.1147 | 1247332.1817
110 | 2678949.943 | 1247343.6975 | 2678959.4434 | 1247343.8463 | 2678962.9594 | 1247344.7048
111 | 2678949.943 | 1247343.6975 | 2678948.7161 | 1247373.4249
112 | 2678962.9594 | 1247344.7048 | 2678969.9851 | 1247346.9111 | 2678972.1391 | 1247346.2504
113 | 2678962.9594 | 1247344.7048 | 2678962.0893 | 1247348.218 | 2678964.3816 | 1247353.052 | 2678969.9856 | 1247355.9398 | 2678974.6484 | 1247359.1709 | 2678979.1359 | 1247366.4916 | 2678980.7046 | 1247367.7321
114 | 2678948.7161 | 1247373.4249 | 2678937.0119 | 1247372.2976
115 | 2678948.7161 | 1247373.4249 | 2678948.8539 | 1247376.1176
116 | 2678997.4824 | 1247375.0644 | 2678990.9938 | 1247373.9438 | 2678986.2294 | 1247372.1012 | 2678980.7046 | 1247367.7321
117 | 2678930.2374 | 1247371.6451 | 2678937.0119 | 1247372.2976
118 | 2678948.8539 | 1247376.1176 | 2678948.9379 | 1247391.2855
119 | 2678997.4824 | 1247375.0644 | 2679004.3177 | 1247373.9768 | 2679011.3355 | 1247376.7724 | 2679011.3355 | 1247376.7724
120 | 2678930.2374 | 1247371.6451 | 2678916.9796 | 1247370.3682
121 | 2678948.9782 | 1247398.5467 | 2678948.9379 | 1247391.2855
122 | 2678902.649 | 1247368.9879 | 2678910.3162 | 1247369.7264
123 | 2678902.649 | 1247368.9879 | 2678896.5845 | 1247368.4038
124 | 2678910.3162 | 1247369.7264 | 2678916.9796 | 1247370.3682
125 | 2678890.1251 | 1247367.7816 | 2678896.5845 | 1247368.4038
126 | 2678890.1251 | 1247367.7816 | 2678877.2029 | 1247366.537
127 | 2678875.6082 | 1247366.3834 | 2678877.2029 | 1247366.537
128 | 2678949.048 | 1247403.5068 | 2678948.9782 | 1247398.5467
129 | 2678949.048 | 1247403.5068 | 2678958.4488 | 1247400.9189 | 2678970.7997 | 1247400.85
130 | 2678949.048 | 1247403.5068 | 2678944.338 | 1247404.3891 | 2678932.1711 | 1247404.2604
131 | 2678949.048 | 1247403.5068 | 2678950.5062 | 1247424.4636
132 | 2678932.1711 | 1247404.2604 | 2678929.1985 | 1247403.7141
133 | 2678950.5062 | 1247424.4636 | 2678951.7565 | 1247431.2838
134 | 2678929.1985 | 1247403.7141 | 2678923.7666 | 1247402.7158
135 | 2679077.6943 | 1247355.3541 | 2679078.0686 | 1247353.2171
136 | 2679077.6943 | 1247355.3541 | 2679076.2526 | 1247363.5835 | 2679071.3667 | 1247382.2806
137 | 2679118.3362 | 1247357.2231 | 2679131.0411 | 1247348.9444
138 | 2679145.1732 | 1247339.7355 | 2679131.0411 | 1247348.9444
139 | 2679145.1732 | 1247339.7355 | 2679154.7962 | 1247333.4649 | 2679160.1744 | 1247329.4247
140 | 2679160.1744 | 1247329.4247 | 2679176.2172 | 1247317.3731
141 | 2679185.8292 | 1247310.1523 | 2679176.2172 | 1247317.3731
142 | 2679011.3355 | 1247376.7724 | 2679015.2649 | 1247381.7505 | 2679016.2975 | 1247386.8521
143 | 2679185.8292 | 1247310.1523 | 2679202.2788 | 1247297.7951 | 2679204.844 | 1247295.7367
144 | 2679138.932 | 1247379.8544 | 2679152.4672 | 1247370.9248
145 | 2679138.932 | 1247379.8544 | 2679124.3571 | 1247389.47

## bus_geodata
| x | y | coords
0 | 2679063.2673 | 1247247.4914
1 | 2679060.6709 | 1247242.6582
2 | 2679055.8018 | 1247233.5942
3 | 2679080.1617 | 1247278.9408
4 | 2679064.1077 | 1247283.0965
5 | 2679095.5762 | 1247270.5857
6 | 2679081.3574 | 1247301.2531
7 | 2679079.5627 | 1247219.1005
8 | 2679049.0719 | 1247221.3179
9 | 2679046.2412 | 1247292.6023
10 | 2679112.6009 | 1247257.7136
11 | 2679081.3546 | 1247302.7629
12 | 2679073.0905 | 1247208.3385
13 | 2679082.1813 | 1247215.8997
14 | 2679048.9236 | 1247221.0474
15 | 2679036.8228 | 1247297.6134
16 | 2679125.9695 | 1247274.2261
17 | 2679102.4821 | 1247243.8046
18 | 2679080.6594 | 1247320.4279
19 | 2679092.3331 | 1247229.8541
20 | 2679087.8376 | 1247212.6061
21 | 2679114.659 | 1247286.6716
22 | 2679134.8055 | 1247267.3882
23 | 2679138.4028 | 1247238.5883
24 | 2679149.4648 | 1247229.8518
25 | 2679128.4928 | 1247224.4428
26 | 2679106.805 | 1247292.0752
27 | 2679137.0633 | 1247265.7143
28 | 2679162.6699 | 1247246.7292
29 | 2679118.5913 | 1247210.3094
30 | 2679158.7978 | 1247175.9228
31 | 2679139.4264 | 1247157.1031
32 | 2679162.7933 | 1247179.8045
33 | 2679138.405 | 1247156.1108
34 | 2679190.2929 | 1247206.6466
35 | 2679171.8351 | 1247168.4905
36 | 2679137.3195 | 1247155.0563
37 | 2679198.5079 | 1247217.0861
38 | 2679168.4804 | 1247214.6393
39 | 2679177.5696 | 1247161.3151
40 | 2679210.4836 | 1247230.4297
41 | 2679181.0884 | 1247231.4945
42 | 2679232.3638 | 1247254.3654
43 | 2679224.8602 | 1247246.2131
44 | 2679241.9684 | 1247265.9466
45 | 2679254.7885 | 1247384.4484
46 | 2679214.822 | 1247329.1299
47 | 2679240.6586 | 1247397.1105
48 | 2679191.1412 | 1247345.5478
49 | 2679197.5519 | 1247341.3471
50 | 2679183.2995 | 1247350.668
51 | 2679225.6539 | 1247321.4638
52 | 2679209.9595 | 1247332.5697
53 | 2679061.002 | 1247424.1687
54 | 2679053.0558 | 1247428.1323
55 | 2679089.0973 | 1247410.1625
56 | 2679058.2473 | 1247438.1532
57 | 2679072.7702 | 1247430.8818
58 | 2679262.3698 | 1247289.1805
59 | 2679239.4549 | 1247310.3586
60 | 2679162.4552 | 1247246.8884
61 | 2679222.3696 | 1247281.6735
62 | 2678971.1278 | 1247488.4624
63 | 2678961.7708 | 1247478.1415
64 | 2679009.1504 | 1247456.2543
65 | 2679169.9323 | 1247359.4024
66 | 2679027.4587 | 1247401.961
67 | 2679027.6855 | 1247408.1797
68 | 2679015.2208 | 1247392.9915
69 | 2679109.1974 | 1247398.5661
70 | 2679099.1114 | 1247417.0886
71 | 2679156.2536 | 1247382.3253
72 | 2679133.676 | 1247397.4184
73 | 2679151.8782 | 1247254.7303
74 | 2679043.3245 | 1247210.8336
75 | 2679025.0174 | 1247215.1261
76 | 2679016.1111 | 1247163.0363
77 | 2678962.0929 | 1247021.3697
78 | 2679073.7285 | 1247126.8513
79 | 2678964.2609 | 1247035.5422
80 | 2678963.55 | 1247036.2295
81 | 2679158.4562 | 1246871.6452
82 | 2678932.1161 | 1247044.5883
83 | 2678907.0416 | 1246950.6302
84 | 2678866.7454 | 1246927.2329
85 | 2678795.2335 | 1247005.4502
86 | 2678808.036 | 1246955.8964
87 | 2678837.2273 | 1246984.9238
88 | 2678991.7542 | 1247240.9008
89 | 2678972.1708 | 1247287.6241
90 | 2678932.1151 | 1247044.5889
91 | 2678862.251 | 1246972.3279
92 | 2678853.224 | 1246976.7949
93 | 2679016.4004 | 1247308.4791
94 | 2679022.6972 | 1247329.6562
95 | 2679004.8227 | 1247314.2203
96 | 2679011.4858 | 1247296.3715
97 | 2679023.4218 | 1247333.7639
98 | 2678976.1086 | 1247318.6661
99 | 2679003.4657 | 1247282.0654
100 | 2678952.0988 | 1247320.7873
101 | 2678953.7676 | 1247315.7281
102 | 2678950.1147 | 1247332.1817
103 | 2678946.1164 | 1247315.1146
104 | 2678949.943 | 1247343.6975
105 | 2678962.9594 | 1247344.7048
106 | 2678948.7161 | 1247373.4249
107 | 2678972.1391 | 1247346.2504
108 | 2678980.7046 | 1247367.7321
109 | 2678937.0119 | 1247372.2976
110 | 2678948.8539 | 1247376.1176
111 | 2678997.4824 | 1247375.0644
112 | 2678930.2374 | 1247371.6451
113 | 2678948.9379 | 1247391.2855
114 | 2678902.649 | 1247368.9879
115 | 2678910.3162 | 1247369.7264
116 | 2678896.5845 | 1247368.4038
117 | 2678916.9796 | 1247370.3682
118 | 2678890.1251 | 1247367.7816
119 | 2678877.2029 | 1247366.537
120 | 2678875.6082 | 1247366.3834
121 | 2678948.9782 | 1247398.5467
122 | 2678949.0481 | 1247403.5068
123 | 2678970.7997 | 1247400.85
124 | 2678932.1711 | 1247404.2604
125 | 2678950.5062 | 1247424.4636
126 | 2678929.1985 | 1247403.7141
127 | 2678951.7565 | 1247431.2838
128 | 2679078.0686 | 1247353.2171
129 | 2679077.6943 | 1247355.3541
130 | 2679071.3667 | 1247382.2806
131 | 2679118.3362 | 1247357.2231
132 | 2679131.0411 | 1247348.9444
133 | 2679145.1732 | 1247339.7355
134 | 2679160.1744 | 1247329.4247
135 | 2679176.2172 | 1247317.3731
136 | 2679010.6479 | 1247392.6525
137 | 2679016.2975 | 1247386.8521
138 | 2679185.8292 | 1247310.1523
139 | 2679204.844 | 1247295.7367
140 | 2679152.4672 | 1247370.9248
141 | 2679138.932 | 1247379.8544
142 | 2679124.3571 | 1247389.47
143 | 2679123.5881 | 1247403.2838
144 | 2678928.5934 | 1247046.72
145 | 2679011.3355 | 1247376.7724
146 | 2678923.7666 | 1247402.7158
147 | 2679081.3546 | 1247302.7629

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98923 | -0.20637 | 0.0043617 | 0.0010931
1 | 0.98925 | -0.20595 | 0.0021879 | 0.00054833
2 | 0.98932 | -0.20475 | 0 | 0
3 | 0.99557 | -0.084141 | 0 | 0
4 | 0.99488 | -0.097473 | 0.0021461 | 0.00053787
5 | 0.99444 | -0.10588 | 0.0018612 | 0.00046646
6 | 0.99795 | -0.038822 | 0.0021505 | 0.00053898
7 | 0.99023 | -0.18692 | 0 | 0
8 | 0.98894 | -0.21211 | 0.002489 | 0.00062381
9 | 0.99404 | -0.11354 | 0.0021398 | 0.00053627
10 | 0.99308 | -0.13197 | 0 | 0
11 | 0.99811 | -0.035762 | 0 | 0
12 | 0.99022 | -0.18718 | 0.001189 | 0.00029799
13 | 0.99038 | -0.18418 | 0 | 0
14 | 0.98893 | -0.21226 | 0.0015512 | 0.00038876
15 | 0.9936 | -0.12192 | 0.0036588 | 0.00091699
16 | 0.99202 | -0.15217 | 0 | 0
17 | 0.9921 | -0.15079 | 0.0052003 | 0.0013033
18 | 1 | 0 | -0.4859 | -0.12373
19 | 0.99121 | -0.1681 | 0.0041597 | 0.0010425
20 | 0.99028 | -0.18595 | 0.015206 | 0.003811
21 | 0.99175 | -0.15739 | 0.010358 | 0.0025961
22 | 0.99151 | -0.16195 | 0.0069104 | 0.0017319
23 | 0.98972 | -0.19657 | 0 | 0
24 | 0.98985 | -0.19396 | 0 | 0
25 | 0.98955 | -0.19977 | 0.0051972 | 0.0013026
26 | 0.99169 | -0.15859 | 0.0071395 | 0.0017893
27 | 0.99139 | -0.16433 | 0.0064786 | 0.0016237
28 | 0.99006 | -0.18999 | 0 | 0
29 | 0.98947 | -0.20138 | 0.0052284 | 0.0013104
30 | 0.98751 | -0.23928 | 0.0037721 | 0.00094538
31 | 0.98731 | -0.24317 | 0.0015862 | 0.00039754
32 | 0.98757 | -0.2381 | 0 | 0
33 | 0.9873 | -0.24334 | 0.0043342 | 0.0010863
34 | 0.98812 | -0.2274 | 0 | 0
35 | 0.98752 | -0.23906 | 0.0016117 | 0.00040393
36 | 0.98729 | -0.24339 | 0.0021342 | 0.00053487
37 | 0.98836 | -0.22269 | 0 | 0
38 | 0.98802 | -0.22927 | 0.0043555 | 0.0010916
39 | 0.9875 | -0.2394 | 0.002086 | 0.00052281
40 | 0.9878 | -0.23346 | 0.0056088 | 0.0014057
41 | 0.98917 | -0.20713 | 0.0068045 | 0.0017054
42 | 0.98684 | -0.25207 | 0 | 0
43 | 0.98716 | -0.24575 | 0.0013737 | 0.00034428
44 | 0.98639 | -0.26065 | 0 | 0
45 | 0.98401 | -0.30677 | 0 | 0
46 | 0.98454 | -0.29645 | 0 | 0
47 | 0.98387 | -0.30954 | 0.0081016 | 0.0020305
48 | 0.98331 | -0.32027 | 0 | 0
49 | 0.98381 | -0.31066 | 0.0047331 | 0.0011862
50 | 0.98271 | -0.33203 | 0.0040634 | 0.0010184
51 | 0.9848 | -0.29146 | 0.0013235 | 0.00033171
52 | 0.98433 | -0.3005 | 0.0012821 | 0.00032132
53 | 0.97612 | -0.46075 | 0 | 0
54 | 0.97583 | -0.46642 | 0 | 0
55 | 0.97714 | -0.44067 | 0.0066953 | 0.001678
56 | 0.97546 | -0.47366 | 0 | 0
57 | 0.97493 | -0.48408 | 0.0086662 | 0.002172
58 | 0.98578 | -0.27259 | 0 | 0
59 | 0.98515 | -0.28468 | 0.0012575 | 0.00031515
60 | 0.99007 | -0.18979 | 0.0057447 | 0.0014398
61 | 0.98544 | -0.27923 | 0.0015923 | 0.00039907
62 | 0.9842 | -0.30389 | 0 | 0
63 | 0.98425 | -0.30283 | 0 | 0
64 | 0.98401 | -0.30766 | 0.0042066 | 0.0010543
65 | 0.98174 | -0.35093 | 0.0048996 | 0.001228
66 | 0.98275 | -0.33212 | 0 | 0
67 | 0.9827 | -0.3332 | 0.0096138 | 0.0024094
68 | 0.9829 | -0.32925 | 0 | 0
69 | 0.97804 | -0.42301 | 0.0055244 | 0.0013846
70 | 0.9742 | -0.49845 | 0.0040088 | 0.0010047
71 | 0.97292 | -0.52375 | 0.019269 | 0.0048292
72 | 0.97341 | -0.51412 | 0 | 0
73 | 0.99061 | -0.17941 | 0.0068994 | 0.0017291
74 | 0.98866 | -0.21755 | 0 | 0
75 | 0.98854 | -0.21973 | 0.0063794 | 0.0015988
76 | 0.98767 | -0.23681 | 0 | 0
77 | 0.98561 | -0.27698 | 0 | 0
78 | 0.98732 | -0.24362 | 0.0056002 | 0.0014036
79 | 0.98554 | -0.2784 | 0 | 0
80 | 0.98553 | -0.2785 | 0.0054601 | 0.0013684
81 | 0.98494 | -0.29018 | 0 | 0
82 | 0.98542 | -0.28071 | 0.00246 | 0.00061654
83 | 0.98432 | -0.30238 | 0.00068085 | 0.00017064
84 | 0.98417 | -0.30528 | 0 | 0
85 | 0.98421 | -0.30453 | 0 | 0
86 | 0.98416 | -0.3055 | 0.00018703 | 4.6875e-05
87 | 0.98422 | -0.30436 | 0.00031356 | 7.8585e-05
88 | 0.98902 | -0.2103 | 0.0024898 | 0.00062401
89 | 0.98913 | -0.20804 | 0.0018283 | 0.00045821
90 | 0.98542 | -0.28071 | 0.000991 | 0.00024837
91 | 0.98423 | -0.30407 | 0.0011756 | 0.00029462
92 | 0.98423 | -0.30419 | 0.00019893 | 4.9856e-05
93 | 0.99267 | -0.13974 | 0 | 0
94 | 0.99254 | -0.14231 | 0.0033518 | 0.00084004
95 | 0.9922 | -0.14888 | 0.0033469 | 0.00083881
96 | 0.99258 | -0.14158 | 0.0023254 | 0.00058279
97 | 0.99253 | -0.14254 | 0.0031267 | 0.00078362
98 | 0.99107 | -0.17054 | 0.0028701 | 0.00071933
99 | 0.99249 | -0.14321 | 0.0056351 | 0.0014123
100 | 0.98937 | -0.20346 | 0 | 0
101 | 0.98927 | -0.20545 | 0 | 0
102 | 0.98795 | -0.23095 | 0.010916 | 0.0027359
103 | 0.98915 | -0.20771 | 0.016584 | 0.0041563
104 | 0.98665 | -0.25605 | 0 | 0
105 | 0.98584 | -0.2719 | 0 | 0
106 | 0.98517 | -0.285 | 0 | 0
107 | 0.98569 | -0.27486 | 0.017176 | 0.0043047
108 | 0.98437 | -0.30047 | 0.016804 | 0.0042115
109 | 0.98479 | -0.29233 | 0.002677 | 0.00067091
110 | 0.98512 | -0.28595 | 0 | 0
111 | 0.98379 | -0.31182 | 0 | 0
112 | 0.98459 | -0.29624 | 0.0025633 | 0.00064243
113 | 0.98484 | -0.29128 | 0.0025052 | 0.00062786
114 | 0.98389 | -0.30986 | 0.008774 | 0.002199
115 | 0.98406 | -0.30651 | 0.0026088 | 0.00065382
116 | 0.98381 | -0.31155 | 0.0018358 | 0.00046011
117 | 0.98423 | -0.30329 | 0.0026764 | 0.00067077
118 | 0.98373 | -0.31313 | 0.00179 | 0.00044863
119 | 0.98359 | -0.31588 | 0.0058956 | 0.0014776
120 | 0.98358 | -0.31605 | 0.0058508 | 0.0014663
121 | 0.98473 | -0.29351 | 0 | 0
122 | 0.98465 | -0.29503 | 0 | 0
123 | 0.98456 | -0.29685 | 0.0045612 | 0.0011432
124 | 0.98459 | -0.29632 | 0 | 0
125 | 0.98449 | -0.29816 | 0 | 0
126 | 0.98458 | -0.29655 | 0.0021151 | 0.00053009
127 | 0.98444 | -0.29919 | 0.0040694 | 0.0010199
128 | 0.99956 | -0.0085079 | 0.0076166 | 0.0019089
129 | 0.99954 | -0.0087806 | 0.0038772 | 0.00097172
130 | 0.99946 | -0.010387 | 0.003327 | 0.00083381
131 | 0.98279 | -0.33088 | 0.0045534 | 0.0011412
132 | 0.98286 | -0.32964 | 0.0044271 | 0.0011095
133 | 0.983 | -0.3269 | 0.0051912 | 0.001301
134 | 0.98323 | -0.32225 | 0.0045633 | 0.0011437
135 | 0.98358 | -0.31547 | 0.0077344 | 0.0019384
136 | 0.98284 | -0.33041 | 0.014059 | 0.0035235
137 | 0.98304 | -0.32656 | 0.0049824 | 0.0012487
138 | 0.98387 | -0.30974 | 0.0073432 | 0.0018404
139 | 0.98462 | -0.29522 | 0.0058141 | 0.0014572
140 | 0.98056 | -0.37389 | 0.0031149 | 0.00078068
141 | 0.97969 | -0.39081 | 0.0039541 | 0.000991
142 | 0.97882 | -0.40781 | 0.0063195 | 0.0015838
143 | 0.97362 | -0.50999 | 0.003061 | 0.00076716
144 | 0.98541 | -0.28086 | 0.0019989 | 0.00050097
145 | 0.98334 | -0.32059 | 0.0049827 | 0.0012488
146 | 0.98456 | -0.29676 | 0.0021151 | 0.00053009
147 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0043617 | -0.0010931 | 0.0043618 | 0.0010931 | 8.8563e-08 | -1.3758e-08 | 0.0065609 | 0.0065609 | 0.0065609 | 0.98923 | -0.20637 | 0.98925 | -0.20595 | 1.8025
1 | -0.0065497 | -0.0016415 | 0.00655 | 0.0016416 | 3.7449e-07 | 1.0757e-07 | 0.0098519 | 0.0098518 | 0.0098519 | 0.98925 | -0.20595 | 0.98932 | -0.20475 | 2.7066
2 | -0.036103 | -0.0090573 | 0.036134 | 0.0090766 | 3.0715e-05 | 1.9301e-05 | 0.054306 | 0.054305 | 0.054306 | 0.98932 | -0.20475 | 0.99023 | -0.18692 | 14.9191
3 | 0.029553 | 0.0074157 | -0.029543 | -0.0074093 | 1.0375e-05 | 6.4601e-06 | 0.044454 | 0.044454 | 0.044454 | 0.98932 | -0.20475 | 0.98894 | -0.21211 | 12.2126
4 | 0.18386 | 0.046683 | -0.18375 | -0.046608 | 0.00011787 | 7.457e-05 | 0.27502 | 0.27502 | 0.27502 | 0.99557 | -0.084141 | 0.99488 | -0.097473 | 18.8889
5 | 0.28151 | 0.071578 | -0.28122 | -0.07139 | 0.00029448 | 0.00018755 | 0.42112 | 0.42112 | 0.42112 | 0.99557 | -0.084141 | 0.99444 | -0.10588 | 28.9232
6 | -0.46538 | -0.11826 | 0.4664 | 0.11891 | 0.0010179 | 0.00065031 | 0.69614 | 0.69614 | 0.69614 | 0.99557 | -0.084141 | 0.99795 | -0.038822 | 47.8121
7 | 0.1816 | 0.04607 | -0.18146 | -0.045982 | 0.00014018 | 8.8663e-05 | 0.27181 | 0.27181 | 0.27181 | 0.99488 | -0.097473 | 0.99404 | -0.11354 | 18.6685
8 | 0.27936 | 0.070924 | -0.27901 | -0.070701 | 0.00035017 | 0.00022301 | 0.41834 | 0.41834 | 0.41834 | 0.99444 | -0.10588 | 0.99308 | -0.13197 | 28.732
9 | -0.46855 | -0.11945 | 0.46862 | 0.11949 | 6.923e-05 | 4.4228e-05 | 0.69935 | 0.69935 | 0.69935 | 0.99795 | -0.038822 | 0.99811 | -0.035762 | 48.0323
10 | 0.001189 | 0.00029783 | -0.001189 | -0.00029799 | 1.5033e-08 | -1.5193e-07 | 0.0017866 | 0.0017867 | 0.0017867 | 0.99023 | -0.18692 | 0.99022 | -0.18718 | 0.49085
11 | -0.037323 | -0.0093745 | 0.037328 | 0.0093775 | 4.874e-06 | 3.0662e-06 | 0.056092 | 0.056092 | 0.056092 | 0.99023 | -0.18692 | 0.99038 | -0.18418 | 15.4099
12 | 0.027054 | 0.0067855 | -0.027054 | -0.0067854 | 1.9168e-07 | 1.1872e-07 | 0.040709 | 0.040709 | 0.040709 | 0.98894 | -0.21211 | 0.98893 | -0.21226 | 11.1837
13 | 0.17932 | 0.045445 | -0.17925 | -0.0454 | 7.2164e-05 | 4.5632e-05 | 0.26861 | 0.26861 | 0.26861 | 0.99404 | -0.11354 | 0.9936 | -0.12192 | 18.4485
14 | 0.21697 | 0.055075 | -0.21676 | -0.054941 | 0.0002106 | 0.00013369 | 0.32535 | 0.32535 | 0.32535 | 0.99308 | -0.13197 | 0.99202 | -0.15217 | 22.3457
15 | 0.062038 | 0.015626 | -0.061983 | -0.015591 | 5.5769e-05 | 3.547e-05 | 0.092985 | 0.092985 | 0.092985 | 0.99308 | -0.13197 | 0.9921 | -0.15079 | 25.5454
16 | -0.46862 | -0.11949 | 0.46943 | 0.12001 | 0.00081063 | 0.00051788 | 0.69935 | 0.69935 | 0.69935 | 0.99811 | -0.035762 | 1 | 0 | 48.0323
17 | 0.015207 | 0.0038118 | -0.015206 | -0.003811 | 1.2786e-06 | 7.343e-07 | 0.022849 | 0.022849 | 0.022849 | 0.99038 | -0.18418 | 0.99028 | -0.18595 | 6.2772
18 | -0.052535 | -0.013189 | 0.052576 | 0.013215 | 4.0326e-05 | 2.5587e-05 | 0.078941 | 0.078941 | 0.078941 | 0.99038 | -0.18418 | 0.99121 | -0.1681 | 21.6871
19 | 0.025502 | 0.0063966 | -0.025496 | -0.0063926 | 6.4323e-06 | 3.9672e-06 | 0.038375 | 0.038375 | 0.038375 | 0.98893 | -0.21226 | 0.98866 | -0.21755 | 10.5425
20 | 0.17559 | 0.044483 | -0.17544 | -0.044388 | 0.00015016 | 9.4904e-05 | 0.26313 | 0.26313 | 0.26313 | 0.9936 | -0.12192 | 0.99267 | -0.13974 | 18.0722
21 | 0.017503 | 0.0043881 | -0.017498 | -0.0043855 | 4.3533e-06 | 2.5687e-06 | 0.026254 | 0.026254 | 0.026254 | 0.99202 | -0.15217 | 0.99175 | -0.15739 | 7.2127
22 | 0.19926 | 0.050553 | -0.19916 | -0.050494 | 9.3728e-05 | 5.9409e-05 | 0.2991 | 0.2991 | 0.2991 | 0.99202 | -0.15217 | 0.99151 | -0.16195 | 20.5425
23 | 0.056782 | 0.014287 | -0.056735 | -0.014257 | 4.6945e-05 | 2.9822e-05 | 0.085185 | 0.085186 | 0.085186 | 0.9921 | -0.15079 | 0.99121 | -0.1681 | 23.4026
24 | 0.014827 | 0.0037177 | -0.014821 | -0.0037143 | 6.0092e-06 | 3.4142e-06 | 0.022064 | 0.022064 | 0.022064 | 1 | 0 | 0.99956 | -0.0085079 | 6.0615
25 | 0.0071399 | 0.0017895 | -0.0071395 | -0.0017893 | 4.1027e-07 | 1.3957e-07 | 0.010713 | 0.010713 | 0.010713 | 0.99175 | -0.15739 | 0.99169 | -0.15859 | 2.943
26 | 0.19225 | 0.048762 | -0.19223 | -0.048748 | 2.1966e-05 | 1.3913e-05 | 0.28873 | 0.28873 | 0.28873 | 0.99151 | -0.16195 | 0.99139 | -0.16433 | 19.8302
27 | -0.010428 | -0.0026137 | 0.010429 | 0.0026144 | 1.297e-06 | 6.492e-07 | 0.015678 | 0.015678 | 0.015678 | 0.98972 | -0.19657 | 0.98985 | -0.19396 | 4.3071
28 | 0.010428 | 0.0026137 | -0.010426 | -0.0026129 | 1.592e-06 | 7.9694e-07 | 0.015678 | 0.015678 | 0.015678 | 0.98972 | -0.19657 | 0.98955 | -0.19977 | 4.3071
29 | -0.010429 | -0.0026144 | 0.010431 | 0.0026154 | 1.973e-06 | 9.8751e-07 | 0.015678 | 0.015678 | 0.015678 | 0.98985 | -0.19396 | 0.99006 | -0.18999 | 4.3071
30 | 0.0052288 | 0.0013104 | -0.0052284 | -0.0013104 | 4.0006e-07 | 3.437e-08 | 0.0078626 | 0.0078627 | 0.0078627 | 0.98955 | -0.19977 | 0.98947 | -0.20138 | 2.1601
31 | 0.18575 | 0.047124 | -0.18562 | -0.047039 | 0.00013459 | 8.5188e-05 | 0.279 | 0.279 | 0.279 | 0.99139 | -0.16433 | 0.99061 | -0.17941 | 19.1624
32 | -0.17288 | -0.043813 | 0.17288 | 0.043814 | 1.6938e-06 | 1.0703e-06 | 0.26001 | 0.26001 | 0.26001 | 0.99006 | -0.18999 | 0.99007 | -0.18979 | 17.8576
33 | 0.16245 | 0.041197 | -0.16232 | -0.041113 | 0.00013377 | 8.4387e-05 | 0.24433 | 0.24433 | 0.24433 | 0.99006 | -0.18999 | 0.98917 | -0.20713 | 16.7809
34 | 0.0080561 | 0.0020193 | -0.0080546 | -0.0020187 | 1.4925e-06 | 6.0976e-07 | 0.012139 | 0.01214 | 0.01214 | 0.98751 | -0.23928 | 0.98731 | -0.24317 | 3.335
35 | -0.011828 | -0.0029647 | 0.011829 | 0.002965 | 6.6361e-07 | 3.5344e-07 | 0.017823 | 0.017823 | 0.017823 | 0.98751 | -0.23928 | 0.98757 | -0.2381 | 4.8965
36 | 0.0064684 | 0.0016211 | -0.0064684 | -0.0016211 | 5.0753e-08 | 1.4271e-08 | 0.0097489 | 0.0097489 | 0.0097489 | 0.98731 | -0.24317 | 0.9873 | -0.24334 | 2.6783
37 | -0.015527 | -0.0038916 | 0.015535 | 0.0038961 | 7.9215e-06 | 4.5757e-06 | 0.023395 | 0.023395 | 0.023395 | 0.98757 | -0.2381 | 0.98812 | -0.2274 | 6.4272
38 | 0.0036979 | 0.00092656 | -0.0036978 | -0.00092664 | 1.6861e-07 | -7.7393e-08 | 0.0055718 | 0.0055718 | 0.0055718 | 0.98757 | -0.2381 | 0.98752 | -0.23906 | 1.5307
39 | 0.0021342 | 0.00053486 | -0.0021342 | -0.00053487 | 5.8715e-09 | -1.5595e-08 | 0.0032165 | 0.0032165 | 0.0032165 | 0.9873 | -0.24334 | 0.98729 | -0.24339 | 0.88366
40 | -0.019891 | -0.0049877 | 0.019895 | 0.0049904 | 4.465e-06 | 2.6876e-06 | 0.029954 | 0.029954 | 0.029954 | 0.98812 | -0.2274 | 0.98836 | -0.22269 | 8.2293
41 | 0.0043559 | 0.0010915 | -0.0043555 | -0.0010916 | 3.874e-07 | -5.9571e-08 | 0.0065596 | 0.0065597 | 0.0065597 | 0.98812 | -0.2274 | 0.98802 | -0.22927 | 1.8021
42 | 0.0020861 | 0.00052271 | -0.002086 | -0.00052281 | 3.4033e-08 | -9.5732e-08 | 0.0031433 | 0.0031433 | 0.0031433 | 0.98752 | -0.23906 | 0.9875 | -0.2394 | 0.86356
43 | 0.1355 | 0.034344 | -0.13543 | -0.0343 | 7.0048e-05 | 4.3912e-05 | 0.20414 | 0.20414 | 0.20414 | 0.98836 | -0.22269 | 0.9878 | -0.23346 | 14.0206
44 | -0.1554 | -0.039334 | 0.15551 | 0.039407 | 0.00011614 | 7.317e-05 | 0.23409 | 0.23409 | 0.23409 | 0.98836 | -0.22269 | 0.98917 | -0.20713 | 16.0779
45 | 0.12982 | 0.032894 | -0.12975 | -0.032846 | 7.665e-05 | 4.7963e-05 | 0.19569 | 0.19569 | 0.19569 | 0.9878 | -0.23346 | 0.98716 | -0.24575 | 13.4404
46 | -0.12833 | -0.032478 | 0.12837 | 0.032502 | 3.8942e-05 | 2.4356e-05 | 0.19362 | 0.19362 | 0.19362 | 0.98684 | -0.25207 | 0.98716 | -0.24575 | 13.2982
47 | 0.12833 | 0.032478 | -0.12828 | -0.032445 | 5.2818e-05 | 3.3036e-05 | 0.19362 | 0.19362 | 0.19362 | 0.98684 | -0.25207 | 0.98639 | -0.26065 | 13.2982
48 | 0.041327 | 0.010398 | -0.041291 | -0.010375 | 3.6643e-05 | 2.3131e-05 | 0.062358 | 0.062359 | 0.062359 | 0.98639 | -0.26065 | 0.98544 | -0.27923 | 17.1315
49 | 0.086953 | 0.022047 | -0.086903 | -0.022017 | 4.9883e-05 | 3.0349e-05 | 0.13126 | 0.13126 | 0.13126 | 0.98639 | -0.26065 | 0.98578 | -0.27259 | 9.0154
50 | -0.0081027 | -0.0020309 | 0.0081067 | 0.0020326 | 3.9863e-06 | 1.6513e-06 | 0.012253 | 0.012253 | 0.012253 | 0.98401 | -0.30677 | 0.98454 | -0.29645 | 3.3662
51 | 0.0081027 | 0.0020309 | -0.0081016 | -0.0020305 | 1.0682e-06 | 4.4266e-07 | 0.012253 | 0.012253 | 0.012253 | 0.98401 | -0.30677 | 0.98387 | -0.30954 | 3.3662
52 | -0.084224 | -0.02131 | 0.084244 | 0.021322 | 2.0182e-05 | 1.2241e-05 | 0.12737 | 0.12737 | 0.12737 | 0.98454 | -0.29645 | 0.9848 | -0.29146 | 8.7477
53 | 0.076117 | 0.019277 | -0.076102 | -0.019268 | 1.4799e-05 | 9.3198e-06 | 0.11511 | 0.11511 | 0.11511 | 0.98454 | -0.29645 | 0.98433 | -0.3005 | 15.8123
54 | -0.070018 | -0.017717 | 0.070051 | 0.017737 | 3.2305e-05 | 2.0578e-05 | 0.10602 | 0.10602 | 0.10602 | 0.98331 | -0.32027 | 0.98381 | -0.31066 | 29.1255
55 | 0.070018 | 0.017717 | -0.069979 | -0.017692 | 3.9473e-05 | 2.5144e-05 | 0.10602 | 0.10602 | 0.10602 | 0.98331 | -0.32027 | 0.98271 | -0.33203 | 29.1255
56 | -0.074784 | -0.018924 | 0.07482 | 0.018947 | 3.6501e-05 | 2.2974e-05 | 0.11318 | 0.11318 | 0.11318 | 0.98381 | -0.31066 | 0.98433 | -0.3005 | 15.5461
57 | 0.065915 | 0.016673 | -0.065856 | -0.016635 | 5.9717e-05 | 3.8016e-05 | 0.099864 | 0.099864 | 0.099864 | 0.98271 | -0.33203 | 0.98174 | -0.35093 | 27.4352
58 | -0.085568 | -0.021654 | 0.085595 | 0.021671 | 2.7847e-05 | 1.6918e-05 | 0.12937 | 0.12937 | 0.12937 | 0.9848 | -0.29146 | 0.98515 | -0.28468 | 8.885
59 | 0.035087 | 0.0088239 | -0.035077 | -0.0088179 | 9.5081e-06 | 5.9745e-06 | 0.053498 | 0.053498 | 0.053498 | 0.97612 | -0.46075 | 0.97583 | -0.46642 | 14.6973
60 | -0.035087 | -0.0088239 | 0.035121 | 0.0088451 | 3.3693e-05 | 2.1171e-05 | 0.053498 | 0.053498 | 0.053498 | 0.97612 | -0.46075 | 0.97714 | -0.44067 | 14.6973
61 | 0.035077 | 0.0088179 | -0.035065 | -0.0088103 | 1.2113e-05 | 7.6112e-06 | 0.053498 | 0.053498 | 0.053498 | 0.97583 | -0.46642 | 0.97546 | -0.47366 | 14.6973
62 | -0.041816 | -0.010523 | 0.041851 | 0.010545 | 3.5313e-05 | 2.2309e-05 | 0.063694 | 0.063694 | 0.063694 | 0.97714 | -0.44067 | 0.97804 | -0.42301 | 17.4982
63 | 0.035065 | 0.0088103 | -0.035048 | -0.0087994 | 1.7432e-05 | 1.0954e-05 | 0.053498 | 0.053498 | 0.053498 | 0.97546 | -0.47366 | 0.97493 | -0.48408 | 14.6973
64 | 0.026382 | 0.0066274 | -0.026364 | -0.0066162 | 1.8084e-05 | 1.1203e-05 | 0.040271 | 0.040271 | 0.040271 | 0.97493 | -0.48408 | 0.9742 | -0.49845 | 11.0636
65 | 0.086903 | 0.022017 | -0.086853 | -0.021986 | 5.0412e-05 | 3.0673e-05 | 0.13126 | 0.13126 | 0.13126 | 0.98578 | -0.27259 | 0.98515 | -0.28468 | 9.0154
66 | -0.17863 | -0.045253 | 0.17872 | 0.04531 | 8.9084e-05 | 5.6336e-05 | 0.26864 | 0.26864 | 0.26864 | 0.99007 | -0.18979 | 0.99061 | -0.17941 | 18.4506
67 | 0.039698 | 0.0099756 | -0.039668 | -0.0099565 | 3.0289e-05 | 1.9099e-05 | 0.059954 | 0.059954 | 0.059954 | 0.98544 | -0.27923 | 0.98462 | -0.29522 | 16.4709
68 | -0.0042073 | -0.0010541 | 0.0042075 | 0.0010541 | 2.1112e-07 | -4.1715e-08 | 0.0063609 | 0.0063609 | 0.0063609 | 0.9842 | -0.30389 | 0.98425 | -0.30283 | 1.7475
69 | 0.0042073 | 0.0010541 | -0.0042066 | -0.0010543 | 7.5689e-07 | -1.4937e-07 | 0.0063609 | 0.0063612 | 0.0063612 | 0.9842 | -0.30389 | 0.98401 | -0.30766 | 1.7476
70 | -0.0042075 | -0.0010541 | 0.0042083 | 0.0010539 | 7.2914e-07 | -1.4425e-07 | 0.0063609 | 0.0063607 | 0.0063609 | 0.98425 | -0.30283 | 0.98444 | -0.29919 | 1.7475
71 | 0.060956 | 0.015407 | -0.060889 | -0.015365 | 6.7045e-05 | 4.2645e-05 | 0.092438 | 0.092438 | 0.092438 | 0.98174 | -0.35093 | 0.98056 | -0.37389 | 25.395
72 | 0.0096143 | 0.0024097 | -0.0096138 | -0.0024094 | 4.9454e-07 | 2.3766e-07 | 0.014557 | 0.014557 | 0.014557 | 0.98275 | -0.33212 | 0.9827 | -0.3332 | 3.9993
73 | -0.0096143 | -0.0024097 | 0.0096156 | 0.0024103 | 1.3139e-06 | 6.3135e-07 | 0.014557 | 0.014557 | 0.014557 | 0.98275 | -0.33212 | 0.9829 | -0.32925 | 3.9993
74 | 0.01406 | 0.0035239 | -0.014059 | -0.0035235 | 7.7675e-07 | 4.3918e-07 | 0.021285 | 0.021285 | 0.021285 | 0.9829 | -0.32925 | 0.98284 | -0.33041 | 5.8475
75 | -0.023675 | -0.0059342 | 0.023678 | 0.0059361 | 3.0376e-06 | 1.8641e-06 | 0.035842 | 0.035842 | 0.035842 | 0.9829 | -0.32925 | 0.98304 | -0.32656 | 9.8468
76 | -0.047376 | -0.01193 | 0.04741 | 0.011952 | 3.4469e-05 | 2.1838e-05 | 0.072098 | 0.072098 | 0.072098 | 0.97804 | -0.42301 | 0.97882 | -0.40781 | 19.8073
77 | 0.022355 | 0.0056115 | -0.022342 | -0.005604 | 1.229e-05 | 7.5161e-06 | 0.034148 | 0.034148 | 0.034148 | 0.9742 | -0.49845 | 0.97362 | -0.50999 | 9.3814
78 | -0.019269 | -0.0048292 | 0.019278 | 0.0048345 | 8.8449e-06 | 5.3233e-06 | 0.02947 | 0.02947 | 0.02947 | 0.97292 | -0.52375 | 0.97341 | -0.51412 | 8.0962
79 | -0.019278 | -0.0048345 | 0.019281 | 0.0048368 | 3.8004e-06 | 2.2872e-06 | 0.02947 | 0.02947 | 0.02947 | 0.97341 | -0.51412 | 0.97362 | -0.50999 | 8.0962
80 | 0.0063801 | 0.001599 | -0.0063794 | -0.0015988 | 6.6253e-07 | 1.7835e-07 | 0.0096026 | 0.0096026 | 0.0096026 | 0.98866 | -0.21755 | 0.98854 | -0.21973 | 2.6381
81 | 0.019116 | 0.0047936 | -0.019098 | -0.0047831 | 1.7528e-05 | 1.0495e-05 | 0.028772 | 0.028772 | 0.028772 | 0.98866 | -0.21755 | 0.98767 | -0.23681 | 7.9045
82 | 0.013496 | 0.0033793 | -0.013471 | -0.0033649 | 2.5761e-05 | 1.4365e-05 | 0.020332 | 0.020333 | 0.020333 | 0.98767 | -0.23681 | 0.98561 | -0.27698 | 5.586
83 | 0.0056021 | 0.0014038 | -0.0056002 | -0.0014036 | 1.8175e-06 | 2.928e-07 | 0.00844 | 0.0084403 | 0.0084403 | 0.98767 | -0.23681 | 0.98732 | -0.24362 | 2.3188
84 | 0.0025592 | 0.00063047 | -0.0025576 | -0.00063308 | 1.5904e-06 | -2.6064e-06 | 0.0038598 | 0.0038611 | 0.0038611 | 0.98561 | -0.27698 | 0.98494 | -0.29018 | 1.0607
85 | 0.0054509 | 0.001366 | -0.0054499 | -0.0013658 | 9.6897e-07 | 1.3399e-07 | 0.0082294 | 0.0082296 | 0.0082296 | 0.98561 | -0.27698 | 0.98542 | -0.28071 | 2.2609
86 | 0.0054605 | 0.0013685 | -0.0054601 | -0.0013684 | 3.6875e-07 | 5.1618e-08 | 0.0082439 | 0.008244 | 0.008244 | 0.98561 | -0.27698 | 0.98554 | -0.2784 | 2.2648
87 | 0.0054601 | 0.0013684 | -0.0054601 | -0.0013684 | 2.5201e-08 | 3.5288e-09 | 0.008244 | 0.008244 | 0.008244 | 0.98554 | -0.2784 | 0.98553 | -0.2785 | 2.2648
88 | 0.0025576 | 0.00063308 | -0.0025561 | -0.00063549 | 1.4745e-06 | -2.41e-06 | 0.0038611 | 0.0038623 | 0.0038623 | 0.98494 | -0.29018 | 0.98432 | -0.30238 | 1.0611
89 | 0.0029899 | 0.00074929 | -0.0029899 | -0.00074929 | 8.4103e-12 | 5.3826e-12 | 0.0045148 | 0.0045148 | 0.0045148 | 0.98542 | -0.28071 | 0.98542 | -0.28071 | 1.2403
90 | 0.0018752 | 0.00046485 | -0.0018751 | -0.00046539 | 1.4981e-07 | -5.3672e-07 | 0.002833 | 0.0028332 | 0.0028332 | 0.98432 | -0.30238 | 0.98423 | -0.30407 | 0.77836
91 | -0.00018703 | -4.6045e-05 | 0.00018704 | 4.3271e-05 | 6.5198e-09 | -2.7739e-06 | 0.00028249 | 0.00028155 | 0.00028249 | 0.98417 | -0.30528 | 0.98421 | -0.30453 | 0.077608
92 | 0.00018703 | 4.6045e-05 | -0.00018703 | -4.6875e-05 | 1.9599e-09 | -8.3008e-07 | 0.00028249 | 0.00028279 | 0.00028279 | 0.98417 | -0.30528 | 0.98416 | -0.3055 | 0.077689
93 | -0.00018704 | -4.3271e-05 | 0.00018704 | 4.2678e-05 | 1.3887e-09 | -5.9321e-07 | 0.00028155 | 0.00028135 | 0.00028155 | 0.98421 | -0.30453 | 0.98422 | -0.30436 | 0.077348
94 | -0.0005006 | -0.00012126 | 0.0005006 | 0.00012104 | 3.839e-09 | -2.2558e-07 | 0.00075537 | 0.00075529 | 0.00075537 | 0.98422 | -0.30436 | 0.98423 | -0.30419 | 0.20752
95 | -0.0024898 | -0.00062401 | 0.0024901 | 0.00062353 | 2.6803e-07 | -4.822e-07 | 0.003746 | 0.0037458 | 0.003746 | 0.98902 | -0.2103 | 0.98913 | -0.20804 | 1.0291
96 | -0.0043184 | -0.0010817 | 0.0043189 | 0.0010816 | 5.337e-07 | -9.1378e-08 | 0.0064962 | 0.0064961 | 0.0064962 | 0.98913 | -0.20804 | 0.98927 | -0.20545 | 1.7847
97 | 0.0019989 | 0.00050092 | -0.0019989 | -0.00050097 | 1.4064e-08 | -4.3439e-08 | 0.0030184 | 0.0030184 | 0.0030184 | 0.98542 | -0.28071 | 0.98541 | -0.28086 | 0.82923
98 | 0.00069954 | 0.00017077 | -0.00069953 | -0.00017089 | 4.212e-09 | -1.2531e-07 | 0.001056 | 0.001056 | 0.001056 | 0.98423 | -0.30407 | 0.98423 | -0.30419 | 0.29012
99 | 0.0064793 | 0.0016238 | -0.0064785 | -0.0016236 | 7.9279e-07 | 2.177e-07 | 0.0097125 | 0.0097126 | 0.0097126 | 0.99267 | -0.13974 | 0.99254 | -0.14231 | 2.6683
100 | 0.161 | 0.040768 | -0.16093 | -0.040724 | 7.065e-05 | 4.4548e-05 | 0.24148 | 0.24148 | 0.24148 | 0.99267 | -0.13974 | 0.9922 | -0.14888 | 16.5855
101 | 0.0079616 | 0.0019954 | -0.0079609 | -0.0019952 | 6.9794e-07 | 2.7777e-07 | 0.011935 | 0.011935 | 0.011935 | 0.99267 | -0.13974 | 0.99258 | -0.14158 | 3.2787
102 | 0.0031267 | 0.00078359 | -0.0031267 | -0.00078362 | 3.437e-08 | -3.1912e-08 | 0.0046876 | 0.0046876 | 0.0046876 | 0.99254 | -0.14231 | 0.99253 | -0.14254 | 1.2878
103 | 0.15758 | 0.039885 | -0.15742 | -0.039782 | 0.00016364 | 0.00010312 | 0.23647 | 0.23647 | 0.23647 | 0.9922 | -0.14888 | 0.99107 | -0.17054 | 16.2408
104 | 0.0056356 | 0.0014124 | -0.0056351 | -0.0014123 | 4.3904e-07 | 6.8997e-08 | 0.0084485 | 0.0084486 | 0.0084486 | 0.99258 | -0.14158 | 0.99249 | -0.14321 | 2.321
105 | 0.15455 | 0.039063 | -0.1543 | -0.038907 | 0.00024358 | 0.00015527 | 0.23216 | 0.23216 | 0.23216 | 0.99107 | -0.17054 | 0.98937 | -0.20346 | 31.8897
106 | 0.020906 | 0.0052402 | -0.020904 | -0.005239 | 1.9747e-06 | 1.1954e-06 | 0.031444 | 0.031444 | 0.031444 | 0.98937 | -0.20346 | 0.98927 | -0.20545 | 8.6384
107 | 0.1334 | 0.033667 | -0.13322 | -0.033555 | 0.00017539 | 0.0001121 | 0.20071 | 0.20071 | 0.20071 | 0.98937 | -0.20346 | 0.98795 | -0.23095 | 55.1411
108 | 0.016586 | 0.0041573 | -0.016584 | -0.0041563 | 1.7862e-06 | 1.0449e-06 | 0.024948 | 0.024948 | 0.024948 | 0.98927 | -0.20545 | 0.98915 | -0.20771 | 6.8538
109 | 0.12231 | 0.030819 | -0.12216 | -0.030726 | 0.00014665 | 9.3711e-05 | 0.18427 | 0.18427 | 0.18427 | 0.98795 | -0.23095 | 0.98665 | -0.25605 | 50.6241
110 | 0.067787 | 0.017053 | -0.067735 | -0.01702 | 5.1295e-05 | 3.2662e-05 | 0.10225 | 0.10225 | 0.10225 | 0.98665 | -0.25605 | 0.98584 | -0.2719 | 28.0919
111 | 0.054372 | 0.013673 | -0.054297 | -0.013625 | 7.5061e-05 | 4.766e-05 | 0.082017 | 0.082017 | 0.082017 | 0.98665 | -0.25605 | 0.98517 | -0.285 | 22.5322
112 | 0.017178 | 0.0043061 | -0.017176 | -0.0043047 | 2.4181e-06 | 1.4253e-06 | 0.025929 | 0.025929 | 0.025929 | 0.98584 | -0.2719 | 0.98569 | -0.27486 | 7.1234
113 | 0.050557 | 0.012714 | -0.050488 | -0.01267 | 6.8887e-05 | 4.3686e-05 | 0.076325 | 0.076326 | 0.076326 | 0.98584 | -0.2719 | 0.98437 | -0.30047 | 20.9686
114 | 0.034711 | 0.0087141 | -0.034699 | -0.0087065 | 1.2123e-05 | 7.609e-06 | 0.052434 | 0.052434 | 0.052434 | 0.98517 | -0.285 | 0.98479 | -0.29233 | 14.405
115 | 0.019586 | 0.0049109 | -0.019585 | -0.0049103 | 8.8479e-07 | 5.3194e-07 | 0.029583 | 0.029583 | 0.029583 | 0.98517 | -0.285 | 0.98512 | -0.28595 | 8.1273
116 | 0.033684 | 0.0084589 | -0.033666 | -0.0084475 | 1.8221e-05 | 1.1423e-05 | 0.050924 | 0.050924 | 0.050924 | 0.98437 | -0.30047 | 0.98379 | -0.31182 | 13.9901
117 | 0.032022 | 0.0080356 | -0.032016 | -0.0080318 | 5.976e-06 | 3.7381e-06 | 0.048389 | 0.048389 | 0.048389 | 0.98479 | -0.29233 | 0.98459 | -0.29624 | 13.2938
118 | 0.019585 | 0.0049103 | -0.01958 | -0.0049074 | 4.978e-06 | 2.9928e-06 | 0.029583 | 0.029583 | 0.029583 | 0.98512 | -0.28595 | 0.98484 | -0.29128 | 8.1273
119 | 0.033666 | 0.0084475 | -0.033652 | -0.0084387 | 1.4077e-05 | 8.8254e-06 | 0.050924 | 0.050924 | 0.050924 | 0.98379 | -0.31182 | 0.98334 | -0.32059 | 13.9901
120 | 0.029453 | 0.0073894 | -0.029443 | -0.0073832 | 9.8975e-06 | 6.1651e-06 | 0.044515 | 0.044515 | 0.044515 | 0.98459 | -0.29624 | 0.98423 | -0.30329 | 12.2295
121 | 0.017074 | 0.0042795 | -0.017073 | -0.0042784 | 1.8123e-06 | 1.0675e-06 | 0.025798 | 0.025798 | 0.025798 | 0.98484 | -0.29128 | 0.98473 | -0.29351 | 7.0874
122 | -0.02415 | -0.0060537 | 0.024154 | 0.0060561 | 3.8533e-06 | 2.3683e-06 | 0.036524 | 0.036524 | 0.036524 | 0.98389 | -0.30986 | 0.98406 | -0.30651 | 10.0342
123 | 0.015376 | 0.0038548 | -0.015375 | -0.0038541 | 1.2356e-06 | 7.1339e-07 | 0.023255 | 0.023255 | 0.023255 | 0.98389 | -0.30986 | 0.98381 | -0.31155 | 6.3887
124 | -0.026763 | -0.0067099 | 0.026767 | 0.0067125 | 4.1113e-06 | 2.5462e-06 | 0.040469 | 0.040469 | 0.040469 | 0.98406 | -0.30651 | 0.98423 | -0.30329 | 11.1179
125 | 0.013539 | 0.003394 | -0.013538 | -0.0033934 | 1.0205e-06 | 5.7072e-07 | 0.020478 | 0.020478 | 0.020478 | 0.98381 | -0.31155 | 0.98373 | -0.31313 | 5.6259
126 | 0.011748 | 0.0029448 | -0.011746 | -0.0029439 | 1.5374e-06 | 8.1912e-07 | 0.017771 | 0.017771 | 0.017771 | 0.98373 | -0.31313 | 0.98359 | -0.31588 | 4.882
127 | 0.0058508 | 0.0014664 | -0.0058508 | -0.0014663 | 4.7072e-08 | 9.7915e-09 | 0.0088514 | 0.0088515 | 0.0088515 | 0.98359 | -0.31588 | 0.98358 | -0.31605 | 2.4317
128 | 0.017073 | 0.0042784 | -0.017071 | -0.0042777 | 1.2382e-06 | 7.2932e-07 | 0.025798 | 0.025798 | 0.025798 | 0.98473 | -0.29351 | 0.98465 | -0.29503 | 7.0874
129 | 0.0045616 | 0.0011431 | -0.0045612 | -0.0011432 | 3.9386e-07 | -2.9027e-08 | 0.0068935 | 0.0068936 | 0.0068936 | 0.98465 | -0.29503 | 0.98456 | -0.29685 | 1.8939
130 | 0.0042305 | 0.0010601 | -0.0042302 | -0.0010601 | 2.5918e-07 | -4.9203e-08 | 0.006393 | 0.0063931 | 0.0063931 | 0.98465 | -0.29503 | 0.98459 | -0.29632 | 1.7564
131 | 0.0082793 | 0.0020745 | -0.0082781 | -0.002074 | 1.2334e-06 | 5.2215e-07 | 0.012512 | 0.012512 | 0.012512 | 0.98465 | -0.29503 | 0.98449 | -0.29816 | 3.4373
132 | 0.0042302 | 0.0010601 | -0.0042302 | -0.0010601 | 4.6324e-08 | -8.7906e-09 | 0.0063931 | 0.0063931 | 0.0063931 | 0.98459 | -0.29632 | 0.98458 | -0.29655 | 1.7564
133 | 0.0082781 | 0.002074 | -0.0082777 | -0.0020738 | 4.0704e-07 | 1.7235e-07 | 0.012512 | 0.012512 | 0.012512 | 0.98449 | -0.29816 | 0.98444 | -0.29919 | 3.4373
134 | 0.0021151 | 0.00053003 | -0.0021151 | -0.00053009 | 2.1163e-08 | -5.6694e-08 | 0.0031966 | 0.0031966 | 0.0031966 | 0.98458 | -0.29655 | 0.98456 | -0.29676 | 0.87819
135 | 0.0072045 | 0.0018054 | -0.0072044 | -0.0018053 | 9.3587e-08 | 3.1457e-08 | 0.010725 | 0.010725 | 0.010725 | 0.99956 | -0.0085079 | 0.99954 | -0.0087806 | 2.9465
136 | 0.0033272 | 0.00083361 | -0.003327 | -0.00083381 | 2.5466e-07 | -1.9979e-07 | 0.0049531 | 0.0049532 | 0.0049532 | 0.99954 | -0.0087806 | 0.99946 | -0.010387 | 1.3608
137 | -0.0045534 | -0.0011412 | 0.0045537 | 0.0011412 | 2.7028e-07 | -1.9189e-08 | 0.0068942 | 0.0068941 | 0.0068942 | 0.98279 | -0.33088 | 0.98286 | -0.32964 | 1.894
138 | -0.0089808 | -0.0022507 | 0.008982 | 0.0022513 | 1.1694e-06 | 5.3459e-07 | 0.013597 | 0.013597 | 0.013597 | 0.98286 | -0.32964 | 0.983 | -0.3269 | 3.7354
139 | -0.014173 | -0.0035523 | 0.014176 | 0.0035541 | 3.1438e-06 | 1.7811e-06 | 0.021455 | 0.021455 | 0.021455 | 0.983 | -0.3269 | 0.98323 | -0.32225 | 5.8942
140 | -0.01874 | -0.0046978 | 0.018746 | 0.0047014 | 6.0522e-06 | 3.6188e-06 | 0.028361 | 0.028361 | 0.028361 | 0.98323 | -0.32225 | 0.98358 | -0.31547 | 7.7914
141 | -0.02648 | -0.0066398 | 0.026487 | 0.0066443 | 7.2356e-06 | 4.4781e-06 | 0.040062 | 0.040062 | 0.040062 | 0.98358 | -0.31547 | 0.98387 | -0.30974 | 11.006
142 | -0.028661 | -0.0071848 | 0.028669 | 0.0071899 | 8.1502e-06 | 5.0697e-06 | 0.043384 | 0.043384 | 0.043384 | 0.98304 | -0.32656 | 0.98334 | -0.32059 | 11.9187
143 | -0.033831 | -0.0084847 | 0.033854 | 0.0084993 | 2.3429e-05 | 1.4691e-05 | 0.051168 | 0.051168 | 0.051168 | 0.98387 | -0.30974 | 0.98462 | -0.29522 | 14.057
144 | 0.057774 | 0.014584 | -0.057727 | -0.014554 | 4.6781e-05 | 2.9735e-05 | 0.087711 | 0.087711 | 0.087711 | 0.98056 | -0.37389 | 0.97969 | -0.39081 | 24.0964
145 | 0.053773 | 0.013563 | -0.05373 | -0.013536 | 4.3712e-05 | 2.7756e-05 | 0.081705 | 0.081705 | 0.081705 | 0.97969 | -0.39081 | 0.97882 | -0.40781 | 22.4465

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.49617 | 0.1263

## res_load
| p_mw | q_mvar
0 | 0.0043617 | 0.0010931
1 | 0.0021879 | 0.00054833
2 | 0.0021461 | 0.00053787
3 | 0.0018612 | 0.00046646
4 | 0.0021505 | 0.00053898
5 | 0.002489 | 0.00062381
6 | 0.0021398 | 0.00053627
7 | 0.001189 | 0.00029799
8 | 0.0015512 | 0.00038876
9 | 0.0036588 | 0.00091699
10 | 0.0052003 | 0.0013033
11 | 0.010269 | 0.0025737
12 | 0.0041597 | 0.0010425
13 | 0.015206 | 0.003811
14 | 0.010358 | 0.0025961
15 | 0.0069104 | 0.0017319
16 | 0.0051972 | 0.0013026
17 | 0.0071395 | 0.0017893
18 | 0.0064786 | 0.0016237
19 | 0.0052284 | 0.0013104
20 | 0.0037721 | 0.00094538
21 | 0.0015862 | 0.00039754
22 | 0.0043342 | 0.0010863
23 | 0.0016117 | 0.00040393
24 | 0.0021342 | 0.00053487
25 | 0.0043555 | 0.0010916
26 | 0.002086 | 0.00052281
27 | 0.0056088 | 0.0014057
28 | 0.0068045 | 0.0017054
29 | 0.0013737 | 0.00034428
30 | 0.0081016 | 0.0020305
31 | 0.0047331 | 0.0011862
32 | 0.0040634 | 0.0010184
33 | 0.0013235 | 0.00033171
34 | 0.0012821 | 0.00032132
35 | 0.0066953 | 0.001678
36 | 0.0086662 | 0.002172
37 | 0.0012575 | 0.00031515
38 | 0.0057447 | 0.0014398
39 | 0.0015923 | 0.00039907
40 | 0.0042066 | 0.0010543
41 | 0.0048996 | 0.001228
42 | 0.0096138 | 0.0024094
43 | 0.0055244 | 0.0013846
44 | 0.0040088 | 0.0010047
45 | 0.019269 | 0.0048292
46 | 0.0068994 | 0.0017291
47 | 0.0063794 | 0.0015988
48 | 0.0056002 | 0.0014036
49 | 0.0054601 | 0.0013684
50 | 0.00246 | 0.00061654
51 | 0.00068085 | 0.00017064
52 | 0.00018703 | 4.6875e-05
53 | 0.00031356 | 7.8585e-05
54 | 0.0024898 | 0.00062401
55 | 0.0018283 | 0.00045821
56 | 0.000991 | 0.00024837
57 | 0.0011756 | 0.00029462
58 | 0.00019893 | 4.9856e-05
59 | 0.0033518 | 0.00084004
60 | 0.0033469 | 0.00083881
61 | 0.0023254 | 0.00058279
62 | 0.0031267 | 0.00078362
63 | 0.0028701 | 0.00071933
64 | 0.0056351 | 0.0014123
65 | 0.010916 | 0.0027359
66 | 0.016584 | 0.0041563
67 | 0.017176 | 0.0043047
68 | 0.016804 | 0.0042115
69 | 0.002677 | 0.00067091
70 | 0.0025633 | 0.00064243
71 | 0.0025052 | 0.00062786
72 | 0.008774 | 0.002199
73 | 0.0026088 | 0.00065382
74 | 0.0018358 | 0.00046011
75 | 0.0026764 | 0.00067077
76 | 0.00179 | 0.00044863
77 | 0.0058956 | 0.0014776
78 | 0.0058508 | 0.0014663
79 | 0.0045612 | 0.0011432
80 | 0.0021151 | 0.00053009
81 | 0.0040694 | 0.0010199
82 | 0.0076166 | 0.0019089
83 | 0.0038772 | 0.00097172
84 | 0.003327 | 0.00083381
85 | 0.0045534 | 0.0011412
86 | 0.0044271 | 0.0011095
87 | 0.0051912 | 0.001301
88 | 0.0045633 | 0.0011437
89 | 0.0077344 | 0.0019384
90 | 0.014059 | 0.0035235
91 | 0.0049824 | 0.0012487
92 | 0.0073432 | 0.0018404
93 | 0.0058141 | 0.0014572
94 | 0.0031149 | 0.00078068
95 | 0.0039541 | 0.000991
96 | 0.0063195 | 0.0015838
97 | 0.003061 | 0.00076716
98 | 0.0019989 | 0.00050097
99 | 0.0049827 | 0.0012488
100 | 0.0021151 | 0.00053009

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1