## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-454_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-454_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-454_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-454_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-454_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-454_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-454_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_261-454_0_4_node_15 | 0.4 | n |  | TRUE
8 | bus_LV_261-454_0_4_node_18 | 0.4 | n |  | TRUE
9 | bus_LV_261-454_0_4_node_16 | 0.4 | n |  | TRUE
10 | bus_LV_261-454_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_261-454_0_4_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_261-454_0_4_node_26 | 0.4 | n |  | TRUE
13 | bus_LV_261-454_0_4_node_21 | 0.4 | n |  | TRUE
14 | bus_LV_261-454_0_4_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_261-454_0_4_node_20 | 0.4 | n |  | TRUE
16 | bus_LV_261-454_0_4_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_261-454_0_4_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_261-454_0_4_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_261-454_0_4_node_30 | 0.4 | n |  | TRUE
20 | bus_LV_261-454_0_4_node_31 | 0.4 | n |  | TRUE
21 | bus_LV_261-454_0_4_node_29 | 0.4 | n |  | TRUE
22 | bus_LV_261-454_0_4_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_261-454_0_4_node_25 | 0.4 | n |  | TRUE
24 | bus_LV_261-454_0_4_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_261-454_0_4_node_28 | 0.4 | n |  | TRUE
26 | bus_LV_261-454_0_4_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_261-454_0_4_node_24 | 0.4 | n |  | TRUE
28 | bus_MV_494_0_node_136 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-454_0_4_load_0 | 0 | 0.032989 | 0.0082679 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-454_0_4_load_3 | 3 | 0.043286 | 0.010848 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-454_0_4_load_4 | 4 | 0.031565 | 0.007911 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-454_0_4_load_16 | 9 | 0.014948 | 0.0037462 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-454_0_4_load_26 | 12 | 0.005245 | 0.0013145 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-454_0_4_load_30 | 19 | 0.00032493 | 8.1435e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-454_0_4_load_31 | 20 | 0.070517 | 0.017673 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-454_0_4_load_29 | 21 | 0.00056183 | 0.00014081 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-454_0_4_load_25 | 23 | 0.0007213 | 0.00018077 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-454_0_4_load_22 | 24 | 0.00084356 | 0.00021142 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-454_0_4_load_28 | 25 | 0.027101 | 0.006792 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-454_0_4_load_23 | 26 | 0.00090575 | 0.000227 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-454_0_4_load_24 | 27 | 0.0075468 | 0.0018914 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 7 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-454_0_4_line_0 |  | 0 | 1 | 0.018996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-454_0_4_line_1 |  | 0 | 2 | 0.015731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-454_0_4_line_2 |  | 1 | 3 | 0.020619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-454_0_4_line_3 |  | 1 | 4 | 0.0084395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-454_0_4_line_4 |  | 2 | 5 | 0.063476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-454_0_4_line_5 |  | 3 | 6 | 0.0025763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-454_0_4_line_6 |  | 4 | 7 | 0.029572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_261-454_0_4_line_7 |  | 5 | 8 | 0.044677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-454_0_4_line_8 |  | 5 | 9 | 0.020233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-454_0_4_line_9 |  | 6 | 13 | 0.017705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-454_0_4_line_10 |  | 7 | 22 | 0.11767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_261-454_0_4_line_11 |  | 8 | 23 | 0.018207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-454_0_4_line_12 |  | 8 | 24 | 0.018418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-454_0_4_line_13 |  | 10 | 11 | 0.24119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_261-454_0_4_line_14 |  | 10 | 12 | 0.12148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_261-454_0_4_line_15 |  | 11 | 20 | 0.076405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-454_0_4_line_16 |  | 12 | 22 | 0.053949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_261-454_0_4_line_17 |  | 13 | 25 | 0.0055549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-454_0_4_line_18 |  | 14 | 15 | 0.007443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-454_0_4_line_19 |  | 14 | 16 | 0.22746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-454_0_4_line_20 |  | 15 | 25 | 0.015734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-454_0_4_line_21 |  | 16 | 19 | 0.026183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-454_0_4_line_22 |  | 17 | 18 | 0.24294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-454_0_4_line_23 |  | 17 | 19 | 0.077172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-454_0_4_line_24 |  | 18 | 21 | 0.021583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-454_0_4_line_25 |  | 24 | 26 | 0.012215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-454_0_4_line_26 |  | 26 | 27 | 0.027894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-454_0_4_trafo_15 | 0.63 MVA 20/0.4 kV | 28 | 7 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20
0 | 2685516.525 | 1245401.8677 | 2685512.8915 | 1245420.5126
1 | 2685509.8825 | 1245435.9526 | 2685512.8915 | 1245420.5126
2 | 2685516.525 | 1245401.8677 | 2685496.261 | 1245398.0566
3 | 2685516.525 | 1245401.8677 | 2685524.9617 | 1245401.6512
4 | 2685480.6604 | 1245486.9357 | 2685488.129 | 1245483.5742 | 2685495.5484 | 1245478.911 | 2685501.3067 | 1245473.6345 | 2685504.2572 | 1245465.004 | 2685507.6127 | 1245447.6841 | 2685509.8825 | 1245435.9526
5 | 2685493.7291 | 1245397.5805 | 2685496.261 | 1245398.0566
6 | 2685554.5244 | 1245400.8927 | 2685524.9617 | 1245401.6512
7 | 2685436.4496 | 1245484.8195 | 2685462.3784 | 1245489.2851 | 2685470.5811 | 1245488.992 | 2685480.6604 | 1245486.9357
8 | 2685480.6604 | 1245486.9357 | 2685482.7518 | 1245477.6145 | 2685482.19 | 1245470.9904 | 2685478.8294 | 1245468.7626
9 | 2685493.7291 | 1245397.5805 | 2685476.2183 | 1245394.6371
10 | 2685554.5244 | 1245400.8927 | 2685550.3098 | 1245387.6777 | 2685552.6353 | 1245374.7128 | 2685611.4238 | 1245384.6237 | 2685615.4704 | 1245360.2753 | 2685612.7191 | 1245354.5759
11 | 2685436.4496 | 1245484.8195 | 2685437.6019 | 1245477.742 | 2685439.3566 | 1245466.8456
12 | 2685436.4496 | 1245484.8195 | 2685418.2999 | 1245481.69
13 | 2685560.7751 | 1245240.5648 | 2685561.1218 | 1245238.535 | 2685536.7942 | 1245234.5702 | 2685540.8205 | 1245211.6224 | 2685620.7659 | 1245226.9647 | 2685627.4707 | 1245229.43 | 2685637.0954 | 1245235.8625 | 2685662.1712 | 1245259.6865 | 2685670.9691 | 1245267.8974 | 2685676.3834 | 1245274.9474 | 2685690.818 | 1245293.1248 | 2685697.2931 | 1245303.6261
14 | 2685560.7751 | 1245240.5648 | 2685619.5106 | 1245251.0977 | 2685635.044 | 1245270.1137 | 2685629.1544 | 1245306.9035
15 | 2685697.2931 | 1245303.6261 | 2685706.8694 | 1245319.1425 | 2685714.879 | 1245336.4043 | 2685720.3694 | 1245353.8631 | 2685723.9794 | 1245374.3877
16 | 2685612.7191 | 1245354.5759 | 2685614.601 | 1245350.3666 | 2685622.7598 | 1245346.8484 | 2685629.1544 | 1245306.9035
17 | 2685476.2183 | 1245394.6371 | 2685470.7406 | 1245393.7138
18 | 2685452.6813 | 1245384.1014 | 2685455.2251 | 1245391.0987
19 | 2685351.3938 | 1245512.371 | 2685359.2005 | 1245495.4931 | 2685358.7018 | 1245482.8989 | 2685356.5875 | 1245464.4327 | 2685359.7401 | 1245430.731 | 2685367.6303 | 1245393.8952 | 2685371.5966 | 1245370.335 | 2685380.0622 | 1245372.2582 | 2685403.7329 | 1245376.1462 | 2685428.3686 | 1245380.1928 | 2685452.6813 | 1245384.1014
20 | 2685455.2251 | 1245391.0987 | 2685470.7406 | 1245393.7138
21 | 2685351.3938 | 1245512.371 | 2685345.9811 | 1245524.0906 | 2685341.1252 | 1245536.4447
22 | 2685244.2981 | 1245422.187 | 2685244.787 | 1245430.2222 | 2685245.026 | 1245434.0952 | 2685251.7956 | 1245446.2347 | 2685265.846 | 1245457.5561 | 2685282.6741 | 1245458.5765 | 2685293.9894 | 1245456.2152 | 2685293.6512 | 1245465.0168 | 2685293.5338 | 1245482.6281 | 2685284.0724 | 1245500.0382 | 2685284.6978 | 1245504.3615 | 2685275.0327 | 1245520.7012 | 2685284.8001 | 1245527.7135 | 2685288.7751 | 1245531.8848 | 2685291.8573 | 1245536.1322 | 2685293.2107 | 1245541.8448 | 2685300.2216 | 1245546.1265 | 2685302.8667 | 1245550.8235 | 2685311.3819 | 1245594.4337 | 2685312.4201 | 1245599.4745 | 2685313.2587 | 1245608.4043
23 | 2685313.2587 | 1245608.4043 | 2685317.7452 | 1245595.9263 | 2685341.1252 | 1245536.4447
24 | 2685244.2981 | 1245422.187 | 2685249.6145 | 1245416.1034 | 2685251.6308 | 1245408.3044 | 2685253.5987 | 1245403.3513 | 2685253.7 | 1245403.2887
25 | 2685418.2999 | 1245481.69 | 2685406.2622 | 1245479.6143
26 | 2685411.406 | 1245452.1989 | 2685406.2622 | 1245479.6143 | 2685406.2622 | 1245479.6143

## bus_geodata
| x | y | coords
0 | 2685512.8915 | 1245420.5126
1 | 2685516.525 | 1245401.8677
2 | 2685509.8825 | 1245435.9526
3 | 2685496.261 | 1245398.0566
4 | 2685524.9617 | 1245401.6512
5 | 2685480.6604 | 1245486.9357
6 | 2685493.7291 | 1245397.5805
7 | 2685554.5244 | 1245400.8927
8 | 2685436.4496 | 1245484.8195
9 | 2685478.8294 | 1245468.7626
10 | 2685560.7751 | 1245240.5648
11 | 2685697.2931 | 1245303.6261
12 | 2685629.1544 | 1245306.9035
13 | 2685476.2183 | 1245394.6371
14 | 2685452.6813 | 1245384.1014
15 | 2685455.2251 | 1245391.0987
16 | 2685351.3938 | 1245512.371
17 | 2685313.2587 | 1245608.4043
18 | 2685244.2981 | 1245422.187
19 | 2685341.1252 | 1245536.4447
20 | 2685723.9794 | 1245374.3877
21 | 2685253.7 | 1245403.2887
22 | 2685612.7191 | 1245354.5759
23 | 2685439.3566 | 1245466.8456
24 | 2685418.2999 | 1245481.69
25 | 2685470.7406 | 1245393.7138
26 | 2685406.2622 | 1245479.6143
27 | 2685411.406 | 1245452.1989
28 | 2685552.6353 | 1245374.7128

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99584 | -0.079983 | 0.032989 | 0.0082679
1 | 0.99684 | -0.060652 | 0 | 0
2 | 0.99548 | -0.086889 | 0 | 0
3 | 0.9955 | -0.086471 | 0.043286 | 0.010848
4 | 0.99783 | -0.041537 | 0.031565 | 0.007911
5 | 0.99403 | -0.11481 | 0 | 0
6 | 0.99544 | -0.08774 | 0 | 0
7 | 1 | 0 | -0.2404 | -0.060662
8 | 0.99362 | -0.12271 | 0 | 0
9 | 0.99376 | -0.12014 | 0.014948 | 0.0037462
10 | 0.98998 | -0.18994 | 0 | 0
11 | 0.98208 | -0.34242 | 0 | 0
12 | 0.99396 | -0.11405 | 0.005245 | 0.0013145
13 | 0.99498 | -0.096467 | 0 | 0
14 | 0.99482 | -0.099576 | 0 | 0
15 | 0.99483 | -0.099457 | 0 | 0
16 | 0.99464 | -0.10319 | 0 | 0
17 | 0.99458 | -0.10439 | 0 | 0
18 | 0.99446 | -0.10681 | 0 | 0
19 | 0.99462 | -0.10361 | 0.00032493 | 8.1435e-05
20 | 0.97708 | -0.44028 | 0.070517 | 0.017673
21 | 0.99445 | -0.10703 | 0.00056183 | 0.00014081
22 | 0.99586 | -0.07805 | 0 | 0
23 | 0.99361 | -0.12294 | 0.0007213 | 0.00018077
24 | 0.99347 | -0.12573 | 0.00084356 | 0.00021142
25 | 0.99484 | -0.099206 | 0.027101 | 0.006792
26 | 0.99337 | -0.12756 | 0.00090575 | 0.000227
27 | 0.99318 | -0.13127 | 0.0075468 | 0.0018914
28 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.058007 | -0.014555 | 0.05806 | 0.014589 | 5.3523e-05 | 3.4007e-05 | 0.086682 | 0.086682 | 0.086682 | 0.99584 | -0.079983 | 0.99684 | -0.060652 | 23.8137
1 | 0.025018 | 0.0062876 | -0.025009 | -0.0062825 | 8.2461e-06 | 5.0729e-06 | 0.037388 | 0.037388 | 0.037388 | 0.99584 | -0.079983 | 0.99548 | -0.086889 | 10.2715
2 | 0.071378 | 0.017921 | -0.071291 | -0.017865 | 8.78e-05 | 5.5923e-05 | 0.10656 | 0.10656 | 0.10656 | 0.99684 | -0.060652 | 0.9955 | -0.086471 | 29.2748
3 | -0.12944 | -0.032511 | 0.12956 | 0.032586 | 0.00011818 | 7.5526e-05 | 0.19324 | 0.19324 | 0.19324 | 0.99684 | -0.060652 | 0.99783 | -0.041537 | 53.0884
4 | 0.025009 | 0.0062825 | -0.024976 | -0.006262 | 3.3275e-05 | 2.0472e-05 | 0.037388 | 0.037389 | 0.037389 | 0.99548 | -0.086889 | 0.99403 | -0.11481 | 10.2716
5 | 0.028005 | 0.007017 | -0.028003 | -0.0070159 | 1.6928e-06 | 1.0499e-06 | 0.041859 | 0.041859 | 0.041859 | 0.9955 | -0.086471 | 0.99544 | -0.08774 | 11.4997
6 | -0.16112 | -0.040497 | 0.16144 | 0.040701 | 0.00032022 | 0.00020416 | 0.24031 | 0.24031 | 0.24031 | 0.99783 | -0.041537 | 1 | 0 | 33.0101
7 | 0.010025 | 0.0025136 | -0.010021 | -0.0025118 | 3.7731e-06 | 1.8358e-06 | 0.015007 | 0.015007 | 0.015007 | 0.99403 | -0.11481 | 0.99362 | -0.12271 | 4.1228
8 | 0.014951 | 0.0037484 | -0.014948 | -0.0037462 | 3.8009e-06 | 2.1703e-06 | 0.022382 | 0.022382 | 0.022382 | 0.99403 | -0.11481 | 0.99376 | -0.12014 | 6.1489
9 | 0.028003 | 0.0070159 | -0.027991 | -0.0070087 | 1.1633e-05 | 7.2153e-06 | 0.041859 | 0.041859 | 0.041859 | 0.99544 | -0.08774 | 0.99498 | -0.096467 | 11.4997
10 | 0.077304 | 0.01996 | -0.077011 | -0.019776 | 0.000293 | 0.00018445 | 0.11524 | 0.11524 | 0.11524 | 1 | 0 | 0.99586 | -0.07805 | 15.8296
11 | 0.0007213 | 0.00018054 | -0.0007213 | -0.00018077 | 7.9663e-09 | -2.3073e-07 | 0.0010801 | 0.0010802 | 0.0010802 | 0.99362 | -0.12271 | 0.99361 | -0.12294 | 0.29676
12 | 0.0092995 | 0.0023312 | -0.0092982 | -0.0023306 | 1.3396e-06 | 6.1882e-07 | 0.013927 | 0.013927 | 0.013927 | 0.99362 | -0.12271 | 0.99347 | -0.12573 | 3.8261
13 | 0.071369 | 0.018211 | -0.070848 | -0.017884 | 0.00052155 | 0.00032764 | 0.10739 | 0.10739 | 0.10739 | 0.98998 | -0.18994 | 0.98208 | -0.34242 | 14.7516
14 | -0.071369 | -0.018211 | 0.071632 | 0.018376 | 0.00026269 | 0.00016498 | 0.10739 | 0.10739 | 0.10739 | 0.98998 | -0.18994 | 0.99396 | -0.11405 | 14.7513
15 | 0.070848 | 0.017884 | -0.070517 | -0.017673 | 0.00033044 | 0.00021052 | 0.10739 | 0.10739 | 0.10739 | 0.98208 | -0.34242 | 0.97708 | -0.44028 | 29.5033
16 | -0.076877 | -0.019691 | 0.077011 | 0.019776 | 0.00013434 | 8.4574e-05 | 0.11524 | 0.11524 | 0.11524 | 0.99396 | -0.11405 | 0.99586 | -0.07805 | 15.8297
17 | 0.027991 | 0.0070087 | -0.027988 | -0.0070064 | 3.65e-06 | 2.2638e-06 | 0.041859 | 0.041859 | 0.041859 | 0.99498 | -0.096467 | 0.99484 | -0.099206 | 11.4998
18 | -0.00088702 | -0.00021468 | 0.00088703 | 0.00021459 | 4.8936e-09 | -9.3507e-08 | 0.0013241 | 0.0013241 | 0.0013241 | 0.99482 | -0.099576 | 0.99483 | -0.099457 | 0.36377
19 | 0.00088702 | 0.00021468 | -0.00088687 | -0.00021754 | 1.4967e-07 | -2.857e-06 | 0.0013241 | 0.0013251 | 0.0013251 | 0.99482 | -0.099576 | 0.99464 | -0.10319 | 0.36405
20 | -0.00088703 | -0.00021459 | 0.00088704 | 0.00021439 | 1.0344e-08 | -1.9768e-07 | 0.0013241 | 0.001324 | 0.0013241 | 0.99483 | -0.099457 | 0.99484 | -0.099206 | 0.36376
21 | 0.00088687 | 0.00021754 | -0.00088685 | -0.00021787 | 1.7243e-08 | -3.2879e-07 | 0.0013251 | 0.0013253 | 0.0013253 | 0.99464 | -0.10319 | 0.99462 | -0.10361 | 0.36408
22 | 0.0005619 | 0.00013742 | -0.00056184 | -0.00014053 | 6.4287e-08 | -3.1112e-06 | 0.00083949 | 0.00084059 | 0.00084059 | 0.99458 | -0.10439 | 0.99446 | -0.10681 | 0.23093
23 | -0.0005619 | -0.00013742 | 0.00056193 | 0.00013643 | 2.0387e-08 | -9.8848e-07 | 0.00083949 | 0.00083915 | 0.00083949 | 0.99458 | -0.10439 | 0.99462 | -0.10361 | 0.23063
24 | 0.00056184 | 0.00014053 | -0.00056183 | -0.00014081 | 5.7197e-09 | -2.7637e-07 | 0.00084059 | 0.00084069 | 0.00084069 | 0.99446 | -0.10681 | 0.99445 | -0.10703 | 0.23096
25 | 0.0084546 | 0.0021192 | -0.0084539 | -0.0021189 | 7.3458e-07 | 3.1198e-07 | 0.012663 | 0.012663 | 0.012663 | 0.99347 | -0.12573 | 0.99337 | -0.12756 | 3.479
26 | 0.0075481 | 0.0018919 | -0.0075468 | -0.0018914 | 1.3373e-06 | 4.948e-07 | 0.011307 | 0.011307 | 0.011307 | 0.99337 | -0.12756 | 0.99318 | -0.13127 | 3.1063

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.2404 | 0.060662

## res_load
| p_mw | q_mvar
0 | 0.032989 | 0.0082679
1 | 0.043286 | 0.010848
2 | 0.031565 | 0.007911
3 | 0.014948 | 0.0037462
4 | 0.005245 | 0.0013145
5 | 0.00032493 | 8.1435e-05
6 | 0.070517 | 0.017673
7 | 0.00056183 | 0.00014081
8 | 0.0007213 | 0.00018077
9 | 0.00084356 | 0.00021142
10 | 0.027101 | 0.006792
11 | 0.00090575 | 0.000227
12 | 0.0075468 | 0.0018914

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1