## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-461_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-461_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-461_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-461_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-461_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-461_0_5_node_40 | 0.4 | n |  | TRUE
6 | bus_LV_261-461_0_5_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_261-461_0_5_node_25 | 0.4 | n |  | TRUE
8 | bus_LV_261-461_0_5_node_32 | 0.4 | n |  | TRUE
9 | bus_LV_261-461_0_5_node_30 | 0.4 | n |  | TRUE
10 | bus_LV_261-461_0_5_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_261-461_0_5_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_261-461_0_5_node_27 | 0.4 | n |  | TRUE
13 | bus_LV_261-461_0_5_node_26 | 0.4 | n |  | TRUE
14 | bus_LV_261-461_0_5_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_261-461_0_5_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_261-461_0_5_node_24 | 0.4 | n |  | TRUE
17 | bus_LV_261-461_0_5_node_42 | 0.4 | n |  | TRUE
18 | bus_LV_261-461_0_5_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_261-461_0_5_node_28 | 0.4 | n |  | TRUE
20 | bus_LV_261-461_0_5_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_261-461_0_5_node_44 | 0.4 | n |  | TRUE
22 | bus_LV_261-461_0_5_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_261-461_0_5_node_35 | 0.4 | n |  | TRUE
24 | bus_LV_261-461_0_5_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_261-461_0_5_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_261-461_0_5_node_36 | 0.4 | n |  | TRUE
27 | bus_LV_261-461_0_5_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_261-461_0_5_node_43 | 0.4 | n |  | TRUE
29 | bus_LV_261-461_0_5_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_261-461_0_5_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_261-461_0_5_node_39 | 0.4 | n |  | TRUE
32 | bus_LV_261-461_0_5_node_18 | 0.4 | n |  | TRUE
33 | bus_LV_261-461_0_5_node_33 | 0.4 | n |  | TRUE
34 | bus_LV_261-461_0_5_node_22 | 0.4 | n |  | TRUE
35 | bus_LV_261-461_0_5_node_37 | 0.4 | n |  | TRUE
36 | bus_LV_261-461_0_5_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_261-461_0_5_node_41 | 0.4 | n |  | TRUE
38 | bus_LV_261-461_0_5_node_34 | 0.4 | n |  | TRUE
39 | bus_MV_552_0_node_18 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-461_0_5_load_0 | 0 | 0.058966 | 0.014778 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-461_0_5_load_40 | 5 | 0.004263 | 0.0010684 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-461_0_5_load_25 | 7 | 0.019517 | 0.0048914 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-461_0_5_load_32 | 8 | 0.0020381 | 0.00051081 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-461_0_5_load_30 | 9 | 0.011111 | 0.0027847 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-461_0_5_load_27 | 12 | 0.018162 | 0.0045518 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-461_0_5_load_26 | 13 | 0.030649 | 0.0076814 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-461_0_5_load_42 | 17 | 0.0097422 | 0.0024416 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-461_0_5_load_28 | 19 | 0.0091515 | 0.0022936 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-461_0_5_load_44 | 21 | 0.01849 | 0.0046339 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-461_0_5_load_36 | 26 | 0.020928 | 0.005245 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-461_0_5_load_43 | 28 | 0.0010702 | 0.00026822 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-461_0_5_load_29 | 30 | 0.018336 | 0.0045953 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-461_0_5_load_39 | 31 | 0.035906 | 0.0089988 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-461_0_5_load_33 | 33 | 0.0018323 | 0.00045922 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-461_0_5_load_37 | 35 | 0.0089245 | 0.0022367 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-461_0_5_load_31 | 36 | 0.0029397 | 0.00073676 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-461_0_5_load_41 | 37 | 0.0097336 | 0.0024395 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-461_0_5_load_34 | 38 | 0.041236 | 0.010335 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 5 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-461_0_5_line_0 |  | 0 | 1 | 0.01735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
1 | LV_261-461_0_5_line_1 |  | 0 | 2 | 0.032432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
2 | LV_261-461_0_5_line_2 |  | 1 | 3 | 0.091049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
3 | LV_261-461_0_5_line_3 |  | 2 | 4 | 0.013044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
4 | LV_261-461_0_5_line_4 |  | 3 | 5 | 0.0067357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
5 | LV_261-461_0_5_line_5 |  | 4 | 6 | 0.055133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
6 | LV_261-461_0_5_line_6 |  | 4 | 7 | 0.064524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-461_0_5_line_7 |  | 6 | 8 | 0.051417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
8 | LV_261-461_0_5_line_8 |  | 6 | 9 | 0.026246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-461_0_5_line_9 |  | 8 | 32 | 0.037815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_261-461_0_5_line_10 |  | 9 | 36 | 0.0022961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-461_0_5_line_11 |  | 10 | 11 | 0.076005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-461_0_5_line_12 |  | 10 | 12 | 0.028203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-461_0_5_line_13 |  | 11 | 13 | 0.039267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-461_0_5_line_14 |  | 13 | 16 | 0.030722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
15 | LV_261-461_0_5_line_15 |  | 14 | 15 | 0.063532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
16 | LV_261-461_0_5_line_16 |  | 14 | 16 | 0.036585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
17 | LV_261-461_0_5_line_17 |  | 14 | 17 | 0.012629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-461_0_5_line_18 |  | 15 | 18 | 0.072119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
19 | LV_261-461_0_5_line_19 |  | 15 | 19 | 0.092436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-461_0_5_line_20 |  | 17 | 37 | 0.018213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-461_0_5_line_21 |  | 18 | 34 | 0.085902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-461_0_5_line_22 |  | 18 | 30 | 0.016844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
23 | LV_261-461_0_5_line_23 |  | 20 | 21 | 0.01238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-461_0_5_line_24 |  | 20 | 22 | 0.054024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_261-461_0_5_line_25 |  | 20 | 23 | 0.024085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-461_0_5_line_26 |  | 22 | 29 | 0.038123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_261-461_0_5_line_27 |  | 22 | 30 | 0.053139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
28 | LV_261-461_0_5_line_28 |  | 22 | 27 | 0.04762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_261-461_0_5_line_29 |  | 23 | 38 | 0.049925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-461_0_5_line_30 |  | 24 | 25 | 0.081412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-461_0_5_line_31 |  | 24 | 26 | 0.045345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-461_0_5_line_32 |  | 25 | 31 | 0.033025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-461_0_5_line_33 |  | 27 | 28 | 0.03747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
34 | LV_261-461_0_5_line_34 |  | 28 | 33 | 0.012524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
35 | LV_261-461_0_5_line_35 |  | 29 | 31 | 0.036819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-461_0_5_line_36 |  | 32 | 33 | 0.048589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
37 | LV_261-461_0_5_line_37 |  | 34 | 35 | 0.079085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-461_0_5_trafo_40 | 0.63 MVA 20/0.4 kV | 39 | 5 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2686572.6363 | 1251243.503 | 2686565.6349 | 1251246.3362 | 2686555.8545 | 1251246.9022
1 | 2686523.4766 | 1251248.778 | 2686535.4139 | 1251248.085 | 2686555.8545 | 1251246.9022
2 | 2686572.6363 | 1251243.503 | 2686580.5954 | 1251250.5579 | 2686581.3509 | 1251251.5474 | 2686582.418 | 1251244.1352 | 2686583.9578 | 1251239.4987 | 2686585.8236 | 1251235.8009 | 2686588.075 | 1251232.5758 | 2686591.0748 | 1251230.8294 | 2686594.7656 | 1251230.3497 | 2686599.0364 | 1251230.4788 | 2686596.9702 | 1251266.4647 | 2686597.751 | 1251269.8564 | 2686600.3885 | 1251271.7186 | 2686604.8858 | 1251271.84
3 | 2686513.3674 | 1251248.3523 | 2686514.7828 | 1251249.1291 | 2686516.9845 | 1251250.8514 | 2686518.604 | 1251252.6431 | 2686523.4766 | 1251248.778
4 | 2686604.8858 | 1251271.84 | 2686607.0117 | 1251278.2314
5 | 2686489.1588 | 1251290.6976 | 2686491.1982 | 1251285.4456 | 2686492.2726 | 1251282.6925 | 2686495.8288 | 1251280.5762 | 2686500.9151 | 1251266.2173 | 2686508.0715 | 1251246.051 | 2686513.3674 | 1251248.3523
6 | 2686513.3674 | 1251248.3523 | 2686515.1045 | 1251243.6407 | 2686534.8567 | 1251187.5128
7 | 2686489.1588 | 1251290.6976 | 2686487.6057 | 1251294.7002 | 2686485.2071 | 1251297.1559 | 2686482.0576 | 1251300.3679 | 2686469.7383 | 1251337.5738
8 | 2686489.1588 | 1251290.6976 | 2686514.1264 | 1251298.7879
9 | 2686473.5031 | 1251373.8986 | 2686468.9348 | 1251360.0326 | 2686466.4926 | 1251347.3763 | 2686469.7383 | 1251337.5738
10 | 2686516.2992 | 1251299.5296 | 2686514.9968 | 1251299.0699 | 2686514.1264 | 1251298.7879
11 | 2686701.4389 | 1251207.1361 | 2686695.7553 | 1251206.5748 | 2686675.4854 | 1251203.5538 | 2686657.8017 | 1251200.226 | 2686646.5646 | 1251197.9378 | 2686626.8601 | 1251192.9015
12 | 2686701.4389 | 1251207.1361 | 2686703.8399 | 1251235.2366
13 | 2686626.8601 | 1251192.9015 | 2686626.5624 | 1251194.6763 | 2686630.1273 | 1251231.9733
14 | 2686633.0504 | 1251262.5557 | 2686630.1273 | 1251231.9733
15 | 2686669.4391 | 1251299.9826 | 2686669.31 | 1251300.0364 | 2686642.4738 | 1251301.0892 | 2686642.1955 | 1251295.859 | 2686642.036 | 1251292.8321 | 2686641.8656 | 1251289.516 | 2686643.2373 | 1251280.3736 | 2686658.6856 | 1251277.564
16 | 2686633.0504 | 1251262.5557 | 2686647.4998 | 1251267.1371 | 2686657.7014 | 1251266.4079 | 2686658.6856 | 1251277.564
17 | 2686658.6856 | 1251277.564 | 2686671.278 | 1251276.6067
18 | 2686652.2445 | 1251352.5042 | 2686656.9415 | 1251345.1674 | 2686659.9452 | 1251335.415 | 2686665.1948 | 1251332.6119 | 2686672.3236 | 1251327.7792 | 2686683.5582 | 1251318.8701 | 2686680.0787 | 1251315.2275 | 2686675.1338 | 1251312.164 | 2686673.1502 | 1251307.9207 | 2686669.4391 | 1251299.9826
19 | 2686669.4391 | 1251299.9826 | 2686755.8675 | 1251267.201
20 | 2686689.439 | 1251275.226 | 2686671.278 | 1251276.6067
21 | 2686652.2445 | 1251352.5042 | 2686659.0804 | 1251355.3063 | 2686665.7274 | 1251357.0826 | 2686671.0562 | 1251350.9337 | 2686675.5051 | 1251353.3339 | 2686680.7507 | 1251355.4455 | 2686694.0178 | 1251359.8096 | 2686714.0914 | 1251366.4082 | 2686720.3276 | 1251367.8895 | 2686726.4963 | 1251367.7908 | 2686730.9711 | 1251365.321
22 | 2686652.2445 | 1251352.5042 | 2686649.896 | 1251356.1727 | 2686637.5038 | 1251357.7199
23 | 2686586.3472 | 1251395.1511 | 2686598.7132 | 1251394.0309
24 | 2686584.8231 | 1251364.6391 | 2686580.3255 | 1251363.5059 | 2686575.1625 | 1251363.486 | 2686575.2853 | 1251367.4797 | 2686580.1946 | 1251367.8184 | 2686584.8305 | 1251369.2983 | 2686589.7489 | 1251372.1056 | 2686592.7551 | 1251374.5625 | 2686595.5306 | 1251378.3393 | 2686597.1924 | 1251382.3999 | 2686598.3543 | 1251386.053 | 2686598.6615 | 1251392.9182 | 2686598.7132 | 1251394.0309
25 | 2686601.1257 | 1251417.9843 | 2686598.97 | 1251399.183 | 2686598.7132 | 1251394.0309
26 | 2686551.6091 | 1251372.8824 | 2686551.4314 | 1251369.0325 | 2686557.5312 | 1251366.9311 | 2686561.3551 | 1251365.6082 | 2686575.1625 | 1251363.486 | 2686580.3255 | 1251363.5059 | 2686584.8231 | 1251364.6391
27 | 2686584.8231 | 1251364.6391 | 2686593.4041 | 1251363.219 | 2686623.828 | 1251359.4274 | 2686637.5038 | 1251357.7199
28 | 2686560.5453 | 1251329.6025 | 2686566.2463 | 1251337.7475 | 2686571.2151 | 1251344.8587 | 2686572.3764 | 1251348.5563 | 2686573.9628 | 1251353.6388 | 2686574.9508 | 1251356.8001 | 2686575.0585 | 1251360.271 | 2686575.1625 | 1251363.486 | 2686580.3255 | 1251363.5059 | 2686584.8231 | 1251364.6391
29 | 2686601.1257 | 1251417.9843 | 2686605.1039 | 1251417.4643 | 2686618.2673 | 1251416.0111 | 2686650.7591 | 1251412.6071
30 | 2686473.7949 | 1251460.9241 | 2686471.076 | 1251435.6876 | 2686469.5996 | 1251422.0336 | 2686468.9731 | 1251420.4788 | 2686468.0235 | 1251419.3419 | 2686471.0197 | 1251415.2492 | 2686474.9935 | 1251410.8927 | 2686478.2843 | 1251407.3047 | 2686489.1854 | 1251395.3548 | 2686495.7772 | 1251392.6489
31 | 2686473.7949 | 1251460.9241 | 2686477.9099 | 1251460.3393 | 2686480.958 | 1251459.9279 | 2686518.8454 | 1251455.7837
32 | 2686495.7772 | 1251392.6489 | 2686497.6943 | 1251396.2796 | 2686504.7384 | 1251396.7161 | 2686525.615 | 1251390.2293
33 | 2686560.5453 | 1251329.6025 | 2686555.6297 | 1251334.8569 | 2686529.6134 | 1251350.3391
34 | 2686529.6134 | 1251350.3391 | 2686518.8513 | 1251356.7436
35 | 2686551.6091 | 1251372.8824 | 2686552.0417 | 1251382.0179 | 2686525.615 | 1251390.2293
36 | 2686473.5031 | 1251373.8986 | 2686513.7019 | 1251359.808 | 2686518.8513 | 1251356.7436
37 | 2686730.9711 | 1251365.321 | 2686737.7177 | 1251359.7823 | 2686747.5414 | 1251348.7733 | 2686754.0548 | 1251340.6069 | 2686757.2461 | 1251336.6061 | 2686772.6232 | 1251322.6763 | 2686788.7563 | 1251312.1016

## bus_geodata
| x | y | coords
0 | 2686555.8545 | 1251246.9022
1 | 2686572.6363 | 1251243.503
2 | 2686523.4766 | 1251248.778
3 | 2686604.8858 | 1251271.84
4 | 2686513.3674 | 1251248.3523
5 | 2686607.0117 | 1251278.2314
6 | 2686489.1588 | 1251290.6976
7 | 2686534.8567 | 1251187.5128
8 | 2686469.7383 | 1251337.5738
9 | 2686514.1264 | 1251298.7879
10 | 2686701.4389 | 1251207.1361
11 | 2686626.8601 | 1251192.9015
12 | 2686703.8399 | 1251235.2366
13 | 2686630.1273 | 1251231.9733
14 | 2686658.6856 | 1251277.564
15 | 2686669.4391 | 1251299.9827
16 | 2686633.0504 | 1251262.5557
17 | 2686671.278 | 1251276.6067
18 | 2686652.2445 | 1251352.5042
19 | 2686755.8675 | 1251267.201
20 | 2686598.7132 | 1251394.0309
21 | 2686586.3472 | 1251395.1511
22 | 2686584.8231 | 1251364.6391
23 | 2686601.1257 | 1251417.9843
24 | 2686473.7949 | 1251460.9241
25 | 2686495.7772 | 1251392.6489
26 | 2686518.8454 | 1251455.7837
27 | 2686560.5453 | 1251329.6025
28 | 2686529.6134 | 1251350.3391
29 | 2686551.6091 | 1251372.8824
30 | 2686637.5038 | 1251357.7199
31 | 2686525.615 | 1251390.2293
32 | 2686473.5031 | 1251373.8986
33 | 2686518.8513 | 1251356.7436
34 | 2686730.9711 | 1251365.3211
35 | 2686788.7563 | 1251312.1016
36 | 2686516.2992 | 1251299.5296
37 | 2686689.439 | 1251275.226
38 | 2686650.7591 | 1251412.6071
39 | 2686604.8858 | 1251271.84

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9932 | -0.12886 | 0.058966 | 0.014778
1 | 0.99422 | -0.10933 | 0 | 0
2 | 0.99163 | -0.15869 | 0 | 0
3 | 0.9996 | -0.0074904 | 0 | 0
4 | 0.991 | -0.17071 | 0 | 0
5 | 1 | 0 | -0.32628 | -0.0836
6 | 0.98854 | -0.21787 | 0 | 0
7 | 0.98985 | -0.19309 | 0.019517 | 0.0048914
8 | 0.98638 | -0.25947 | 0.0020381 | 0.00051081
9 | 0.9882 | -0.22445 | 0.011111 | 0.0027847
10 | 0.97304 | -0.51988 | 0 | 0
11 | 0.97433 | -0.4945 | 0 | 0
12 | 0.97256 | -0.52931 | 0.018162 | 0.0045518
13 | 0.97499 | -0.48141 | 0.030649 | 0.0076814
14 | 0.9756 | -0.46937 | 0 | 0
15 | 0.97641 | -0.45349 | 0 | 0
16 | 0.97527 | -0.47591 | 0 | 0
17 | 0.97537 | -0.47387 | 0.0097422 | 0.0024416
18 | 0.97745 | -0.43308 | 0 | 0
19 | 0.97562 | -0.46897 | 0.0091515 | 0.0022936
20 | 0.97775 | -0.42708 | 0 | 0
21 | 0.97754 | -0.43126 | 0.01849 | 0.0046339
22 | 0.97875 | -0.40749 | 0 | 0
23 | 0.97683 | -0.44521 | 0 | 0
24 | 0.9739 | -0.50276 | 0 | 0
25 | 0.97549 | -0.4715 | 0 | 0
26 | 0.97302 | -0.52022 | 0.020928 | 0.005245
27 | 0.98071 | -0.36922 | 0 | 0
28 | 0.98226 | -0.33921 | 0.0010702 | 0.00026822
29 | 0.97808 | -0.42065 | 0 | 0
30 | 0.97772 | -0.42777 | 0.018336 | 0.0045953
31 | 0.97614 | -0.45885 | 0.035906 | 0.0089988
32 | 0.9848 | -0.2899 | 0 | 0
33 | 0.98277 | -0.32915 | 0.0018323 | 0.00045922
34 | 0.97674 | -0.44708 | 0 | 0
35 | 0.97608 | -0.45999 | 0.0089245 | 0.0022367
36 | 0.9882 | -0.22457 | 0.0029397 | 0.00073676
37 | 0.97521 | -0.47712 | 0.0097336 | 0.0024395
38 | 0.97492 | -0.48289 | 0.041236 | 0.010335
39 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.32261 | -0.082313 | 0.32292 | 0.082507 | 0.00030464 | 0.00019385 | 0.48386 | 0.48386 | 0.48386 | 0.9932 | -0.12886 | 0.99422 | -0.10933 | 26.5857
1 | 0.26365 | 0.067535 | -0.26327 | -0.067293 | 0.00038051 | 0.00024143 | 0.39552 | 0.39552 | 0.39552 | 0.9932 | -0.12886 | 0.99163 | -0.15869 | 21.7317
2 | -0.32292 | -0.082507 | 0.32452 | 0.083524 | 0.0015987 | 0.0010172 | 0.48386 | 0.48386 | 0.48386 | 0.99422 | -0.10933 | 0.9996 | -0.0074904 | 26.5857
3 | 0.26327 | 0.067293 | -0.26311 | -0.067196 | 0.00015305 | 9.7108e-05 | 0.39552 | 0.39552 | 0.39552 | 0.99163 | -0.15869 | 0.991 | -0.17071 | 21.7317
4 | -0.32452 | -0.083524 | 0.32463 | 0.0836 | 0.00011827 | 7.5252e-05 | 0.48386 | 0.48386 | 0.48386 | 0.9996 | -0.0074904 | 1 | 0 | 26.5855
5 | 0.24358 | 0.062292 | -0.24302 | -0.061941 | 0.00055445 | 0.00035131 | 0.36618 | 0.36618 | 0.36618 | 0.991 | -0.17071 | 0.98854 | -0.21787 | 20.1198
6 | 0.019538 | 0.0049039 | -0.019517 | -0.0048914 | 2.0828e-05 | 1.2499e-05 | 0.029339 | 0.029339 | 0.029339 | 0.991 | -0.17071 | 0.98985 | -0.19309 | 8.0602
7 | 0.22897 | 0.058417 | -0.22851 | -0.058127 | 0.00045906 | 0.00029051 | 0.34502 | 0.34502 | 0.34502 | 0.98854 | -0.21787 | 0.98638 | -0.25947 | 18.9574
8 | 0.014055 | 0.0035239 | -0.014051 | -0.0035214 | 4.4057e-06 | 2.4833e-06 | 0.021157 | 0.021157 | 0.021157 | 0.98854 | -0.21787 | 0.9882 | -0.22445 | 5.8125
9 | 0.22647 | 0.057616 | -0.22614 | -0.057406 | 0.00033163 | 0.00020983 | 0.34195 | 0.34195 | 0.34195 | 0.98638 | -0.25947 | 0.9848 | -0.2899 | 18.7885
10 | 0.0029397 | 0.00073674 | -0.0029397 | -0.00073676 | 1.6872e-08 | -1.8619e-08 | 0.0044266 | 0.0044266 | 0.0044266 | 0.9882 | -0.22445 | 0.9882 | -0.22457 | 1.2161
11 | -0.01817 | -0.0045567 | 0.018192 | 0.0045698 | 2.2007e-05 | 1.3139e-05 | 0.027787 | 0.027787 | 0.027787 | 0.97304 | -0.51988 | 0.97433 | -0.4945 | 7.6339
12 | 0.01817 | 0.0045567 | -0.018162 | -0.0045518 | 8.1662e-06 | 4.8762e-06 | 0.027787 | 0.027788 | 0.027788 | 0.97304 | -0.51988 | 0.97256 | -0.52931 | 7.6339
13 | -0.018192 | -0.0045698 | 0.018203 | 0.0045766 | 1.1369e-05 | 6.787e-06 | 0.027787 | 0.027787 | 0.027787 | 0.97433 | -0.4945 | 0.97499 | -0.48141 | 7.6338
14 | -0.048852 | -0.012258 | 0.048865 | 0.012264 | 1.281e-05 | 6.2821e-06 | 0.074563 | 0.074562 | 0.074563 | 0.97499 | -0.48141 | 0.97527 | -0.47591 | 4.0969
15 | -0.068362 | -0.017156 | 0.068414 | 0.017185 | 5.181e-05 | 2.9189e-05 | 0.10428 | 0.10427 | 0.10428 | 0.9756 | -0.46937 | 0.97641 | -0.45349 | 5.7294
16 | 0.04888 | 0.012272 | -0.048865 | -0.012264 | 1.5255e-05 | 7.4795e-06 | 0.074561 | 0.074562 | 0.074562 | 0.9756 | -0.46937 | 0.97527 | -0.47591 | 4.0968
17 | 0.019481 | 0.0048843 | -0.019477 | -0.0048818 | 4.1814e-06 | 2.5185e-06 | 0.029714 | 0.029714 | 0.029714 | 0.9756 | -0.46937 | 0.97537 | -0.47387 | 8.1633
18 | -0.077572 | -0.019482 | 0.077647 | 0.019526 | 7.5609e-05 | 4.3875e-05 | 0.11823 | 0.11823 | 0.11823 | 0.97641 | -0.45349 | 0.97745 | -0.43308 | 6.4962
19 | 0.0091582 | 0.0022967 | -0.0091515 | -0.0022936 | 6.753e-06 | 3.1667e-06 | 0.013957 | 0.013958 | 0.013958 | 0.97641 | -0.45349 | 0.97562 | -0.46897 | 3.8346
20 | 0.0097351 | 0.0024402 | -0.0097336 | -0.0024395 | 1.5066e-06 | 7.3692e-07 | 0.014852 | 0.014852 | 0.014852 | 0.97537 | -0.47387 | 0.97521 | -0.47712 | 4.0802
21 | 0.008936 | 0.002242 | -0.00893 | -0.0022392 | 5.9623e-06 | 2.7399e-06 | 0.013605 | 0.013605 | 0.013605 | 0.97745 | -0.43308 | 0.97674 | -0.44708 | 3.7376
22 | -0.086583 | -0.021768 | 0.086605 | 0.021781 | 2.1957e-05 | 1.2996e-05 | 0.13183 | 0.13183 | 0.13183 | 0.97745 | -0.43308 | 0.97772 | -0.42777 | 7.2437
23 | 0.018493 | 0.0046361 | -0.01849 | -0.0046339 | 3.6775e-06 | 2.1983e-06 | 0.028145 | 0.028145 | 0.028145 | 0.97775 | -0.42708 | 0.97754 | -0.43126 | 7.7321
24 | -0.05984 | -0.01504 | 0.059896 | 0.015074 | 5.6024e-05 | 3.382e-05 | 0.091084 | 0.091083 | 0.091084 | 0.97775 | -0.42708 | 0.97875 | -0.40749 | 8.341
25 | 0.041346 | 0.010404 | -0.041311 | -0.010382 | 3.5778e-05 | 2.2596e-05 | 0.062939 | 0.062939 | 0.062939 | 0.97775 | -0.42708 | 0.97683 | -0.44521 | 17.2909
26 | 0.057034 | 0.014369 | -0.056999 | -0.014347 | 3.5852e-05 | 2.1509e-05 | 0.086737 | 0.086738 | 0.086738 | 0.97875 | -0.40749 | 0.97808 | -0.42065 | 7.943
27 | 0.10504 | 0.026438 | -0.10494 | -0.026376 | 0.00010169 | 6.1749e-05 | 0.15974 | 0.15974 | 0.15974 | 0.97875 | -0.40749 | 0.97772 | -0.42777 | 8.7769
28 | -0.22197 | -0.055881 | 0.22238 | 0.056138 | 0.00040695 | 0.00025745 | 0.33756 | 0.33756 | 0.33756 | 0.97875 | -0.40749 | 0.98071 | -0.36922 | 18.5472
29 | 0.041311 | 0.010382 | -0.041236 | -0.010335 | 7.4163e-05 | 4.6841e-05 | 0.062939 | 0.062939 | 0.062939 | 0.97683 | -0.44521 | 0.97492 | -0.48289 | 17.291
30 | -0.020945 | -0.0052555 | 0.020976 | 0.0052745 | 3.1269e-05 | 1.8998e-05 | 0.032004 | 0.032004 | 0.032004 | 0.9739 | -0.50276 | 0.97549 | -0.4715 | 8.7923
31 | 0.020945 | 0.0052555 | -0.020928 | -0.005245 | 1.7417e-05 | 1.0583e-05 | 0.032004 | 0.032004 | 0.032004 | 0.9739 | -0.50276 | 0.97302 | -0.52022 | 8.7923
32 | -0.020976 | -0.0052745 | 0.020989 | 0.0052822 | 1.2684e-05 | 7.7053e-06 | 0.032004 | 0.032003 | 0.032004 | 0.97549 | -0.4715 | 0.97614 | -0.45885 | 8.7922
33 | -0.22238 | -0.056138 | 0.2227 | 0.056341 | 0.00032021 | 0.00020257 | 0.33756 | 0.33756 | 0.33756 | 0.98071 | -0.36922 | 0.98226 | -0.33921 | 18.5471
34 | -0.22377 | -0.056609 | 0.22388 | 0.056677 | 0.00010806 | 6.8362e-05 | 0.33918 | 0.33918 | 0.33918 | 0.98226 | -0.33921 | 0.98277 | -0.32915 | 18.6361
35 | 0.056999 | 0.014347 | -0.056895 | -0.014281 | 0.00010388 | 6.602e-05 | 0.086738 | 0.086738 | 0.086738 | 0.97808 | -0.42065 | 0.97614 | -0.45885 | 23.8291
36 | 0.22614 | 0.057406 | -0.22571 | -0.057136 | 0.00042612 | 0.00026963 | 0.34195 | 0.34195 | 0.34195 | 0.9848 | -0.2899 | 0.98277 | -0.32915 | 18.7886
37 | 0.00893 | 0.0022392 | -0.0089245 | -0.0022367 | 5.4895e-06 | 2.5241e-06 | 0.013605 | 0.013605 | 0.013605 | 0.97674 | -0.44708 | 0.97608 | -0.45999 | 3.7377

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.33055 | 0.084668

## res_load
| p_mw | q_mvar
0 | 0.058966 | 0.014778
1 | 0.004263 | 0.0010684
2 | 0.019517 | 0.0048914
3 | 0.0020381 | 0.00051081
4 | 0.011111 | 0.0027847
5 | 0.018162 | 0.0045518
6 | 0.030649 | 0.0076814
7 | 0.0097422 | 0.0024416
8 | 0.0091515 | 0.0022936
9 | 0.01849 | 0.0046339
10 | 0.020928 | 0.005245
11 | 0.0010702 | 0.00026822
12 | 0.018336 | 0.0045953
13 | 0.035906 | 0.0089988
14 | 0.0018323 | 0.00045922
15 | 0.0089245 | 0.0022367
16 | 0.0029397 | 0.00073676
17 | 0.0097336 | 0.0024395
18 | 0.041236 | 0.010335

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1