## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-471_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-471_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-471_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_261-471_0_3_node_35 | 0.4 | n |  | TRUE
4 | bus_LV_261-471_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-471_0_3_node_33 | 0.4 | n |  | TRUE
6 | bus_LV_261-471_0_3_node_34 | 0.4 | n |  | TRUE
7 | bus_LV_261-471_0_3_node_30 | 0.4 | n |  | TRUE
8 | bus_LV_261-471_0_3_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_261-471_0_3_node_18 | 0.4 | n |  | TRUE
10 | bus_LV_261-471_0_3_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_261-471_0_3_node_15 | 0.4 | n |  | TRUE
12 | bus_LV_261-471_0_3_node_13 | 0.4 | n |  | TRUE
13 | bus_LV_261-471_0_3_node_42 | 0.4 | n |  | TRUE
14 | bus_LV_261-471_0_3_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_261-471_0_3_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_261-471_0_3_node_19 | 0.4 | n |  | TRUE
17 | bus_LV_261-471_0_3_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_261-471_0_3_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_261-471_0_3_node_23 | 0.4 | n |  | TRUE
20 | bus_LV_261-471_0_3_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_261-471_0_3_node_41 | 0.4 | n |  | TRUE
22 | bus_LV_261-471_0_3_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_261-471_0_3_node_29 | 0.4 | n |  | TRUE
24 | bus_LV_261-471_0_3_node_39 | 0.4 | n |  | TRUE
25 | bus_LV_261-471_0_3_node_36 | 0.4 | n |  | TRUE
26 | bus_LV_261-471_0_3_node_31 | 0.4 | n |  | TRUE
27 | bus_LV_261-471_0_3_node_40 | 0.4 | n |  | TRUE
28 | bus_LV_261-471_0_3_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_261-471_0_3_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_261-471_0_3_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_261-471_0_3_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_261-471_0_3_node_28 | 0.4 | n |  | TRUE
33 | bus_LV_261-471_0_3_node_24 | 0.4 | n |  | TRUE
34 | bus_LV_261-471_0_3_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_261-471_0_3_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_261-471_0_3_node_38 | 0.4 | n |  | TRUE
37 | bus_LV_261-471_0_3_node_32 | 0.4 | n |  | TRUE
38 | bus_LV_261-471_0_3_node_37 | 0.4 | n |  | TRUE
39 | bus_MV_549_0_node_118 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-471_0_3_load_0 | 0 | 0.0049889 | 0.0012503 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-471_0_3_load_35 | 3 | 0.00463 | 0.0011604 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-471_0_3_load_33 | 5 | 0.004061 | 0.0010178 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-471_0_3_load_34 | 6 | 0.0039947 | 0.0010012 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-471_0_3_load_30 | 7 | 0.0039384 | 0.00098705 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-471_0_3_load_18 | 9 | 0.029961 | 0.007509 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-471_0_3_load_15 | 11 | 0.0068039 | 0.0017052 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-471_0_3_load_42 | 13 | 0.01891 | 0.0047394 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-471_0_3_load_19 | 16 | 0.0027706 | 0.00069437 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-471_0_3_load_22 | 17 | 0.0026986 | 0.00067633 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-471_0_3_load_23 | 19 | 0.0066523 | 0.0016672 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-471_0_3_load_21 | 20 | 0.0050643 | 0.0012692 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-471_0_3_load_41 | 21 | 0.025625 | 0.0064221 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-471_0_3_load_29 | 23 | 0.071959 | 0.018035 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-471_0_3_load_36 | 25 | 0.0053986 | 0.001353 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-471_0_3_load_31 | 26 | 0.0038066 | 0.00095402 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-471_0_3_load_40 | 27 | 0.022756 | 0.0057033 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-471_0_3_load_16 | 28 | 0.0046768 | 0.0011721 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-471_0_3_load_20 | 29 | 0.0039234 | 0.00098329 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-471_0_3_load_17 | 30 | 0.0026965 | 0.0006758 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-471_0_3_load_27 | 31 | 0.0044697 | 0.0011202 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-471_0_3_load_28 | 32 | 0.024528 | 0.0061474 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-471_0_3_load_24 | 33 | 0.01662 | 0.0041653 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-471_0_3_load_25 | 34 | 0.0056568 | 0.0014177 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-471_0_3_load_26 | 35 | 0.0028979 | 0.00072629 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-471_0_3_load_38 | 36 | 0.0082499 | 0.0020676 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-471_0_3_load_32 | 37 | 0.0072156 | 0.0018084 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-471_0_3_load_37 | 38 | 0.0029348 | 0.00073554 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 22 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-471_0_3_line_0 |  | 0 | 1 | 0.051271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-471_0_3_line_1 |  | 1 | 2 | 0.0083646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-471_0_3_line_2 |  | 2 | 3 | 0.0054427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-471_0_3_line_3 |  | 3 | 5 | 0.01132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-471_0_3_line_4 |  | 4 | 5 | 0.011675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-471_0_3_line_5 |  | 4 | 6 | 0.028001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-471_0_3_line_6 |  | 4 | 7 | 0.012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-471_0_3_line_7 |  | 6 | 25 | 0.0045218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-471_0_3_line_8 |  | 7 | 26 | 0.011149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-471_0_3_line_9 |  | 8 | 9 | 0.055554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-471_0_3_line_10 |  | 8 | 10 | 0.0097627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-471_0_3_line_11 |  | 8 | 11 | 0.022581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-471_0_3_line_12 |  | 9 | 27 | 0.019092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-471_0_3_line_13 |  | 10 | 12 | 0.010247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-471_0_3_line_14 |  | 10 | 13 | 0.017613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-471_0_3_line_15 |  | 11 | 28 | 0.024187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-471_0_3_line_16 |  | 12 | 21 | 0.015273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-471_0_3_line_17 |  | 13 | 22 | 0.021854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-471_0_3_line_18 |  | 14 | 15 | 0.073048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-471_0_3_line_19 |  | 14 | 16 | 0.039629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-471_0_3_line_20 |  | 15 | 17 | 0.060479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-471_0_3_line_21 |  | 16 | 29 | 0.0011012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-471_0_3_line_22 |  | 17 | 30 | 7.3835e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-471_0_3_line_23 |  | 18 | 19 | 0.009423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-471_0_3_line_24 |  | 18 | 20 | 0.024325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-471_0_3_line_25 |  | 20 | 29 | 0.034499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-471_0_3_line_26 |  | 22 | 23 | 0.020065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-471_0_3_line_27 |  | 22 | 24 | 0.026212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-471_0_3_line_28 |  | 23 | 32 | 0.0237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-471_0_3_line_29 |  | 24 | 35 | 0.0098739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-471_0_3_line_30 |  | 24 | 36 | 0.018793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-471_0_3_line_31 |  | 25 | 38 | 0.010447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-471_0_3_line_32 |  | 26 | 37 | 0.011163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-471_0_3_line_33 |  | 28 | 30 | 0.021677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-471_0_3_line_34 |  | 31 | 32 | 0.020171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-471_0_3_line_35 |  | 33 | 34 | 0.025967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-471_0_3_line_36 |  | 34 | 35 | 0.017681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-471_0_3_line_37 |  | 36 | 38 | 0.0013039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-471_0_3_trafo_14 | 0.63 MVA 20/0.4 kV | 39 | 22 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2678946.6589 | 1249363.2926 | 2678946.0681 | 1249361.7281 | 2678926.2287 | 1249316.2705
1 | 2678946.6589 | 1249363.2926 | 2678950.8648 | 1249361.5918 | 2678954.4103 | 1249360.1491
2 | 2678954.4103 | 1249360.1491 | 2678952.2746 | 1249355.143
3 | 2678947.8327 | 1249344.7314 | 2678952.2746 | 1249355.143
4 | 2678943.2512 | 1249333.9925 | 2678947.8327 | 1249344.7314
5 | 2678943.2512 | 1249333.9925 | 2678969.0162 | 1249323.0289
6 | 2678943.2512 | 1249333.9925 | 2678938.4734 | 1249322.9849
7 | 2678973.177 | 1249321.2584 | 2678969.0162 | 1249323.0289
8 | 2678934.0342 | 1249312.7575 | 2678938.4734 | 1249322.9849
9 | 2679049.465 | 1249331.0722 | 2679045.6646 | 1249322.1817 | 2679027.8018 | 1249279.9157
10 | 2679040.4007 | 1249334.6984 | 2679045.4035 | 1249332.697 | 2679049.465 | 1249331.0722
11 | 2679049.465 | 1249331.0722 | 2679049.6848 | 1249331.5755 | 2679055.2059 | 1249344.4919 | 2679058.3062 | 1249351.8501
12 | 2679027.8018 | 1249279.9157 | 2679020.3695 | 1249262.3299
13 | 2679044.3748 | 1249344.1472 | 2679040.4007 | 1249334.6984
14 | 2679040.4007 | 1249334.6984 | 2679033.5675 | 1249318.4651
15 | 2679058.3062 | 1249351.8501 | 2679067.6976 | 1249374.1395
16 | 2679044.3748 | 1249344.1472 | 2679036.1082 | 1249347.4172 | 2679030.1254 | 1249349.6426
17 | 2679025.0892 | 1249298.3233 | 2679033.5675 | 1249318.4651
18 | 2679144.7926 | 1249409.9461 | 2679148.9336 | 1249422.1548 | 2679141.2863 | 1249429.3691 | 2679134.045 | 1249431.6297 | 2679131.6537 | 1249435.4116 | 2679129.7415 | 1249436.6759 | 2679127.6685 | 1249436.9818 | 2679124.1478 | 1249436.5679 | 2679117.9946 | 1249435.9408 | 2679115.3952 | 1249436.6511 | 2679113.6703 | 1249438.0291 | 2679107.0747 | 1249445.0907 | 2679103.9237 | 1249447.5171 | 2679099.6255 | 1249449.9171
19 | 2679144.7926 | 1249409.9461 | 2679135.1649 | 1249406.0147 | 2679126.706 | 1249389.1895 | 2679124.5208 | 1249379.0238
20 | 2679099.6255 | 1249449.9171 | 2679076.1428 | 1249394.1834
21 | 2679124.2893 | 1249377.9471 | 2679124.5208 | 1249379.0238
22 | 2679076.1428 | 1249394.1834 | 2679076.1141 | 1249394.1153
23 | 2679101.8455 | 1249325.4889 | 2679093.0698 | 1249328.9855
24 | 2679101.8455 | 1249325.4889 | 2679105.9689 | 1249335.6291 | 2679106.0768 | 1249342.8136 | 2679107.7634 | 1249347.7064 | 2679108.4994 | 1249348.4097
25 | 2679124.2893 | 1249377.9471 | 2679123.7983 | 1249375.663 | 2679117.6647 | 1249357.1676 | 2679108.4994 | 1249348.4097
26 | 2679025.0892 | 1249298.3233 | 2679017.3082 | 1249279.8289
27 | 2679001.0498 | 1249308.8439 | 2679003.9883 | 1249307.0596 | 2679025.0892 | 1249298.3233
28 | 2679017.3082 | 1249279.8289 | 2679008.1175 | 1249257.9835
29 | 2679001.0498 | 1249308.8439 | 2678997.1955 | 1249299.7533
30 | 2679001.0498 | 1249308.8439 | 2678997.9287 | 1249310.726 | 2678983.9899 | 1249316.6572
31 | 2678973.177 | 1249321.2584 | 2678982.7901 | 1249317.1678
32 | 2678929.5895 | 1249302.5175 | 2678934.0342 | 1249312.7575
33 | 2679076.1141 | 1249394.1153 | 2679067.6976 | 1249374.1395
34 | 2679000.2952 | 1249239.3908 | 2679008.1175 | 1249257.9835
35 | 2678990.2935 | 1249283.4747 | 2678980.1573 | 1249259.5677
36 | 2678997.1955 | 1249299.7533 | 2678990.2935 | 1249283.4747
37 | 2678983.9899 | 1249316.6572 | 2678982.7901 | 1249317.1678

## bus_geodata
| x | y | coords
0 | 2678926.2287 | 1249316.2705
1 | 2678946.6589 | 1249363.2926
2 | 2678954.4103 | 1249360.1491
3 | 2678952.2746 | 1249355.143
4 | 2678943.2512 | 1249333.9925
5 | 2678947.8327 | 1249344.7314
6 | 2678969.0162 | 1249323.0289
7 | 2678938.4734 | 1249322.9849
8 | 2679049.465 | 1249331.0722
9 | 2679027.8018 | 1249279.9157
10 | 2679040.4007 | 1249334.6984
11 | 2679058.3062 | 1249351.8501
12 | 2679044.3748 | 1249344.1472
13 | 2679033.5675 | 1249318.4651
14 | 2679144.7926 | 1249409.9461
15 | 2679099.6255 | 1249449.9171
16 | 2679124.5208 | 1249379.0238
17 | 2679076.1428 | 1249394.1834
18 | 2679101.8455 | 1249325.4889
19 | 2679093.0698 | 1249328.9855
20 | 2679108.4994 | 1249348.4097
21 | 2679030.1254 | 1249349.6426
22 | 2679025.0892 | 1249298.3233
23 | 2679017.3082 | 1249279.8289
24 | 2679001.0498 | 1249308.8439
25 | 2678973.177 | 1249321.2584
26 | 2678934.0342 | 1249312.7575
27 | 2679020.3695 | 1249262.3299
28 | 2679067.6976 | 1249374.1395
29 | 2679124.2893 | 1249377.9471
30 | 2679076.1141 | 1249394.1153
31 | 2679000.2952 | 1249239.3908
32 | 2679008.1175 | 1249257.9835
33 | 2678980.1573 | 1249259.5677
34 | 2678990.2935 | 1249283.4747
35 | 2678997.1955 | 1249299.7533
36 | 2678983.9899 | 1249316.6572
37 | 2678929.5895 | 1249302.5175
38 | 2678982.7901 | 1249317.1678
39 | 2679030.1831 | 1249296.2897

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99557 | -0.085245 | 0.0049889 | 0.0012503
1 | 0.9958 | -0.080747 | 0 | 0
2 | 0.99584 | -0.080013 | 0 | 0
3 | 0.99587 | -0.079536 | 0.00463 | 0.0011604
4 | 0.99611 | -0.074815 | 0 | 0
5 | 0.99596 | -0.077622 | 0.004061 | 0.0010178
6 | 0.99684 | -0.060736 | 0.0039947 | 0.0010012
7 | 0.99595 | -0.07797 | 0.0039384 | 0.00098705
8 | 0.99474 | -0.10088 | 0 | 0
9 | 0.99206 | -0.15261 | 0.029961 | 0.007509
10 | 0.99553 | -0.085759 | 0 | 0
11 | 0.99401 | -0.11493 | 0.0068039 | 0.0017052
12 | 0.99529 | -0.090378 | 0 | 0
13 | 0.99735 | -0.050623 | 0.01891 | 0.0047394
14 | 0.99065 | -0.17982 | 0 | 0
15 | 0.99189 | -0.15596 | 0 | 0
16 | 0.98999 | -0.19279 | 0.0027706 | 0.00069437
17 | 0.99291 | -0.13624 | 0.0026986 | 0.00067633
18 | 0.98945 | -0.20317 | 0 | 0
19 | 0.98939 | -0.20428 | 0.0066523 | 0.0016672
20 | 0.9896 | -0.20028 | 0.0050643 | 0.0012692
21 | 0.99493 | -0.097266 | 0.025625 | 0.0064221
22 | 1 | 0 | -0.31079 | -0.077953
23 | 0.99816 | -0.035372 | 0.071959 | 0.018035
24 | 0.99823 | -0.034051 | 0 | 0
25 | 0.99697 | -0.058148 | 0.0053986 | 0.001353
26 | 0.99583 | -0.080129 | 0.0038066 | 0.00095402
27 | 0.99167 | -0.16031 | 0.022756 | 0.0057033
28 | 0.99338 | -0.1271 | 0.0046768 | 0.0011721
29 | 0.98997 | -0.19309 | 0.0039234 | 0.00098329
30 | 0.99291 | -0.13622 | 0.0026965 | 0.0006758
31 | 0.99745 | -0.048982 | 0.0044697 | 0.0011202
32 | 0.99754 | -0.047402 | 0.024528 | 0.0061474
33 | 0.99725 | -0.052857 | 0.01662 | 0.0041653
34 | 0.99764 | -0.045296 | 0.0056568 | 0.0014177
35 | 0.998 | -0.038401 | 0.0028979 | 0.00072629
36 | 0.99738 | -0.050246 | 0.0082499 | 0.0020676
37 | 0.99576 | -0.081545 | 0.0072156 | 0.0018084
38 | 0.99734 | -0.051182 | 0.0029348 | 0.00073554
39 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0049889 | -0.0012503 | 0.00499 | 0.0012504 | 1.069e-06 | 1.7299e-08 | 0.0074566 | 0.0074564 | 0.0074566 | 0.99557 | -0.085245 | 0.9958 | -0.080747 | 2.0485
1 | -0.00499 | -0.0012504 | 0.0049901 | 0.0012504 | 1.7439e-07 | 2.7886e-09 | 0.0074564 | 0.0074563 | 0.0074564 | 0.9958 | -0.080747 | 0.99584 | -0.080013 | 2.0484
2 | -0.0049901 | -0.0012504 | 0.0049902 | 0.0012504 | 1.1347e-07 | 1.8094e-09 | 0.0074563 | 0.0074563 | 0.0074563 | 0.99584 | -0.080013 | 0.99587 | -0.079536 | 2.0484
3 | -0.0096203 | -0.0024108 | 0.0096212 | 0.0024112 | 8.7708e-07 | 4.1404e-07 | 0.014374 | 0.014374 | 0.014374 | 0.99587 | -0.079536 | 0.99596 | -0.077622 | 3.949
4 | 0.013684 | 0.00343 | -0.013682 | -0.0034289 | 1.8295e-06 | 1.0189e-06 | 0.020442 | 0.020442 | 0.020442 | 0.99611 | -0.074815 | 0.99596 | -0.077622 | 5.6159
5 | -0.028648 | -0.0071815 | 0.028668 | 0.0071934 | 1.9231e-05 | 1.1943e-05 | 0.042796 | 0.042796 | 0.042796 | 0.99611 | -0.074815 | 0.99684 | -0.060736 | 11.7572
6 | 0.014964 | 0.0037515 | -0.014962 | -0.0037502 | 2.2488e-06 | 1.283e-06 | 0.022355 | 0.022355 | 0.022355 | 0.99611 | -0.074815 | 0.99595 | -0.07797 | 6.1414
7 | -0.032662 | -0.0081946 | 0.032666 | 0.0081971 | 4.0314e-06 | 2.5212e-06 | 0.048759 | 0.048759 | 0.048759 | 0.99684 | -0.060736 | 0.99697 | -0.058148 | 13.3954
8 | 0.011024 | 0.0027632 | -0.011023 | -0.0027626 | 1.1342e-06 | 5.8083e-07 | 0.016471 | 0.016471 | 0.016471 | 0.99595 | -0.07797 | 0.99583 | -0.080129 | 4.5249
9 | 0.052856 | 0.0133 | -0.052726 | -0.013217 | 0.0001303 | 8.2672e-05 | 0.079085 | 0.079085 | 0.079085 | 0.99474 | -0.10088 | 0.99206 | -0.15261 | 21.7268
10 | -0.088248 | -0.022207 | 0.088312 | 0.022248 | 6.3829e-05 | 4.0724e-05 | 0.13204 | 0.13204 | 0.13204 | 0.99474 | -0.10088 | 0.99553 | -0.085759 | 36.275
11 | 0.035392 | 0.0089074 | -0.035368 | -0.0088925 | 2.3746e-05 | 1.4905e-05 | 0.052956 | 0.052956 | 0.052956 | 0.99474 | -0.10088 | 0.99401 | -0.11493 | 14.5483
12 | 0.022765 | 0.0057083 | -0.022756 | -0.0057033 | 8.3476e-06 | 5.0961e-06 | 0.034146 | 0.034146 | 0.034146 | 0.99206 | -0.15261 | 0.99167 | -0.16031 | 9.3808
13 | 0.025639 | 0.0064308 | -0.025633 | -0.0064273 | 5.6438e-06 | 3.4788e-06 | 0.038324 | 0.038324 | 0.038324 | 0.99553 | -0.085759 | 0.99529 | -0.090378 | 10.5286
14 | -0.11395 | -0.028679 | 0.11414 | 0.028801 | 0.0001917 | 0.00012246 | 0.17036 | 0.17036 | 0.17036 | 0.99553 | -0.085759 | 0.99735 | -0.050623 | 46.8036
15 | 0.028565 | 0.0071873 | -0.028548 | -0.007177 | 1.6592e-05 | 1.0306e-05 | 0.042771 | 0.042771 | 0.042771 | 0.99401 | -0.11493 | 0.99338 | -0.1271 | 11.7502
16 | 0.025633 | 0.0064273 | -0.025625 | -0.0064221 | 8.412e-06 | 5.1853e-06 | 0.038324 | 0.038324 | 0.038324 | 0.99529 | -0.090378 | 0.99493 | -0.097266 | 10.5286
17 | -0.13305 | -0.033541 | 0.13338 | 0.033747 | 0.00032316 | 0.00020654 | 0.19858 | 0.19858 | 0.19858 | 0.99735 | -0.050623 | 1 | 0 | 54.5545
18 | -0.018427 | -0.0046235 | 0.018448 | 0.004636 | 2.0989e-05 | 1.2491e-05 | 0.027681 | 0.02768 | 0.027681 | 0.99065 | -0.17982 | 0.99189 | -0.15596 | 7.6046
19 | 0.018427 | 0.0046235 | -0.018416 | -0.0046167 | 1.1387e-05 | 6.7777e-06 | 0.027681 | 0.027681 | 0.027681 | 0.99065 | -0.17982 | 0.98999 | -0.19279 | 7.6046
20 | -0.018448 | -0.004636 | 0.018466 | 0.0046463 | 1.7377e-05 | 1.034e-05 | 0.02768 | 0.02768 | 0.02768 | 0.99189 | -0.15596 | 0.99291 | -0.13624 | 7.6045
21 | 0.015645 | 0.0039224 | -0.015645 | -0.0039222 | 2.2838e-07 | 1.32e-07 | 0.023517 | 0.023517 | 0.023517 | 0.98999 | -0.19279 | 0.98997 | -0.19309 | 6.4606
22 | -0.021164 | -0.0053227 | 0.021164 | 0.0053227 | 2.7868e-08 | 1.6879e-08 | 0.031724 | 0.031724 | 0.031724 | 0.99291 | -0.13624 | 0.99291 | -0.13622 | 8.7155
23 | 0.0066526 | 0.0016673 | -0.0066523 | -0.0016672 | 3.537e-07 | 1.0535e-07 | 0.010005 | 0.010005 | 0.010005 | 0.98945 | -0.20317 | 0.98939 | -0.20428 | 2.7486
24 | -0.0066526 | -0.0016673 | 0.0066535 | 0.0016676 | 9.1305e-07 | 2.7187e-07 | 0.010005 | 0.010005 | 0.010005 | 0.98945 | -0.20317 | 0.9896 | -0.20028 | 2.7486
25 | -0.011718 | -0.0029368 | 0.011722 | 0.0029389 | 4.0163e-06 | 2.127e-06 | 0.01762 | 0.017619 | 0.01762 | 0.9896 | -0.20028 | 0.98997 | -0.19309 | 4.8405
26 | 0.10114 | 0.025421 | -0.10097 | -0.025313 | 0.00017049 | 0.00010885 | 0.15053 | 0.15053 | 0.15053 | 1 | 0 | 0.99816 | -0.035372 | 41.3545
27 | 0.074617 | 0.018784 | -0.074495 | -0.018707 | 0.00012124 | 7.7251e-05 | 0.11106 | 0.11106 | 0.11106 | 1 | 0 | 0.99823 | -0.034051 | 30.511
28 | 0.029015 | 0.0072779 | -0.028998 | -0.0072676 | 1.663e-05 | 1.0333e-05 | 0.043257 | 0.043257 | 0.043257 | 0.99816 | -0.035372 | 0.99754 | -0.047402 | 11.8837
29 | 0.025193 | 0.0063205 | -0.025188 | -0.0063173 | 5.2227e-06 | 3.2135e-06 | 0.037556 | 0.037557 | 0.037557 | 0.99823 | -0.034051 | 0.998 | -0.038401 | 10.3177
30 | 0.049302 | 0.012387 | -0.049264 | -0.012362 | 3.8075e-05 | 2.4123e-05 | 0.073504 | 0.073504 | 0.073504 | 0.99823 | -0.034051 | 0.99738 | -0.050246 | 20.1933
31 | -0.038065 | -0.0095501 | 0.038078 | 0.0095581 | 1.2647e-05 | 7.9578e-06 | 0.056817 | 0.056817 | 0.056817 | 0.99697 | -0.058148 | 0.99734 | -0.051182 | 15.609
32 | 0.0072161 | 0.0018086 | -0.0072156 | -0.0018084 | 4.867e-07 | 1.6627e-07 | 0.010783 | 0.010783 | 0.010783 | 0.99583 | -0.080129 | 0.99576 | -0.081545 | 2.9623
33 | 0.023871 | 0.0060049 | -0.023861 | -0.0059985 | 1.0398e-05 | 6.3742e-06 | 0.035765 | 0.035765 | 0.035765 | 0.99338 | -0.1271 | 0.99291 | -0.13622 | 9.8257
34 | -0.0044697 | -0.0011202 | 0.00447 | 0.0011202 | 3.3631e-07 | -4.8071e-08 | 0.0066679 | 0.0066678 | 0.0066679 | 0.99745 | -0.048982 | 0.99754 | -0.047402 | 1.8318
35 | -0.01662 | -0.0041653 | 0.016626 | 0.0041688 | 5.9883e-06 | 3.4936e-06 | 0.024799 | 0.024798 | 0.024799 | 0.99725 | -0.052857 | 0.99764 | -0.045296 | 6.8128
36 | -0.022283 | -0.0055865 | 0.02229 | 0.005591 | 7.3242e-06 | 4.4565e-06 | 0.033236 | 0.033236 | 0.033236 | 0.99764 | -0.045296 | 0.998 | -0.038401 | 9.1307
37 | 0.041014 | 0.010295 | -0.041012 | -0.010294 | 1.8312e-06 | 1.1549e-06 | 0.061196 | 0.061196 | 0.061196 | 0.99738 | -0.050246 | 0.99734 | -0.051182 | 16.812

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.31079 | 0.077953

## res_load
| p_mw | q_mvar
0 | 0.0049889 | 0.0012503
1 | 0.00463 | 0.0011604
2 | 0.004061 | 0.0010178
3 | 0.0039947 | 0.0010012
4 | 0.0039384 | 0.00098705
5 | 0.029961 | 0.007509
6 | 0.0068039 | 0.0017052
7 | 0.01891 | 0.0047394
8 | 0.0027706 | 0.00069437
9 | 0.0026986 | 0.00067633
10 | 0.0066523 | 0.0016672
11 | 0.0050643 | 0.0012692
12 | 0.025625 | 0.0064221
13 | 0.071959 | 0.018035
14 | 0.0053986 | 0.001353
15 | 0.0038066 | 0.00095402
16 | 0.022756 | 0.0057033
17 | 0.0046768 | 0.0011721
18 | 0.0039234 | 0.00098329
19 | 0.0026965 | 0.0006758
20 | 0.0044697 | 0.0011202
21 | 0.024528 | 0.0061474
22 | 0.01662 | 0.0041653
23 | 0.0056568 | 0.0014177
24 | 0.0028979 | 0.00072629
25 | 0.0082499 | 0.0020676
26 | 0.0072156 | 0.0018084
27 | 0.0029348 | 0.00073554

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1