## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-476_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-476_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-476_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-476_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-476_0_3_node_41 | 0.4 | n |  | TRUE
5 | bus_LV_261-476_0_3_node_31 | 0.4 | n |  | TRUE
6 | bus_LV_261-476_0_3_node_97 | 0.4 | n |  | TRUE
7 | bus_LV_261-476_0_3_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_261-476_0_3_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_261-476_0_3_node_50 | 0.4 | n |  | TRUE
10 | bus_LV_261-476_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_261-476_0_3_node_104 | 0.4 | n |  | TRUE
12 | bus_LV_261-476_0_3_node_106 | 0.4 | n |  | TRUE
13 | bus_LV_261-476_0_3_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_261-476_0_3_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_261-476_0_3_node_72 | 0.4 | n |  | TRUE
16 | bus_LV_261-476_0_3_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_261-476_0_3_node_76 | 0.4 | n |  | TRUE
18 | bus_LV_261-476_0_3_node_74 | 0.4 | n |  | TRUE
19 | bus_LV_261-476_0_3_node_58 | 0.4 | n |  | TRUE
20 | bus_LV_261-476_0_3_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_261-476_0_3_node_49 | 0.4 | n |  | TRUE
22 | bus_LV_261-476_0_3_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_261-476_0_3_node_96 | 0.4 | n |  | TRUE
24 | bus_LV_261-476_0_3_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_261-476_0_3_node_61 | 0.4 | n |  | TRUE
26 | bus_LV_261-476_0_3_node_59 | 0.4 | n |  | TRUE
27 | bus_LV_261-476_0_3_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_261-476_0_3_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_261-476_0_3_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_261-476_0_3_node_46 | 0.4 | n |  | TRUE
31 | bus_LV_261-476_0_3_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_261-476_0_3_node_95 | 0.4 | n |  | TRUE
33 | bus_LV_261-476_0_3_node_94 | 0.4 | n |  | TRUE
34 | bus_LV_261-476_0_3_node_17 | 0.4 | n |  | TRUE
35 | bus_LV_261-476_0_3_node_118 | 0.4 | n |  | TRUE
36 | bus_LV_261-476_0_3_node_18 | 0.4 | n |  | TRUE
37 | bus_LV_261-476_0_3_node_116 | 0.4 | n |  | TRUE
38 | bus_LV_261-476_0_3_node_47 | 0.4 | n |  | TRUE
39 | bus_LV_261-476_0_3_node_45 | 0.4 | n |  | TRUE
40 | bus_LV_261-476_0_3_node_98 | 0.4 | n |  | TRUE
41 | bus_LV_261-476_0_3_node_20 | 0.4 | n |  | TRUE
42 | bus_LV_261-476_0_3_node_92 | 0.4 | n |  | TRUE
43 | bus_LV_261-476_0_3_node_21 | 0.4 | n |  | TRUE
44 | bus_LV_261-476_0_3_node_66 | 0.4 | n |  | TRUE
45 | bus_LV_261-476_0_3_node_65 | 0.4 | n |  | TRUE
46 | bus_LV_261-476_0_3_node_22 | 0.4 | n |  | TRUE
47 | bus_LV_261-476_0_3_node_52 | 0.4 | n |  | TRUE
48 | bus_LV_261-476_0_3_node_127 | 0.4 | n |  | TRUE
49 | bus_LV_261-476_0_3_node_23 | 0.4 | n |  | TRUE
50 | bus_LV_261-476_0_3_node_93 | 0.4 | n |  | TRUE
51 | bus_LV_261-476_0_3_node_55 | 0.4 | n |  | TRUE
52 | bus_LV_261-476_0_3_node_26 | 0.4 | n |  | TRUE
53 | bus_LV_261-476_0_3_node_30 | 0.4 | n |  | TRUE
54 | bus_LV_261-476_0_3_node_110 | 0.4 | n |  | TRUE
55 | bus_LV_261-476_0_3_node_27 | 0.4 | n |  | TRUE
56 | bus_LV_261-476_0_3_node_42 | 0.4 | n |  | TRUE
57 | bus_LV_261-476_0_3_node_28 | 0.4 | n |  | TRUE
58 | bus_LV_261-476_0_3_node_139 | 0.4 | n |  | TRUE
59 | bus_LV_261-476_0_3_node_129 | 0.4 | n |  | TRUE
60 | bus_LV_261-476_0_3_node_29 | 0.4 | n |  | TRUE
61 | bus_LV_261-476_0_3_node_128 | 0.4 | n |  | TRUE
62 | bus_LV_261-476_0_3_node_44 | 0.4 | n |  | TRUE
63 | bus_LV_261-476_0_3_node_124 | 0.4 | n |  | TRUE
64 | bus_LV_261-476_0_3_node_123 | 0.4 | n |  | TRUE
65 | bus_LV_261-476_0_3_node_112 | 0.4 | n |  | TRUE
66 | bus_LV_261-476_0_3_node_32 | 0.4 | n |  | TRUE
67 | bus_LV_261-476_0_3_node_40 | 0.4 | n |  | TRUE
68 | bus_LV_261-476_0_3_node_100 | 0.4 | n |  | TRUE
69 | bus_LV_261-476_0_3_node_35 | 0.4 | n |  | TRUE
70 | bus_LV_261-476_0_3_node_36 | 0.4 | n |  | TRUE
71 | bus_LV_261-476_0_3_node_90 | 0.4 | n |  | TRUE
72 | bus_LV_261-476_0_3_node_39 | 0.4 | n |  | TRUE
73 | bus_LV_261-476_0_3_node_84 | 0.4 | n |  | TRUE
74 | bus_LV_261-476_0_3_node_37 | 0.4 | n |  | TRUE
75 | bus_LV_261-476_0_3_node_101 | 0.4 | n |  | TRUE
76 | bus_LV_261-476_0_3_node_38 | 0.4 | n |  | TRUE
77 | bus_LV_261-476_0_3_node_78 | 0.4 | n |  | TRUE
78 | bus_LV_261-476_0_3_node_86 | 0.4 | n |  | TRUE
79 | bus_LV_261-476_0_3_node_69 | 0.4 | n |  | TRUE
80 | bus_LV_261-476_0_3_node_67 | 0.4 | n |  | TRUE
81 | bus_LV_261-476_0_3_node_111 | 0.4 | n |  | TRUE
82 | bus_LV_261-476_0_3_node_134 | 0.4 | n |  | TRUE
83 | bus_LV_261-476_0_3_node_135 | 0.4 | n |  | TRUE
84 | bus_LV_261-476_0_3_node_48 | 0.4 | n |  | TRUE
85 | bus_LV_261-476_0_3_node_103 | 0.4 | n |  | TRUE
86 | bus_LV_261-476_0_3_node_105 | 0.4 | n |  | TRUE
87 | bus_LV_261-476_0_3_node_73 | 0.4 | n |  | TRUE
88 | bus_LV_261-476_0_3_node_56 | 0.4 | n |  | TRUE
89 | bus_LV_261-476_0_3_node_57 | 0.4 | n |  | TRUE
90 | bus_LV_261-476_0_3_node_64 | 0.4 | n |  | TRUE
91 | bus_LV_261-476_0_3_node_122 | 0.4 | n |  | TRUE
92 | bus_LV_261-476_0_3_node_121 | 0.4 | n |  | TRUE
93 | bus_LV_261-476_0_3_node_108 | 0.4 | n |  | TRUE
94 | bus_LV_261-476_0_3_node_60 | 0.4 | n |  | TRUE
95 | bus_LV_261-476_0_3_node_91 | 0.4 | n |  | TRUE
96 | bus_LV_261-476_0_3_node_120 | 0.4 | n |  | TRUE
97 | bus_LV_261-476_0_3_node_114 | 0.4 | n |  | TRUE
98 | bus_LV_261-476_0_3_node_131 | 0.4 | n |  | TRUE
99 | bus_LV_261-476_0_3_node_130 | 0.4 | n |  | TRUE
100 | bus_LV_261-476_0_3_node_54 | 0.4 | n |  | TRUE
101 | bus_LV_261-476_0_3_node_51 | 0.4 | n |  | TRUE
102 | bus_LV_261-476_0_3_node_109 | 0.4 | n |  | TRUE
103 | bus_LV_261-476_0_3_node_43 | 0.4 | n |  | TRUE
104 | bus_LV_261-476_0_3_node_125 | 0.4 | n |  | TRUE
105 | bus_LV_261-476_0_3_node_119 | 0.4 | n |  | TRUE
106 | bus_LV_261-476_0_3_node_99 | 0.4 | n |  | TRUE
107 | bus_LV_261-476_0_3_node_80 | 0.4 | n |  | TRUE
108 | bus_LV_261-476_0_3_node_83 | 0.4 | n |  | TRUE
109 | bus_LV_261-476_0_3_node_82 | 0.4 | n |  | TRUE
110 | bus_LV_261-476_0_3_node_79 | 0.4 | n |  | TRUE
111 | bus_LV_261-476_0_3_node_87 | 0.4 | n |  | TRUE
112 | bus_LV_261-476_0_3_node_89 | 0.4 | n |  | TRUE
113 | bus_LV_261-476_0_3_node_88 | 0.4 | n |  | TRUE
114 | bus_LV_261-476_0_3_node_102 | 0.4 | n |  | TRUE
115 | bus_LV_261-476_0_3_node_85 | 0.4 | n |  | TRUE
116 | bus_LV_261-476_0_3_node_68 | 0.4 | n |  | TRUE
117 | bus_LV_261-476_0_3_node_137 | 0.4 | n |  | TRUE
118 | bus_LV_261-476_0_3_node_140 | 0.4 | n |  | TRUE
119 | bus_LV_261-476_0_3_node_136 | 0.4 | n |  | TRUE
120 | bus_LV_261-476_0_3_node_141 | 0.4 | n |  | TRUE
121 | bus_LV_261-476_0_3_node_142 | 0.4 | n |  | TRUE
122 | bus_LV_261-476_0_3_node_62 | 0.4 | n |  | TRUE
123 | bus_LV_261-476_0_3_node_138 | 0.4 | n |  | TRUE
124 | bus_LV_261-476_0_3_node_70 | 0.4 | n |  | TRUE
125 | bus_LV_261-476_0_3_node_71 | 0.4 | n |  | TRUE
126 | bus_LV_261-476_0_3_node_132 | 0.4 | n |  | TRUE
127 | bus_LV_261-476_0_3_node_133 | 0.4 | n |  | TRUE
128 | bus_LV_261-476_0_3_node_75 | 0.4 | n |  | TRUE
129 | bus_LV_261-476_0_3_node_77 | 0.4 | n |  | TRUE
130 | bus_LV_261-476_0_3_node_107 | 0.4 | n |  | TRUE
131 | bus_LV_261-476_0_3_node_81 | 0.4 | n |  | TRUE
132 | bus_LV_261-476_0_3_node_113 | 0.4 | n |  | TRUE
133 | bus_LV_261-476_0_3_node_115 | 0.4 | n |  | TRUE
134 | bus_LV_261-476_0_3_node_117 | 0.4 | n |  | TRUE
135 | bus_LV_261-476_0_3_node_126 | 0.4 | n |  | TRUE
136 | bus_MV_359_0_node_59 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-476_0_3_load_0 | 0 | 0.0044984 | 0.0011274 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-476_0_3_load_97 | 6 | 0.00077471 | 0.00019416 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-476_0_3_load_50 | 9 | 0.00060261 | 0.00015103 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-476_0_3_load_104 | 11 | 0.0028146 | 0.0007054 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-476_0_3_load_106 | 12 | 0.0014772 | 0.00037022 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-476_0_3_load_72 | 15 | 0.0019255 | 0.00048258 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-476_0_3_load_74 | 18 | 0.0018358 | 0.00046009 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-476_0_3_load_58 | 19 | 0.0019199 | 0.00048118 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-476_0_3_load_49 | 21 | 0.0090666 | 0.0022723 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-476_0_3_load_96 | 23 | 0.0043288 | 0.0010849 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-476_0_3_load_61 | 25 | 0.0027612 | 0.00069201 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-476_0_3_load_59 | 26 | 0.0045105 | 0.0011304 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-476_0_3_load_46 | 30 | 0.00279 | 0.00069923 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-476_0_3_load_95 | 32 | 0.002843 | 0.00071252 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-476_0_3_load_94 | 33 | 0.053735 | 0.013467 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-476_0_3_load_118 | 35 | 0.00037364 | 9.3642e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-476_0_3_load_116 | 37 | 0.00049508 | 0.00012408 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-476_0_3_load_47 | 38 | 0.00034003 | 8.522e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-476_0_3_load_45 | 39 | 0.0019848 | 0.00049744 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-476_0_3_load_98 | 40 | 0.0013301 | 0.00033335 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-476_0_3_load_92 | 42 | 0.0015679 | 0.00039296 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-476_0_3_load_65 | 45 | 0.051962 | 0.013023 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-476_0_3_load_127 | 48 | 0.00045857 | 0.00011493 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-476_0_3_load_55 | 51 | 0.0016119 | 0.00040398 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-476_0_3_load_110 | 54 | 0.0027555 | 0.0006906 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-476_0_3_load_42 | 56 | 0.00332 | 0.00083206 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-476_0_3_load_139 | 58 | 0.0028664 | 0.00071839 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-476_0_3_load_128 | 61 | 0.0020105 | 0.00050387 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-476_0_3_load_44 | 62 | 0.0019426 | 0.00048686 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-476_0_3_load_123 | 64 | 0.0018423 | 0.00046172 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-476_0_3_load_112 | 65 | 0.00060346 | 0.00015124 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-476_0_3_load_100 | 68 | 0.00090144 | 0.00022592 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-476_0_3_load_90 | 71 | 0.0016409 | 0.00041124 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-476_0_3_load_84 | 73 | 0.00085427 | 0.0002141 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-476_0_3_load_101 | 75 | 0.001732 | 0.00043407 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-476_0_3_load_86 | 78 | 0.0017238 | 0.00043204 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-476_0_3_load_69 | 79 | 0.0012067 | 0.00030242 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-476_0_3_load_67 | 80 | 0.0013357 | 0.00033476 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-476_0_3_load_111 | 81 | 0.00060827 | 0.00015245 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-476_0_3_load_134 | 82 | 0.0013392 | 0.00033562 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-476_0_3_load_48 | 84 | 0.011084 | 0.002778 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-476_0_3_load_103 | 85 | 0.00094237 | 0.00023618 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-476_0_3_load_105 | 86 | 0.0010281 | 0.00025767 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-476_0_3_load_64 | 90 | 0.0004385 | 0.0001099 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-476_0_3_load_122 | 91 | 0.0059943 | 0.0015023 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-476_0_3_load_121 | 92 | 0.0075436 | 0.0018906 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-476_0_3_load_108 | 93 | 0.0031156 | 0.00078084 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-476_0_3_load_60 | 94 | 0.0043206 | 0.0010828 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-476_0_3_load_91 | 95 | 0.00092132 | 0.0002309 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-476_0_3_load_120 | 96 | 0.00031622 | 7.9252e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-476_0_3_load_114 | 97 | 0.00066193 | 0.0001659 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-476_0_3_load_131 | 98 | 0.0019211 | 0.00048148 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-476_0_3_load_51 | 101 | 0.013741 | 0.0034438 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-476_0_3_load_109 | 102 | 0.0031417 | 0.00078738 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-476_0_3_load_43 | 103 | 0.0019266 | 0.00048284 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-476_0_3_load_125 | 104 | 0.0011544 | 0.00028932 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-476_0_3_load_119 | 105 | 0.00051735 | 0.00012966 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-476_0_3_load_99 | 106 | 0.00070659 | 0.00017709 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-476_0_3_load_82 | 109 | 0.0009738 | 0.00024406 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-476_0_3_load_87 | 111 | 0.0016181 | 0.00040554 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-476_0_3_load_88 | 113 | 0.0010725 | 0.00026879 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-476_0_3_load_102 | 114 | 0.0014074 | 0.00035273 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-476_0_3_load_85 | 115 | 0.0010441 | 0.00026167 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-476_0_3_load_140 | 118 | 0.0016564 | 0.00041514 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-476_0_3_load_141 | 120 | 0.0013379 | 0.00033532 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-476_0_3_load_142 | 121 | 0.00098782 | 0.00024757 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-476_0_3_load_62 | 122 | 0.00020514 | 5.1414e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-476_0_3_load_138 | 123 | 0.0019307 | 0.00048387 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-476_0_3_load_71 | 125 | 0.0013873 | 0.0003477 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-476_0_3_load_132 | 126 | 0.0012415 | 0.00031115 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-476_0_3_load_133 | 127 | 0.0011099 | 0.00027817 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-476_0_3_load_77 | 129 | 0.00098909 | 0.00024789 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-476_0_3_load_107 | 130 | 0.0047104 | 0.0011805 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-476_0_3_load_81 | 131 | 0.0011281 | 0.00028273 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-476_0_3_load_113 | 132 | 0.00057764 | 0.00014477 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-476_0_3_load_115 | 133 | 0.00061139 | 0.00015323 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-476_0_3_load_117 | 134 | 0.00058592 | 0.00014685 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-476_0_3_load_126 | 135 | 0.00051005 | 0.00012783 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 25 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-476_0_3_line_0 |  | 0 | 1 | 0.041303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-476_0_3_line_1 |  | 0 | 2 | 0.03045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-476_0_3_line_2 |  | 1 | 3 | 0.00258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-476_0_3_line_3 |  | 2 | 4 | 0.074424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-476_0_3_line_4 |  | 3 | 5 | 0.025567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-476_0_3_line_5 |  | 3 | 6 | 0.012067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-476_0_3_line_6 |  | 4 | 82 | 0.013005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-476_0_3_line_7 |  | 4 | 83 | 0.017066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-476_0_3_line_8 |  | 5 | 65 | 0.024808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-476_0_3_line_9 |  | 5 | 13 | 0.053402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-476_0_3_line_10 |  | 7 | 8 | 0.019832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_261-476_0_3_line_11 |  | 7 | 9 | 0.027654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_261-476_0_3_line_12 |  | 8 | 19 | 0.020854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_261-476_0_3_line_13 |  | 9 | 21 | 0.030549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_261-476_0_3_line_14 |  | 10 | 11 | 0.06209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-476_0_3_line_15 |  | 10 | 12 | 0.084704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-476_0_3_line_16 |  | 11 | 85 | 0.060982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-476_0_3_line_17 |  | 12 | 86 | 0.039888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-476_0_3_line_18 |  | 13 | 14 | 0.061969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_261-476_0_3_line_19 |  | 13 | 15 | 0.025261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_261-476_0_3_line_20 |  | 14 | 22 | 0.11758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-476_0_3_line_21 |  | 14 | 23 | 0.019088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-476_0_3_line_22 |  | 14 | 20 | 0.023299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_261-476_0_3_line_23 |  | 15 | 87 | 0.039609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_261-476_0_3_line_24 |  | 16 | 17 | 0.009742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-476_0_3_line_25 |  | 16 | 18 | 0.024056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-476_0_3_line_26 |  | 17 | 77 | 0.01428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-476_0_3_line_27 |  | 18 | 87 | 0.015577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_261-476_0_3_line_28 |  | 19 | 28 | 0.0094225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_261-476_0_3_line_29 |  | 20 | 21 | 0.038748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_261-476_0_3_line_30 |  | 22 | 40 | 0.029128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-476_0_3_line_31 |  | 23 | 49 | 0.013766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-476_0_3_line_32 |  | 24 | 25 | 0.036157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-476_0_3_line_33 |  | 24 | 26 | 0.0223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-476_0_3_line_34 |  | 25 | 93 | 0.024427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_261-476_0_3_line_35 |  | 26 | 94 | 0.029947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-476_0_3_line_36 |  | 27 | 28 | 0.022726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_261-476_0_3_line_37 |  | 27 | 29 | 0.018623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_261-476_0_3_line_38 |  | 27 | 30 | 0.060646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-476_0_3_line_39 |  | 28 | 51 | 0.0014843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-476_0_3_line_40 |  | 29 | 52 | 0.050348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-476_0_3_line_41 |  | 29 | 53 | 0.023161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-476_0_3_line_42 |  | 29 | 54 | 0.0068936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_261-476_0_3_line_43 |  | 31 | 32 | 0.01476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-476_0_3_line_44 |  | 31 | 33 | 0.014854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-476_0_3_line_45 |  | 32 | 50 | 0.0082539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-476_0_3_line_46 |  | 33 | 41 | 0.015715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-476_0_3_line_47 |  | 34 | 35 | 0.023291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-476_0_3_line_48 |  | 34 | 36 | 0.016828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-476_0_3_line_49 |  | 34 | 37 | 0.0080394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-476_0_3_line_50 |  | 35 | 96 | 0.023358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-476_0_3_line_51 |  | 36 | 38 | 0.034467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-476_0_3_line_52 |  | 36 | 39 | 0.025511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-476_0_3_line_53 |  | 37 | 97 | 0.022055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-476_0_3_line_54 |  | 38 | 84 | 0.026035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-476_0_3_line_55 |  | 41 | 42 | 0.012322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-476_0_3_line_56 |  | 42 | 95 | 0.024053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-476_0_3_line_57 |  | 43 | 44 | 0.032383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-476_0_3_line_58 |  | 43 | 45 | 0.017299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-476_0_3_line_59 |  | 44 | 98 | 0.011206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-476_0_3_line_60 |  | 44 | 99 | 0.015874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-476_0_3_line_61 |  | 46 | 47 | 0.055639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-476_0_3_line_62 |  | 46 | 48 | 0.049236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-476_0_3_line_63 |  | 47 | 100 | 0.13834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-476_0_3_line_64 |  | 47 | 101 | 0.29139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-476_0_3_line_65 |  | 48 | 55 | 0.040236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-476_0_3_line_66 |  | 49 | 50 | 0.003996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-476_0_3_line_67 |  | 51 | 88 | 0.0039043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-476_0_3_line_68 |  | 52 | 55 | 0.070049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-476_0_3_line_69 |  | 52 | 56 | 0.01734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-476_0_3_line_70 |  | 53 | 63 | 0.011401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-476_0_3_line_71 |  | 53 | 64 | 0.014684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-476_0_3_line_72 |  | 54 | 102 | 0.024596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
73 | LV_261-476_0_3_line_73 |  | 56 | 103 | 0.020339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-476_0_3_line_74 |  | 57 | 58 | 0.007545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-476_0_3_line_75 |  | 57 | 59 | 0.005976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-476_0_3_line_76 |  | 59 | 99 | 0.008856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-476_0_3_line_77 |  | 59 | 61 | 0.01431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-476_0_3_line_78 |  | 60 | 61 | 0.017176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-476_0_3_line_79 |  | 60 | 62 | 0.02876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-476_0_3_line_80 |  | 62 | 103 | 0.016058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_261-476_0_3_line_81 |  | 63 | 104 | 0.0096788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-476_0_3_line_82 |  | 64 | 105 | 0.019217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_261-476_0_3_line_83 |  | 65 | 81 | 0.015799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_261-476_0_3_line_84 |  | 66 | 67 | 0.004234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_261-476_0_3_line_85 |  | 66 | 68 | 0.0085695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_261-476_0_3_line_86 |  | 67 | 81 | 0.04085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_261-476_0_3_line_87 |  | 67 | 74 | 0.1052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_261-476_0_3_line_88 |  | 68 | 106 | 0.015381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_261-476_0_3_line_89 |  | 69 | 70 | 0.050712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_261-476_0_3_line_90 |  | 69 | 71 | 0.001751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_261-476_0_3_line_91 |  | 70 | 72 | 0.09008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_261-476_0_3_line_92 |  | 70 | 73 | 0.021188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_261-476_0_3_line_93 |  | 71 | 112 | 0.0079088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_261-476_0_3_line_94 |  | 72 | 79 | 0.01552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_261-476_0_3_line_95 |  | 72 | 80 | 0.016883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_261-476_0_3_line_96 |  | 73 | 115 | 0.020443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_261-476_0_3_line_97 |  | 74 | 75 | 0.02102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_261-476_0_3_line_98 |  | 76 | 77 | 0.009898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_261-476_0_3_line_99 |  | 76 | 78 | 0.025218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_261-476_0_3_line_100 |  | 78 | 108 | 0.025437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_261-476_0_3_line_101 |  | 80 | 116 | 0.0074221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_261-476_0_3_line_102 |  | 83 | 117 | 0.00582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_261-476_0_3_line_103 |  | 83 | 118 | 0.01143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_261-476_0_3_line_104 |  | 85 | 114 | 0.032254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_261-476_0_3_line_105 |  | 86 | 110 | 0.077044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_261-476_0_3_line_106 |  | 87 | 128 | 0.009665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_261-476_0_3_line_107 |  | 88 | 89 | 0.018358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_261-476_0_3_line_108 |  | 89 | 90 | 0.0189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_261-476_0_3_line_109 |  | 91 | 92 | 0.022808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-476_0_3_line_110 |  | 92 | 96 | 0.023307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_261-476_0_3_line_111 |  | 93 | 102 | 0.025946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
112 | LV_261-476_0_3_line_112 |  | 97 | 132 | 0.023338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_261-476_0_3_line_113 |  | 99 | 123 | 0.011214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_261-476_0_3_line_114 |  | 100 | 122 | 0.060561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_261-476_0_3_line_115 |  | 104 | 135 | 0.04826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_261-476_0_3_line_116 |  | 105 | 134 | 0.021078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_261-476_0_3_line_117 |  | 107 | 108 | 0.023365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_261-476_0_3_line_118 |  | 107 | 109 | 0.012366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_261-476_0_3_line_119 |  | 107 | 110 | 0.08253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_261-476_0_3_line_120 |  | 108 | 111 | 0.031387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_261-476_0_3_line_121 |  | 109 | 131 | 0.020916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_261-476_0_3_line_122 |  | 110 | 130 | 0.005671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_261-476_0_3_line_123 |  | 111 | 113 | 0.024366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_261-476_0_3_line_124 |  | 112 | 113 | 0.016372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_261-476_0_3_line_125 |  | 116 | 124 | 0.007914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_261-476_0_3_line_126 |  | 116 | 125 | 0.01907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_261-476_0_3_line_127 |  | 117 | 121 | 0.007464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_261-476_0_3_line_128 |  | 117 | 119 | 0.028951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_261-476_0_3_line_129 |  | 119 | 120 | 0.009151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_261-476_0_3_line_130 |  | 124 | 126 | 0.022978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_261-476_0_3_line_131 |  | 124 | 127 | 0.008917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_261-476_0_3_line_132 |  | 128 | 129 | 0.013632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_261-476_0_3_line_133 |  | 132 | 133 | 0.021762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_261-476_0_3_line_134 |  | 133 | 134 | 0.029828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-476_0_3_trafo_61 | 0.63 MVA 20/0.4 kV | 136 | 25 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17
0 | 2681739.1074 | 1243635.5401 | 2681759.7163 | 1243636.2912 | 2681770.7394 | 1243637.1771 | 2681780.3139 | 1243638.1261
1 | 2681810.6158 | 1243641.1295 | 2681780.3139 | 1243638.1261
2 | 2681739.143 | 1243632.961 | 2681739.1074 | 1243635.5401
3 | 2681810.6158 | 1243641.1295 | 2681802.4658 | 1243600.7324 | 2681779.8463 | 1243598.8749 | 2681769.7987 | 1243595.7675
4 | 2681739.143 | 1243632.961 | 2681713.5019 | 1243632.6298
5 | 2681739.143 | 1243632.961 | 2681743.9064 | 1243621.8741
6 | 2681769.7987 | 1243595.7675 | 2681764.6003 | 1243607.6934
7 | 2681763.7203 | 1243581.618 | 2681766.1484 | 1243594.6386 | 2681769.7987 | 1243595.7675
8 | 2681713.5019 | 1243632.6298 | 2681715.2931 | 1243607.8869
9 | 2681713.5019 | 1243632.6298 | 2681709.92 | 1243632.5805 | 2681709.9273 | 1243639.7302 | 2681709.8485 | 1243646.5451 | 2681709.5903 | 1243669.6694 | 2681709.4983 | 1243677.9964 | 2681713.8944 | 1243678.2015
10 | 2681661.9145 | 1243804.5328 | 2681664.2879 | 1243804.521 | 2681667.7641 | 1243814.9875 | 2681670.3055 | 1243820.8934
11 | 2681661.9145 | 1243804.5328 | 2681661.7419 | 1243797.8589 | 2681661.1528 | 1243776.8897
12 | 2681670.3055 | 1243820.8934 | 2681674.9447 | 1243828.6851 | 2681675.4965 | 1243840.4575
13 | 2681661.1528 | 1243776.8897 | 2681660.6007 | 1243757.2361 | 2681660.4794 | 1243746.3493
14 | 2681725.2007 | 1244070.93 | 2681761.6085 | 1244073.5445 | 2681769.2628 | 1244049.128
15 | 2681725.2007 | 1244070.93 | 2681724.0227 | 1243986.2347
16 | 2681787.5047 | 1243990.938 | 2681769.2628 | 1244049.128
17 | 2681723.4679 | 1243946.3501 | 2681724.0227 | 1243986.2347
18 | 2681664.8694 | 1243687.6557 | 2681665.1102 | 1243691.0281 | 2681666.261 | 1243693.0788 | 2681667.661 | 1243694.5991 | 2681670.4417 | 1243695.2045 | 2681674.0879 | 1243694.9767 | 2681680.9315 | 1243693.0918 | 2681685.5486 | 1243691.5209 | 2681686.5357 | 1243691.1898 | 2681692.1773 | 1243689.3216 | 2681695.8914 | 1243688.0051 | 2681696.9466 | 1243687.675 | 2681701.9489 | 1243686.1205 | 2681705.3496 | 1243685.0666 | 2681707.642 | 1243684.3532 | 2681709.4652 | 1243684.2337 | 2681709.4983 | 1243677.9964 | 2681713.8944 | 1243678.2015
19 | 2681713.8944 | 1243678.2015 | 2681714.132 | 1243703.4611
20 | 2681643.8704 | 1243593.9213 | 2681643.8311 | 1243602.8161 | 2681643.829 | 1243603.5165 | 2681643.8563 | 1243614.1579 | 2681643.5611 | 1243622.4265 | 2681642.998 | 1243638.0745 | 2681642.9611 | 1243639.6529 | 2681642.3726 | 1243664.2848 | 2681645.5644 | 1243664.6735 | 2681645.3833 | 1243666.8503 | 2681643.3556 | 1243679.0757 | 2681643.4275 | 1243687.0269 | 2681648.5576 | 1243687.1753 | 2681656.2567 | 1243687.3814 | 2681664.8694 | 1243687.6557
21 | 2681664.8694 | 1243687.6557 | 2681665.9881 | 1243668.6007
22 | 2681664.8694 | 1243687.6557 | 2681665.1102 | 1243691.0281 | 2681666.261 | 1243693.0788 | 2681667.661 | 1243694.5991 | 2681667.1324 | 1243702.2529 | 2681666.594 | 1243710.0623
23 | 2681714.5046 | 1243743.0679 | 2681714.132 | 1243703.4611
24 | 2681754.1844 | 1243753.0104 | 2681754.1373 | 1243743.2694
25 | 2681754.1373 | 1243743.2694 | 2681730.0817 | 1243743.1471
26 | 2681754.2521 | 1243767.2884 | 2681754.1844 | 1243753.0104
27 | 2681714.5046 | 1243743.0679 | 2681730.0817 | 1243743.1471
28 | 2681675.9378 | 1243849.8697 | 2681675.4965 | 1243840.4575
29 | 2681666.594 | 1243710.0623 | 2681665.1143 | 1243711.0315 | 2681662.391 | 1243713.3957 | 2681660.7801 | 1243716.7649 | 2681660.1069 | 1243721.1922 | 2681660.2626 | 1243726.8984 | 2681660.4794 | 1243746.3493
30 | 2681643.8704 | 1243593.9213 | 2681624.2516 | 1243589.8707 | 2681624.3216 | 1243580.7753
31 | 2681666.7949 | 1243654.8585 | 2681665.9881 | 1243668.6007
32 | 2681641.679 | 1243745.4117 | 2681641.9453 | 1243757.3573 | 2681642.7096 | 1243781.5533
33 | 2681641.679 | 1243745.4117 | 2681634.2181 | 1243741.6285 | 2681620.2854 | 1243741.8913
34 | 2681643.559 | 1243805.9656 | 2681643.0139 | 1243791.1853 | 2681642.7096 | 1243781.5533
35 | 2681590.3433 | 1243742.2478 | 2681596.7271 | 1243742.3356 | 2681620.2854 | 1243741.8913
36 | 2681664.5474 | 1243862.5109 | 2681664.2782 | 1243857.915 | 2681664.0321 | 1243852.7301 | 2681666.591 | 1243850.2302 | 2681669.8578 | 1243850.1084 | 2681675.9378 | 1243849.8697
37 | 2681645.9431 | 1243863.3444 | 2681651.2446 | 1243863.1061 | 2681658.3157 | 1243862.7921 | 2681664.5474 | 1243862.5109
38 | 2681664.5474 | 1243862.5109 | 2681665.1133 | 1243865.8767 | 2681666.2671 | 1243876.4892 | 2681667.7022 | 1243889.7296 | 2681667.5137 | 1243895.7313 | 2681667.0946 | 1243903.1198 | 2681667.0882 | 1243908.5236 | 2681666.9571 | 1243913.1029 | 2681667.3868 | 1243922.9438
39 | 2681675.9378 | 1243849.8697 | 2681677.4209 | 1243849.8105
40 | 2681601.106 | 1243875.0584 | 2681614.281 | 1243874.4169 | 2681638.0143 | 1243873.2536 | 2681642.3748 | 1243871.0898 | 2681645.9431 | 1243863.3444
41 | 2681643.7993 | 1243885.6533 | 2681643.0373 | 1243877.8705 | 2681642.3748 | 1243871.0898 | 2681645.9431 | 1243863.3444
42 | 2681645.9431 | 1243863.3444 | 2681645.496 | 1243858.4903 | 2681645.4216 | 1243856.4728
43 | 2681669.3571 | 1243627.9743 | 2681667.8654 | 1243642.6583
44 | 2681669.3571 | 1243627.9743 | 2681670.8571 | 1243613.196
45 | 2681667.0312 | 1243650.87 | 2681667.8654 | 1243642.6583
46 | 2681672.444 | 1243597.5615 | 2681670.8571 | 1243613.196
47 | 2681655.6972 | 1244044.1649 | 2681656.6021 | 1244067.4381
48 | 2681672.5143 | 1244043.5515 | 2681666.8128 | 1244043.7621 | 2681661.3306 | 1244043.9645 | 2681655.6972 | 1244044.1649
49 | 2681655.6972 | 1244044.1649 | 2681655.3189 | 1244036.1344
50 | 2681657.5095 | 1244090.7786 | 2681656.6021 | 1244067.4381
51 | 2681672.5143 | 1244043.5515 | 2681672.8944 | 1244048.8828 | 2681674.0899 | 1244058.1059 | 2681675.1276 | 1244065.6256 | 2681675.6724 | 1244069.9696 | 2681676.0095 | 1244077.815
52 | 2681672.5143 | 1244043.5515 | 2681672.4329 | 1244038.4912 | 2681671.5406 | 1244018.0608
53 | 2681654.2945 | 1244014.1032 | 2681654.7732 | 1244024.5492 | 2681655.3189 | 1244036.1344
54 | 2681677.1271 | 1244103.8264 | 2681676.0095 | 1244077.815
55 | 2681672.444 | 1243597.5615 | 2681673.69 | 1243585.3023
56 | 2681676.122 | 1243561.3728 | 2681673.69 | 1243585.3023
57 | 2681562.9073 | 1243737.7007 | 2681563.6876 | 1243754.6014 | 2681564.4049 | 1243770.0446
58 | 2681562.9073 | 1243737.7007 | 2681545.613 | 1243737.2953
59 | 2681564.4049 | 1243770.0446 | 2681553.1658 | 1243770.0457
60 | 2681564.4049 | 1243770.0446 | 2681565.1391 | 1243785.8995
61 | 2681595.43 | 1243977.7657 | 2681589.7176 | 1243980.4113 | 2681549.9175 | 1243997.9991 | 2681544.4285 | 1244000.3365
62 | 2681595.43 | 1243977.7657 | 2681575.566 | 1243932.7148
63 | 2681472.3273 | 1243974.3941 | 2681482.8941 | 1243973.7832 | 2681490.3618 | 1243975.954 | 2681497.2425 | 1243979.0396 | 2681507.1269 | 1243988.4821 | 2681512.2166 | 1244005.2975 | 2681516.7878 | 1244027.9323 | 2681519.1035 | 1244032.1115 | 2681532.378 | 1244037.3977 | 2681538.3127 | 1244020.2335 | 2681543.253 | 1244006.6805 | 2681544.4285 | 1244000.3365
64 | 2681544.4285 | 1244000.3365 | 2681434.4673 | 1243747.8107 | 2681430.1049 | 1243732.4533
65 | 2681559.3331 | 1243895.8992 | 2681575.566 | 1243932.7148
66 | 2681667.0312 | 1243650.87 | 2681666.7949 | 1243654.8585
67 | 2681681.3221 | 1243849.6547 | 2681677.4209 | 1243849.8105
68 | 2681559.3331 | 1243895.8992 | 2681556.3939 | 1243889.2429 | 2681551.2193 | 1243877.5077 | 2681571.4585 | 1243876.5074 | 2681601.106 | 1243875.0584
69 | 2681601.106 | 1243875.0584 | 2681600.2371 | 1243857.7401
70 | 2681643.7993 | 1243885.6533 | 2681632.3674 | 1243885.4069
71 | 2681643.7993 | 1243885.6533 | 2681648.9621 | 1243894.9421 | 2681649.1379 | 1243898.9956
72 | 2681644.5151 | 1243831.8935 | 2681645.4216 | 1243856.4728
73 | 2681600.2371 | 1243857.7401 | 2681599.2178 | 1243837.4265
74 | 2681562.5354 | 1243799.9072 | 2681554.9686 | 1243799.981
75 | 2681565.5541 | 1243794.7449 | 2681562.5354 | 1243799.9072
76 | 2681565.5541 | 1243794.7449 | 2681565.1391 | 1243785.8995
77 | 2681565.5541 | 1243794.7449 | 2681579.8332 | 1243793.7993
78 | 2681596.9718 | 1243792.6642 | 2681579.8332 | 1243793.7993
79 | 2681596.9718 | 1243792.6642 | 2681598.4131 | 1243821.3882
80 | 2681599.2178 | 1243837.4265 | 2681598.4131 | 1243821.3882
81 | 2681632.3674 | 1243885.4069 | 2681631.6118 | 1243885.3854 | 2681622.8062 | 1243883.9431
82 | 2681649.9705 | 1243918.1945 | 2681649.1379 | 1243898.9956
83 | 2681716.4338 | 1243592.1291 | 2681715.2931 | 1243607.8869
84 | 2681719.177 | 1243547.1573 | 2681719.3833 | 1243551.3855
85 | 2681719.177 | 1243547.1573 | 2681717.7759 | 1243538.7032
86 | 2681719.3833 | 1243551.3855 | 2681716.4338 | 1243592.1291
87 | 2681719.3833 | 1243551.3855 | 2681726.1867 | 1243550.7787 | 2681738.295 | 1243549.7114 | 2681788.4077 | 1243546.9776 | 2681782.6576 | 1243526.0166 | 2681779.509 | 1243512.0742
88 | 2681715.2612 | 1243523.5295 | 2681717.7759 | 1243538.7032
89 | 2681828.0548 | 1243834.8989 | 2681836.4371 | 1243834.87 | 2681843.0802 | 1243834.9061 | 2681844.6872 | 1243829.0907 | 2681844.8785 | 1243805.3762 | 2681844.0678 | 1243799.4941
90 | 2681828.0548 | 1243834.8989 | 2681826.3038 | 1243834.905
91 | 2681805.5567 | 1243729.5236 | 2681819.3623 | 1243728.6689 | 2681819.3249 | 1243731.3815 | 2681822.3385 | 1243734.8255 | 2681825.8386 | 1243738.6098 | 2681827.7252 | 1243742.661 | 2681833.518 | 1243761.599 | 2681835.1252 | 1243766.7249 | 2681839.2169 | 1243776.9331 | 2681842.2889 | 1243786.5491 | 2681844.0678 | 1243799.4941
92 | 2681844.0678 | 1243799.4941 | 2681822.8927 | 1243800.2221
93 | 2681818.395 | 1243834.9324 | 2681826.3038 | 1243834.905
94 | 2681805.5567 | 1243729.5236 | 2681800.8103 | 1243744.3022
95 | 2681805.5567 | 1243729.5236 | 2681804.1657 | 1243720.2311 | 2681797.7103 | 1243716.4394
96 | 2681822.8927 | 1243800.2221 | 2681802.4614 | 1243800.9246
97 | 2681779.509 | 1243512.0742 | 2681758.5095 | 1243512.9982
98 | 2681754.2521 | 1243767.2884 | 2681764.178 | 1243767.1472
99 | 2681764.178 | 1243767.1472 | 2681764.0297 | 1243792.3652
100 | 2681763.8801 | 1243817.802 | 2681764.0297 | 1243792.3652
101 | 2681790.3301 | 1243717.2271 | 2681797.7103 | 1243716.4394
102 | 2681763.7203 | 1243581.618 | 2681757.8985 | 1243581.193
103 | 2681763.7203 | 1243581.618 | 2681766.2947 | 1243579.6409 | 2681770.048 | 1243577.1353 | 2681773.41 | 1243575.6027
104 | 2681797.1531 | 1243960.1606 | 2681787.5047 | 1243990.938
105 | 2681715.761 | 1243875.681 | 2681715.788 | 1243878.1054 | 2681715.832 | 1243883.1429 | 2681717.3656 | 1243941.3284 | 2681723.3937 | 1243941.0111 | 2681723.4679 | 1243946.3501
106 | 2681714.5982 | 1243752.7317 | 2681714.5046 | 1243743.0679
107 | 2681686.8317 | 1243837.0548 | 2681687.3113 | 1243849.4259 | 2681681.3221 | 1243849.6547
108 | 2681686.8317 | 1243837.0548 | 2681688.5267 | 1243834.1649 | 2681687.761 | 1243818.6338
109 | 2681658.533 | 1244114.0635 | 2681659.5071 | 1244135.7614 | 2681659.5872 | 1244136.8471
110 | 2681657.5095 | 1244090.7786 | 2681657.6506 | 1244094.4059 | 2681658.533 | 1244114.0635
111 | 2681643.559 | 1243805.9656 | 2681644.5151 | 1243831.8935
112 | 2681653.2261 | 1243990.7899 | 2681654.2945 | 1244014.1032
113 | 2681565.1391 | 1243785.8995 | 2681553.9133 | 1243786.5902
114 | 2681472.3273 | 1243974.3941 | 2681470.9889 | 1244034.9407
115 | 2681622.8062 | 1243883.9431 | 2681614.4182 | 1243882.5691 | 2681588.8105 | 1243883.7401 | 2681583.3411 | 1243886.8449 | 2681578.3933 | 1243892.9222
116 | 2681649.9705 | 1243918.1945 | 2681650.8839 | 1243939.253
117 | 2681740.5157 | 1243817.958 | 2681761.7863 | 1243817.8176 | 2681763.8801 | 1243817.802
118 | 2681740.5157 | 1243817.958 | 2681740.5123 | 1243805.5916
119 | 2681740.5157 | 1243817.958 | 2681739.0642 | 1243817.9825 | 2681720.8139 | 1243818.3425 | 2681715.2193 | 1243818.4544 | 2681715.761 | 1243875.681
120 | 2681763.8801 | 1243817.802 | 2681763.6481 | 1243835.178 | 2681777.6577 | 1243835.1152
121 | 2681740.5064 | 1243784.6757 | 2681740.5123 | 1243805.5916
122 | 2681720.6411 | 1243878.5948 | 2681715.761 | 1243875.681
123 | 2681777.6577 | 1243835.1152 | 2681802.0231 | 1243835.0058
124 | 2681818.395 | 1243834.9324 | 2681802.0231 | 1243835.0058
125 | 2681790.3301 | 1243717.2271 | 2681787.5823 | 1243724.6502
126 | 2681790.3301 | 1243717.2271 | 2681777.6932 | 1243708.9692 | 2681773.7232 | 1243709.1446
127 | 2681757.8985 | 1243581.193 | 2681757.389 | 1243573.7473
128 | 2681739.7442 | 1243583.3111 | 2681745.9887 | 1243581.0288 | 2681750.7954 | 1243584.353 | 2681752.8317 | 1243590.163 | 2681757.8985 | 1243581.193
129 | 2681739.7442 | 1243583.3111 | 2681732.9815 | 1243577.1246
130 | 2681787.5823 | 1243724.6502 | 2681787.7729 | 1243727.8217 | 2681790.0355 | 1243731.4667 | 2681784.0785 | 1243745.7949
131 | 2681778.6561 | 1243725.1942 | 2681787.5823 | 1243724.6502
132 | 2681714.5982 | 1243752.7317 | 2681728.2295 | 1243752.8277
133 | 2681653.2261 | 1243990.7899 | 2681652.2299 | 1243969.0506
134 | 2681652.2299 | 1243969.0506 | 2681651.2281 | 1243947.1889 | 2681650.8839 | 1243939.253

## bus_geodata
| x | y | coords
0 | 2681780.3139 | 1243638.1261
1 | 2681739.1074 | 1243635.5401
2 | 2681810.6158 | 1243641.1295
3 | 2681739.143 | 1243632.961
4 | 2681769.7987 | 1243595.7675
5 | 2681713.5019 | 1243632.6298
6 | 2681743.9064 | 1243621.8741
7 | 2681661.9145 | 1243804.5328
8 | 2681670.3055 | 1243820.8934
9 | 2681661.1528 | 1243776.8897
10 | 2681725.2007 | 1244070.93
11 | 2681769.2628 | 1244049.128
12 | 2681724.0227 | 1243986.2347
13 | 2681713.8944 | 1243678.2015
14 | 2681664.8694 | 1243687.6557
15 | 2681714.132 | 1243703.4611
16 | 2681754.1373 | 1243743.2694
17 | 2681754.1844 | 1243753.0104
18 | 2681730.0817 | 1243743.1471
19 | 2681675.4965 | 1243840.4575
20 | 2681666.594 | 1243710.0623
21 | 2681660.4794 | 1243746.3493
22 | 2681643.8704 | 1243593.9213
23 | 2681665.9881 | 1243668.6007
24 | 2681641.679 | 1243745.4117
25 | 2681642.7096 | 1243781.5533
26 | 2681620.2854 | 1243741.8913
27 | 2681664.5474 | 1243862.5109
28 | 2681675.9378 | 1243849.8697
29 | 2681645.9431 | 1243863.3444
30 | 2681667.3868 | 1243922.9438
31 | 2681669.3571 | 1243627.9743
32 | 2681667.8654 | 1243642.6583
33 | 2681670.8571 | 1243613.196
34 | 2681655.6972 | 1244044.1649
35 | 2681656.6021 | 1244067.4381
36 | 2681672.5143 | 1244043.5515
37 | 2681655.3189 | 1244036.1344
38 | 2681676.0095 | 1244077.815
39 | 2681671.5406 | 1244018.0608
40 | 2681624.3216 | 1243580.7753
41 | 2681672.444 | 1243597.5615
42 | 2681673.69 | 1243585.3023
43 | 2681562.9073 | 1243737.7007
44 | 2681564.4049 | 1243770.0446
45 | 2681545.613 | 1243737.2953
46 | 2681595.43 | 1243977.7657
47 | 2681544.4285 | 1244000.3365
48 | 2681575.566 | 1243932.7148
49 | 2681666.7949 | 1243654.8585
50 | 2681667.0312 | 1243650.87
51 | 2681677.4209 | 1243849.8105
52 | 2681601.106 | 1243875.0584
53 | 2681643.7993 | 1243885.6533
54 | 2681645.4216 | 1243856.4728
55 | 2681559.3331 | 1243895.8992
56 | 2681600.2371 | 1243857.7401
57 | 2681562.5354 | 1243799.9072
58 | 2681554.9686 | 1243799.981
59 | 2681565.5541 | 1243794.7449
60 | 2681596.9718 | 1243792.6642
61 | 2681579.8332 | 1243793.7993
62 | 2681598.4131 | 1243821.3882
63 | 2681632.3674 | 1243885.4069
64 | 2681649.1379 | 1243898.9956
65 | 2681715.2931 | 1243607.8869
66 | 2681719.177 | 1243547.1573
67 | 2681719.3833 | 1243551.3855
68 | 2681717.7759 | 1243538.7032
69 | 2681828.0548 | 1243834.8989
70 | 2681844.0678 | 1243799.4941
71 | 2681826.3038 | 1243834.905
72 | 2681805.5567 | 1243729.5236
73 | 2681822.8927 | 1243800.2221
74 | 2681779.509 | 1243512.0742
75 | 2681758.5095 | 1243512.9982
76 | 2681764.178 | 1243767.1472
77 | 2681754.2521 | 1243767.2884
78 | 2681764.0297 | 1243792.3652
79 | 2681800.8103 | 1243744.3022
80 | 2681797.7103 | 1243716.4394
81 | 2681716.4338 | 1243592.1291
82 | 2681764.6003 | 1243607.6934
83 | 2681763.7203 | 1243581.618
84 | 2681677.1271 | 1244103.8264
85 | 2681787.5047 | 1243990.938
86 | 2681723.4679 | 1243946.3501
87 | 2681714.5046 | 1243743.0679
88 | 2681681.3221 | 1243849.6547
89 | 2681686.8317 | 1243837.0548
90 | 2681687.761 | 1243818.6338
91 | 2681659.5872 | 1244136.8471
92 | 2681658.533 | 1244114.0635
93 | 2681643.559 | 1243805.9656
94 | 2681590.3433 | 1243742.2478
95 | 2681676.122 | 1243561.3728
96 | 2681657.5095 | 1244090.7786
97 | 2681654.2945 | 1244014.1032
98 | 2681553.1658 | 1243770.0457
99 | 2681565.1391 | 1243785.8995
100 | 2681472.3273 | 1243974.3941
101 | 2681430.1049 | 1243732.4533
102 | 2681644.5151 | 1243831.8935
103 | 2681599.2178 | 1243837.4265
104 | 2681622.8062 | 1243883.9431
105 | 2681649.9705 | 1243918.1945
106 | 2681715.2612 | 1243523.5295
107 | 2681740.5157 | 1243817.958
108 | 2681763.8801 | 1243817.802
109 | 2681740.5123 | 1243805.5916
110 | 2681715.761 | 1243875.681
111 | 2681777.6577 | 1243835.1152
112 | 2681818.395 | 1243834.9324
113 | 2681802.0231 | 1243835.0058
114 | 2681797.1531 | 1243960.1606
115 | 2681802.4614 | 1243800.9246
116 | 2681790.3301 | 1243717.2271
117 | 2681757.8985 | 1243581.193
118 | 2681773.41 | 1243575.6027
119 | 2681739.7442 | 1243583.3112
120 | 2681732.9815 | 1243577.1247
121 | 2681757.389 | 1243573.7473
122 | 2681470.9889 | 1244034.9407
123 | 2681553.9133 | 1243786.5902
124 | 2681787.5823 | 1243724.6502
125 | 2681773.7232 | 1243709.1446
126 | 2681784.0785 | 1243745.7949
127 | 2681778.6561 | 1243725.1942
128 | 2681714.5982 | 1243752.7317
129 | 2681728.2295 | 1243752.8277
130 | 2681720.6411 | 1243878.5948
131 | 2681740.5064 | 1243784.6757
132 | 2681653.2261 | 1243990.7899
133 | 2681652.2299 | 1243969.0506
134 | 2681650.8839 | 1243939.253
135 | 2681578.3933 | 1243892.9222
136 | 2681641.679 | 1243745.4117

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97567 | -0.46765 | 0.0044984 | 0.0011274
1 | 0.97605 | -0.46022 | 0 | 0
2 | 0.97552 | -0.47062 | 0 | 0
3 | 0.97607 | -0.45975 | 0 | 0
4 | 0.97515 | -0.47788 | 0 | 0
5 | 0.97632 | -0.45479 | 0 | 0
6 | 0.97606 | -0.45992 | 0.00077471 | 0.00019416
7 | 0.98507 | -0.28428 | 0 | 0
8 | 0.98621 | -0.26239 | 0 | 0
9 | 0.98349 | -0.3149 | 0.00060261 | 0.00015103
10 | 0.97052 | -0.56906 | 0 | 0
11 | 0.97023 | -0.575 | 0.0028146 | 0.0007054
12 | 0.97093 | -0.56096 | 0.0014772 | 0.00037022
13 | 0.97707 | -0.44 | 0 | 0
14 | 0.97848 | -0.41251 | 0 | 0
15 | 0.97668 | -0.44773 | 0.0019255 | 0.00048258
16 | 0.97523 | -0.47618 | 0 | 0
17 | 0.97497 | -0.48132 | 0 | 0
18 | 0.97587 | -0.46352 | 0.0018358 | 0.00046009
19 | 0.9874 | -0.23941 | 0.0019199 | 0.00048118
20 | 0.9797 | -0.38849 | 0 | 0
21 | 0.98175 | -0.34867 | 0.0090666 | 0.0022723
22 | 0.97833 | -0.41536 | 0 | 0
23 | 0.97735 | -0.43456 | 0.0043288 | 0.0010849
24 | 0.99971 | -0.0055683 | 0 | 0
25 | 1 | 0 | -0.27135 | -0.069567
26 | 0.99953 | -0.0090039 | 0.0045105 | 0.0011304
27 | 0.9893 | -0.20315 | 0 | 0
28 | 0.98795 | -0.22889 | 0 | 0
29 | 0.99042 | -0.18164 | 0 | 0
30 | 0.98914 | -0.20616 | 0.00279 | 0.00069923
31 | 0.97515 | -0.47784 | 0 | 0
32 | 0.97592 | -0.46265 | 0.002843 | 0.00071252
33 | 0.97437 | -0.49316 | 0.053735 | 0.013467
34 | 0.98529 | -0.28123 | 0 | 0
35 | 0.98498 | -0.28719 | 0.00037364 | 9.3642e-05
36 | 0.98508 | -0.28529 | 0 | 0
37 | 0.98549 | -0.27725 | 0.00049508 | 0.00012408
38 | 0.98472 | -0.29236 | 0.00034003 | 8.522e-05
39 | 0.98503 | -0.2862 | 0.0019848 | 0.00049744
40 | 0.97829 | -0.41607 | 0.0013301 | 0.00033335
41 | 0.97433 | -0.49388 | 0 | 0
42 | 0.97431 | -0.49445 | 0.0015679 | 0.00039296
43 | 0.97715 | -0.43919 | 0 | 0
44 | 0.97871 | -0.40852 | 0 | 0
45 | 0.97631 | -0.45561 | 0.051962 | 0.013023
46 | 0.98447 | -0.29645 | 0 | 0
47 | 0.98375 | -0.31043 | 0 | 0
48 | 0.98511 | -0.28409 | 0.00045857 | 0.00011493
49 | 0.97659 | -0.44941 | 0 | 0
50 | 0.97637 | -0.45373 | 0 | 0
51 | 0.98795 | -0.22895 | 0.0016119 | 0.00040398
52 | 0.98658 | -0.25556 | 0 | 0
53 | 0.98968 | -0.19589 | 0 | 0
54 | 0.99121 | -0.16654 | 0.0027555 | 0.0006906
55 | 0.98564 | -0.27368 | 0 | 0
56 | 0.98548 | -0.27667 | 0.00332 | 0.00083206
57 | 0.97995 | -0.38431 | 0 | 0
58 | 0.97993 | -0.3847 | 0.0028664 | 0.00071839
59 | 0.97996 | -0.384 | 0 | 0
60 | 0.98171 | -0.34989 | 0 | 0
61 | 0.98074 | -0.36877 | 0.0020105 | 0.00050387
62 | 0.98333 | -0.31838 | 0.0019426 | 0.00048686
63 | 0.98967 | -0.19623 | 0 | 0
64 | 0.98924 | -0.2045 | 0.0018423 | 0.00046172
65 | 0.97622 | -0.45686 | 0.00060346 | 0.00015124
66 | 0.97602 | -0.46063 | 0 | 0
67 | 0.97603 | -0.46051 | 0 | 0
68 | 0.97601 | -0.46088 | 0.00090144 | 0.00022592
69 | 0.97215 | -0.53683 | 0 | 0
70 | 0.97177 | -0.54449 | 0 | 0
71 | 0.97217 | -0.53657 | 0.0016409 | 0.00041124
72 | 0.97124 | -0.55495 | 0 | 0
73 | 0.97173 | -0.54524 | 0.00085427 | 0.0002141
74 | 0.97586 | -0.46384 | 0 | 0
75 | 0.97583 | -0.46451 | 0.001732 | 0.00043407
76 | 0.97432 | -0.49407 | 0 | 0
77 | 0.97458 | -0.48885 | 0 | 0
78 | 0.97364 | -0.50739 | 0.0017238 | 0.00043204
79 | 0.97122 | -0.5553 | 0.0012067 | 0.00030242
80 | 0.97116 | -0.55653 | 0.0013357 | 0.00033476
81 | 0.97616 | -0.45801 | 0.00060827 | 0.00015245
82 | 0.97513 | -0.4782 | 0.0013392 | 0.00033562
83 | 0.97509 | -0.47912 | 0 | 0
84 | 0.98445 | -0.29755 | 0.011084 | 0.002778
85 | 0.97009 | -0.57766 | 0.00094237 | 0.00023618
86 | 0.97118 | -0.55606 | 0.0010281 | 0.00025767
87 | 0.9761 | -0.45916 | 0 | 0
88 | 0.98795 | -0.22898 | 0 | 0
89 | 0.98794 | -0.22912 | 0 | 0
90 | 0.98793 | -0.22927 | 0.0004385 | 0.0001099
91 | 0.98427 | -0.30114 | 0.0059943 | 0.0015023
92 | 0.98439 | -0.29868 | 0.0075436 | 0.0018906
93 | 0.9971 | -0.054611 | 0.0031156 | 0.00078084
94 | 0.99941 | -0.011262 | 0.0043206 | 0.0010828
95 | 0.97428 | -0.49485 | 0.00092132 | 0.0002309
96 | 0.98468 | -0.293 | 0.00031622 | 7.9252e-05
97 | 0.98606 | -0.26611 | 0.00066193 | 0.0001659
98 | 0.97869 | -0.40891 | 0.0019211 | 0.00048148
99 | 0.9795 | -0.39297 | 0 | 0
100 | 0.98373 | -0.31095 | 0 | 0
101 | 0.98005 | -0.38284 | 0.013741 | 0.0034438
102 | 0.99406 | -0.11225 | 0.0031417 | 0.00078738
103 | 0.98426 | -0.30026 | 0.0019266 | 0.00048284
104 | 0.98965 | -0.19651 | 0.0011544 | 0.00028932
105 | 0.98869 | -0.21515 | 0.00051735 | 0.00012966
106 | 0.976 | -0.46108 | 0.00070659 | 0.00017709
107 | 0.97269 | -0.52627 | 0 | 0
108 | 0.973 | -0.52004 | 0 | 0
109 | 0.97266 | -0.52675 | 0.0009738 | 0.00024406
110 | 0.97173 | -0.54513 | 0 | 0
111 | 0.97264 | -0.52727 | 0.0016181 | 0.00040554
112 | 0.97224 | -0.53514 | 0 | 0
113 | 0.97239 | -0.53217 | 0.0010725 | 0.00026879
114 | 0.97005 | -0.5785 | 0.0014074 | 0.00035273
115 | 0.97171 | -0.54563 | 0.0010441 | 0.00026167
116 | 0.97113 | -0.55705 | 0 | 0
117 | 0.97507 | -0.47937 | 0 | 0
118 | 0.97507 | -0.47947 | 0.0016564 | 0.00041514
119 | 0.97504 | -0.48008 | 0 | 0
120 | 0.97503 | -0.48031 | 0.0013379 | 0.00033532
121 | 0.97507 | -0.47951 | 0.00098782 | 0.00024757
122 | 0.98372 | -0.31118 | 0.00020514 | 5.1414e-05
123 | 0.97948 | -0.39336 | 0.0019307 | 0.00048387
124 | 0.97111 | -0.55739 | 0 | 0
125 | 0.97111 | -0.55754 | 0.0013873 | 0.0003477
126 | 0.97109 | -0.55792 | 0.0012415 | 0.00031115
127 | 0.97111 | -0.55757 | 0.0011099 | 0.00027817
128 | 0.97609 | -0.45934 | 0 | 0
129 | 0.97607 | -0.45958 | 0.00098909 | 0.00024789
130 | 0.97171 | -0.54563 | 0.0047104 | 0.0011805
131 | 0.97264 | -0.52719 | 0.0011281 | 0.00028273
132 | 0.98668 | -0.25407 | 0.00057764 | 0.00014477
133 | 0.98727 | -0.24263 | 0.00061139 | 0.00015323
134 | 0.98809 | -0.22665 | 0.00058592 | 0.00014685
135 | 0.98963 | -0.19695 | 0.00051005 | 0.00012783
136 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0098227 | -0.0024605 | 0.0098262 | 0.0024622 | 3.4757e-06 | 1.7085e-06 | 0.01498 | 0.01498 | 0.01498 | 0.97567 | -0.46765 | 0.97605 | -0.46022 | 4.1155
1 | 0.0053243 | 0.0013331 | -0.0053236 | -0.001333 | 7.5287e-07 | 1.0161e-07 | 0.0081198 | 0.0081199 | 0.0081199 | 0.97567 | -0.46765 | 0.97552 | -0.47062 | 2.2307
2 | -0.0098262 | -0.0024622 | 0.0098264 | 0.0024623 | 2.1711e-07 | 1.0671e-07 | 0.01498 | 0.01498 | 0.01498 | 0.97605 | -0.46022 | 0.97607 | -0.45975 | 4.1154
3 | 0.0053236 | 0.001333 | -0.0053217 | -0.0013327 | 1.8402e-06 | 2.4891e-07 | 0.0081199 | 0.0081203 | 0.0081203 | 0.97552 | -0.47062 | 0.97515 | -0.47788 | 2.2308
4 | -0.010601 | -0.0026563 | 0.010604 | 0.0026576 | 2.5041e-06 | 1.283e-06 | 0.016161 | 0.016161 | 0.016161 | 0.97607 | -0.45975 | 0.97632 | -0.45479 | 4.4399
5 | 0.00077472 | 0.00019401 | -0.00077471 | -0.00019416 | 6.3117e-09 | -1.4678e-07 | 0.001181 | 0.0011811 | 0.0011811 | 0.97607 | -0.45975 | 0.97606 | -0.45992 | 0.32447
6 | 0.0013392 | 0.00033547 | -0.0013392 | -0.00033562 | 2.0365e-08 | -1.4921e-07 | 0.0020434 | 0.0020435 | 0.0020435 | 0.97515 | -0.47788 | 0.97513 | -0.4782 | 0.5614
7 | 0.0039825 | 0.00099726 | -0.0039823 | -0.00099733 | 2.3633e-07 | -6.1639e-08 | 0.0060768 | 0.0060769 | 0.0060769 | 0.97515 | -0.47788 | 0.97509 | -0.47912 | 1.6695
8 | 0.0045532 | 0.0011387 | -0.0045527 | -0.0011388 | 4.4789e-07 | -2.3544e-08 | 0.0069386 | 0.0069388 | 0.0069388 | 0.97632 | -0.45479 | 0.97622 | -0.45686 | 1.9063
9 | -0.015157 | -0.0037963 | 0.015167 | 0.0038025 | 1.0685e-05 | 6.1704e-06 | 0.0231 | 0.023099 | 0.0231 | 0.97632 | -0.45479 | 0.97707 | -0.44 | 6.3461
10 | -0.12421 | -0.031567 | 0.12434 | 0.03165 | 0.00013112 | 8.341e-05 | 0.18778 | 0.18778 | 0.18778 | 0.98507 | -0.28428 | 0.98621 | -0.26239 | 25.7941
11 | 0.12421 | 0.031567 | -0.12403 | -0.031451 | 0.00018283 | 0.00011631 | 0.18778 | 0.18778 | 0.18778 | 0.98507 | -0.28428 | 0.98349 | -0.3149 | 25.7941
12 | -0.12434 | -0.03165 | 0.12448 | 0.031738 | 0.00013787 | 8.7707e-05 | 0.18778 | 0.18778 | 0.18778 | 0.98621 | -0.26239 | 0.9874 | -0.23941 | 25.7941
13 | 0.12342 | 0.0313 | -0.12322 | -0.031172 | 0.00020002 | 0.00012724 | 0.18687 | 0.18687 | 0.18687 | 0.98349 | -0.3149 | 0.98175 | -0.34867 | 25.6689
14 | 0.0051662 | 0.0012936 | -0.0051647 | -0.0012934 | 1.4607e-06 | 1.6782e-07 | 0.0079204 | 0.0079207 | 0.0079207 | 0.97052 | -0.56906 | 0.97023 | -0.575 | 2.176
15 | -0.0051662 | -0.0012936 | 0.0051682 | 0.0012938 | 1.9925e-06 | 2.2807e-07 | 0.0079204 | 0.00792 | 0.0079204 | 0.97052 | -0.56906 | 0.97093 | -0.56096 | 2.1759
16 | 0.0023501 | 0.00058798 | -0.0023498 | -0.00058855 | 2.9705e-07 | -5.6289e-07 | 0.003604 | 0.0036043 | 0.0036043 | 0.97023 | -0.575 | 0.97009 | -0.57766 | 0.99018
17 | -0.0066454 | -0.001664 | 0.0066469 | 0.0016645 | 1.5513e-06 | 4.9939e-07 | 0.010184 | 0.010184 | 0.010184 | 0.97093 | -0.56096 | 0.97118 | -0.55606 | 2.7978
18 | -0.048788 | -0.012274 | 0.048852 | 0.012314 | 6.4174e-05 | 3.9517e-05 | 0.074318 | 0.074317 | 0.074318 | 0.97707 | -0.44 | 0.97848 | -0.41251 | 10.2085
19 | 0.033621 | 0.0084716 | -0.033608 | -0.0084643 | 1.2425e-05 | 7.3196e-06 | 0.051219 | 0.051219 | 0.051219 | 0.97707 | -0.44 | 0.97668 | -0.44773 | 7.0355
20 | 0.0013303 | 0.00033165 | -0.0013301 | -0.00033301 | 1.804e-07 | -1.3612e-06 | 0.0020224 | 0.002023 | 0.002023 | 0.97848 | -0.41251 | 0.97833 | -0.41536 | 0.55576
21 | 0.063625 | 0.016033 | -0.063558 | -0.015991 | 6.7056e-05 | 4.2676e-05 | 0.096789 | 0.096789 | 0.096789 | 0.97848 | -0.41251 | 0.97735 | -0.43456 | 26.5903
22 | -0.11381 | -0.028679 | 0.11394 | 0.028762 | 0.00013094 | 8.3217e-05 | 0.17313 | 0.17313 | 0.17313 | 0.97848 | -0.41251 | 0.9797 | -0.38849 | 23.7814
23 | 0.031683 | 0.0079817 | -0.031665 | -0.0079716 | 1.7315e-05 | 1.0091e-05 | 0.048285 | 0.048286 | 0.048286 | 0.97668 | -0.44773 | 0.9761 | -0.45916 | 6.6326
24 | 0.028817 | 0.0072494 | -0.02881 | -0.0072449 | 7.0659e-06 | 4.4006e-06 | 0.043979 | 0.043979 | 0.043979 | 0.97523 | -0.47618 | 0.97497 | -0.48132 | 12.0821
25 | -0.028817 | -0.0072494 | 0.028834 | 0.0072602 | 1.7448e-05 | 1.0866e-05 | 0.043979 | 0.043979 | 0.043979 | 0.97523 | -0.47618 | 0.97587 | -0.46352 | 12.0821
26 | 0.02881 | 0.0072449 | -0.028799 | -0.0072385 | 1.0357e-05 | 6.4507e-06 | 0.043979 | 0.043979 | 0.043979 | 0.97497 | -0.48132 | 0.97458 | -0.48885 | 12.0821
27 | -0.03067 | -0.0077203 | 0.030676 | 0.007724 | 6.391e-06 | 3.7009e-06 | 0.046778 | 0.046778 | 0.046778 | 0.97587 | -0.46352 | 0.9761 | -0.45916 | 6.4255
28 | -0.1264 | -0.032219 | 0.12646 | 0.03226 | 6.4232e-05 | 4.0867e-05 | 0.19067 | 0.19067 | 0.19067 | 0.9874 | -0.23941 | 0.98795 | -0.22889 | 26.1915
29 | -0.11394 | -0.028762 | 0.11416 | 0.0289 | 0.00021777 | 0.00013839 | 0.17313 | 0.17313 | 0.17313 | 0.9797 | -0.38849 | 0.98175 | -0.34867 | 23.7813
30 | 0.0013301 | 0.00033301 | -0.0013301 | -0.00033335 | 4.4704e-08 | -3.3714e-07 | 0.002023 | 0.0020231 | 0.0020231 | 0.97833 | -0.41536 | 0.97829 | -0.41607 | 0.5558
31 | 0.059229 | 0.014906 | -0.059187 | -0.014879 | 4.1998e-05 | 2.6706e-05 | 0.090198 | 0.090198 | 0.090198 | 0.97735 | -0.43456 | 0.97659 | -0.44941 | 24.7797
32 | -0.0088329 | -0.0022138 | 0.0088353 | 0.0022148 | 2.3437e-06 | 1.0257e-06 | 0.013147 | 0.013147 | 0.013147 | 0.99971 | -0.0055683 | 1 | 0 | 3.6119
33 | 0.0088329 | 0.0022138 | -0.0088315 | -0.0022132 | 1.4455e-06 | 6.328e-07 | 0.013147 | 0.013147 | 0.013147 | 0.99971 | -0.0055683 | 0.99953 | -0.0090039 | 3.6119
34 | 0.26086 | 0.067352 | -0.26017 | -0.066909 | 0.0006926 | 0.00044263 | 0.38887 | 0.38887 | 0.38887 | 1 | 0 | 0.9971 | -0.054611 | 53.4164
35 | 0.004321 | 0.0010827 | -0.0043206 | -0.0010828 | 4.6471e-07 | -9.5055e-08 | 0.0064327 | 0.0064328 | 0.0064328 | 0.99953 | -0.0090039 | 0.99941 | -0.011262 | 1.7673
36 | 0.12867 | 0.032875 | -0.12851 | -0.032773 | 0.00015998 | 0.0001018 | 0.19376 | 0.19376 | 0.19376 | 0.9893 | -0.20315 | 0.98795 | -0.22889 | 26.6156
37 | -0.13146 | -0.033574 | 0.1316 | 0.033661 | 0.00013684 | 8.7096e-05 | 0.19796 | 0.19796 | 0.19796 | 0.9893 | -0.20315 | 0.99042 | -0.18164 | 27.1921
38 | 0.0027904 | 0.00069871 | -0.00279 | -0.00069923 | 4.0059e-07 | -5.2219e-07 | 0.0041968 | 0.0041971 | 0.0041971 | 0.9893 | -0.20315 | 0.98914 | -0.20616 | 1.153
39 | 0.0020504 | 0.00051334 | -0.0020504 | -0.00051336 | 5.308e-09 | -1.561e-08 | 0.0030881 | 0.0030881 | 0.0030881 | 0.98795 | -0.22889 | 0.98795 | -0.22895 | 0.84837
40 | 0.083234 | 0.021218 | -0.082938 | -0.021029 | 0.00029586 | 0.0001887 | 0.12518 | 0.12518 | 0.12518 | 0.99042 | -0.18164 | 0.98658 | -0.25556 | 34.39
41 | 0.03476 | 0.0087713 | -0.034737 | -0.0087564 | 2.3707e-05 | 1.4875e-05 | 0.052245 | 0.052246 | 0.052246 | 0.99042 | -0.18164 | 0.98968 | -0.19589 | 14.3532
42 | -0.24959 | -0.06365 | 0.24978 | 0.063767 | 0.00018214 | 0.00011639 | 0.37538 | 0.37538 | 0.37538 | 0.99042 | -0.18164 | 0.99121 | -0.16654 | 51.5636
43 | -0.056266 | -0.014117 | 0.056306 | 0.014143 | 4.0806e-05 | 2.5931e-05 | 0.085863 | 0.085863 | 0.085863 | 0.97515 | -0.47784 | 0.97592 | -0.46265 | 23.5889
44 | 0.056266 | 0.014117 | -0.056225 | -0.014091 | 4.1068e-05 | 2.6098e-05 | 0.085863 | 0.085864 | 0.085864 | 0.97515 | -0.47784 | 0.97437 | -0.49316 | 23.5889
45 | -0.059149 | -0.014855 | 0.059175 | 0.014871 | 2.5182e-05 | 1.6013e-05 | 0.090198 | 0.090198 | 0.090198 | 0.97592 | -0.46265 | 0.97637 | -0.45373 | 24.7797
46 | 0.0024894 | 0.00062332 | -0.0024893 | -0.00062346 | 8.5164e-08 | -1.4122e-07 | 0.0038015 | 0.0038016 | 0.0038016 | 0.97437 | -0.49316 | 0.97433 | -0.49388 | 1.0444
47 | 0.01424 | 0.0035725 | -0.014236 | -0.0035702 | 4.04e-06 | 2.289e-06 | 0.021507 | 0.021507 | 0.021507 | 0.98529 | -0.28123 | 0.98498 | -0.28719 | 5.9086
48 | 0.013418 | 0.0033652 | -0.013416 | -0.0033638 | 2.5918e-06 | 1.4444e-06 | 0.020266 | 0.020266 | 0.020266 | 0.98529 | -0.28123 | 0.98508 | -0.28529 | 5.5675
49 | -0.027658 | -0.0069377 | 0.027664 | 0.006941 | 5.2606e-06 | 3.2644e-06 | 0.041773 | 0.041773 | 0.041773 | 0.98529 | -0.28123 | 0.98549 | -0.27725 | 11.476
50 | 0.013862 | 0.0034765 | -0.013858 | -0.0034744 | 3.8418e-06 | 2.1615e-06 | 0.020943 | 0.020943 | 0.020943 | 0.98498 | -0.28719 | 0.98468 | -0.293 | 5.7535
51 | 0.011431 | 0.0028666 | -0.011427 | -0.0028646 | 3.8538e-06 | 2.0278e-06 | 0.017267 | 0.017268 | 0.017268 | 0.98508 | -0.28529 | 0.98472 | -0.29236 | 4.7439
52 | 0.0019849 | 0.00049717 | -0.0019848 | -0.00049744 | 8.6e-08 | -2.6972e-07 | 0.0029982 | 0.0029983 | 0.0029983 | 0.98508 | -0.28529 | 0.98503 | -0.2862 | 0.82372
53 | -0.028159 | -0.007065 | 0.028174 | 0.0070743 | 1.4953e-05 | 9.2887e-06 | 0.04252 | 0.04252 | 0.04252 | 0.98549 | -0.27725 | 0.98606 | -0.26611 | 11.6814
54 | 0.011087 | 0.0027794 | -0.011084 | -0.002778 | 2.7405e-06 | 1.4228e-06 | 0.016754 | 0.016754 | 0.016754 | 0.98472 | -0.29236 | 0.98445 | -0.29755 | 4.6027
55 | 0.0024893 | 0.00062346 | -0.0024892 | -0.00062357 | 6.6781e-08 | -1.1072e-07 | 0.0038016 | 0.0038016 | 0.0038016 | 0.97433 | -0.49388 | 0.97431 | -0.49445 | 1.0444
56 | 0.00092133 | 0.00023062 | -0.00092132 | -0.0002309 | 1.7858e-08 | -2.8811e-07 | 0.001407 | 0.0014071 | 0.0014071 | 0.97431 | -0.49445 | 0.97428 | -0.49485 | 0.38657
57 | -0.052002 | -0.013049 | 0.052078 | 0.013097 | 7.6164e-05 | 4.8339e-05 | 0.079196 | 0.079196 | 0.079196 | 0.97715 | -0.43919 | 0.97871 | -0.40852 | 21.7571
58 | 0.052002 | 0.013049 | -0.051962 | -0.013023 | 4.0687e-05 | 2.5823e-05 | 0.079196 | 0.079196 | 0.079196 | 0.97715 | -0.43919 | 0.97631 | -0.45561 | 21.7571
59 | 0.0019211 | 0.00048136 | -0.0019211 | -0.00048148 | 3.5851e-08 | -1.1787e-07 | 0.0029208 | 0.0029209 | 0.0029209 | 0.97871 | -0.40852 | 0.97869 | -0.40891 | 0.80244
60 | -0.054 | -0.013578 | 0.05404 | 0.013604 | 4.014e-05 | 2.549e-05 | 0.082116 | 0.082116 | 0.082116 | 0.97871 | -0.40852 | 0.9795 | -0.39297 | 22.5595
61 | 0.014003 | 0.0035248 | -0.013994 | -0.0035195 | 9.3519e-06 | 5.2783e-06 | 0.021171 | 0.021171 | 0.021171 | 0.98447 | -0.29645 | 0.98375 | -0.31043 | 5.8163
62 | -0.014003 | -0.0035248 | 0.014011 | 0.0035294 | 8.2755e-06 | 4.6699e-06 | 0.021171 | 0.021171 | 0.021171 | 0.98447 | -0.29645 | 0.98511 | -0.28409 | 5.8162
63 | 0.00020515 | 4.8893e-05 | -0.00020515 | -5.0646e-05 | 4.9767e-09 | -1.7532e-06 | 0.00030943 | 0.00031004 | 0.00031004 | 0.98375 | -0.31043 | 0.98373 | -0.31095 | 0.085175
64 | 0.013789 | 0.0034706 | -0.013741 | -0.0034438 | 4.756e-05 | 2.6753e-05 | 0.020862 | 0.020863 | 0.020863 | 0.98375 | -0.31043 | 0.98005 | -0.38284 | 5.7317
65 | -0.01447 | -0.0036444 | 0.014477 | 0.0036485 | 7.2123e-06 | 4.1034e-06 | 0.021864 | 0.021863 | 0.021864 | 0.98511 | -0.28409 | 0.98564 | -0.27368 | 6.0065
66 | 0.059187 | 0.014879 | -0.059175 | -0.014871 | 1.2191e-05 | 7.7525e-06 | 0.090198 | 0.090198 | 0.090198 | 0.97659 | -0.44941 | 0.97637 | -0.45373 | 24.7797
67 | 0.00043851 | 0.00010938 | -0.00043851 | -0.00010943 | 6.3832e-10 | -4.9586e-08 | 0.00066028 | 0.0006603 | 0.0006603 | 0.98795 | -0.22895 | 0.98795 | -0.22898 | 0.1814
68 | 0.01449 | 0.0036556 | -0.014477 | -0.0036485 | 1.2556e-05 | 7.1423e-06 | 0.021863 | 0.021863 | 0.021863 | 0.98658 | -0.25556 | 0.98564 | -0.27368 | 6.0064
69 | 0.068449 | 0.017374 | -0.068379 | -0.017329 | 6.941e-05 | 4.4201e-05 | 0.10332 | 0.10332 | 0.10332 | 0.98658 | -0.25556 | 0.98548 | -0.27667 | 28.3838
70 | 0.0016645 | 0.0004163 | -0.0016645 | -0.00041643 | 2.6772e-08 | -1.2937e-07 | 0.0025024 | 0.0025024 | 0.0025024 | 0.98968 | -0.19589 | 0.98967 | -0.19623 | 0.68748
71 | 0.033072 | 0.0083401 | -0.033058 | -0.0083316 | 1.3626e-05 | 8.5318e-06 | 0.049743 | 0.049743 | 0.049743 | 0.98968 | -0.19589 | 0.98924 | -0.2045 | 13.6657
72 | -0.25253 | -0.064457 | 0.2532 | 0.064882 | 0.00066425 | 0.00042449 | 0.37952 | 0.37952 | 0.37952 | 0.99121 | -0.16654 | 0.99406 | -0.11225 | 52.1318
73 | 0.065059 | 0.016497 | -0.064986 | -0.01645 | 7.3707e-05 | 4.6914e-05 | 0.098304 | 0.098304 | 0.098304 | 0.98548 | -0.27667 | 0.98426 | -0.30026 | 27.0066
74 | 0.0028665 | 0.00071833 | -0.0028664 | -0.00071839 | 5.3604e-08 | -6.0746e-08 | 0.0043526 | 0.0043526 | 0.0043526 | 0.97995 | -0.38431 | 0.97993 | -0.3847 | 1.1958
75 | -0.0028665 | -0.00071833 | 0.0028665 | 0.00071828 | 4.2456e-08 | -4.8117e-08 | 0.0043526 | 0.0043526 | 0.0043526 | 0.97995 | -0.38431 | 0.97996 | -0.384 | 1.1958
76 | 0.055994 | 0.014103 | -0.05597 | -0.014088 | 2.4022e-05 | 1.5263e-05 | 0.085049 | 0.085049 | 0.085049 | 0.97996 | -0.384 | 0.9795 | -0.39297 | 23.3652
77 | -0.058861 | -0.014821 | 0.058904 | 0.014848 | 4.2892e-05 | 2.727e-05 | 0.089402 | 0.089402 | 0.089402 | 0.97996 | -0.384 | 0.98074 | -0.36877 | 24.561
78 | 0.060969 | 0.015387 | -0.060914 | -0.015352 | 5.5054e-05 | 3.5018e-05 | 0.092452 | 0.092452 | 0.092452 | 0.98171 | -0.34989 | 0.98074 | -0.36877 | 25.3989
79 | -0.060969 | -0.015387 | 0.061062 | 0.015446 | 9.2184e-05 | 5.8633e-05 | 0.092452 | 0.092452 | 0.092452 | 0.98171 | -0.34989 | 0.98333 | -0.31838 | 25.3989
80 | -0.063004 | -0.015933 | 0.063059 | 0.015968 | 5.4797e-05 | 3.4866e-05 | 0.095392 | 0.095391 | 0.095392 | 0.98333 | -0.31838 | 0.98426 | -0.30026 | 26.2065
81 | 0.0016645 | 0.00041643 | -0.0016645 | -0.00041654 | 2.2729e-08 | -1.0982e-07 | 0.0025024 | 0.0025025 | 0.0025025 | 0.98967 | -0.19623 | 0.98965 | -0.19651 | 0.68749
82 | 0.031216 | 0.0078698 | -0.0312 | -0.0078599 | 1.59e-05 | 9.9294e-06 | 0.046972 | 0.046972 | 0.046972 | 0.98924 | -0.2045 | 0.98869 | -0.21515 | 12.9044
83 | 0.0039493 | 0.00098752 | -0.003949 | -0.00098758 | 2.1464e-07 | -6.0151e-08 | 0.0060189 | 0.006019 | 0.006019 | 0.97622 | -0.45686 | 0.97616 | -0.45801 | 1.6536
84 | -0.0016081 | -0.00040273 | 0.0016081 | 0.00040268 | 9.542e-09 | -4.6809e-08 | 0.0024515 | 0.0024515 | 0.0024515 | 0.97602 | -0.46063 | 0.97603 | -0.46051 | 0.67349
85 | 0.0016081 | 0.00040273 | -0.001608 | -0.00040282 | 1.9313e-08 | -9.4737e-08 | 0.0024515 | 0.0024515 | 0.0024515 | 0.97602 | -0.46063 | 0.97601 | -0.46088 | 0.6735
86 | -0.0033404 | -0.00083539 | 0.0033408 | 0.00083513 | 3.9717e-07 | -2.5642e-07 | 0.0050919 | 0.0050918 | 0.0050919 | 0.97603 | -0.46051 | 0.97616 | -0.45801 | 1.3989
87 | 0.0017323 | 0.00043271 | -0.001732 | -0.00043385 | 2.751e-07 | -1.1385e-06 | 0.0026405 | 0.0026409 | 0.0026409 | 0.97603 | -0.46051 | 0.97586 | -0.46384 | 0.72553
88 | 0.0007066 | 0.0001769 | -0.00070659 | -0.00017709 | 6.6932e-09 | -1.8793e-07 | 0.0010772 | 0.0010773 | 0.0010773 | 0.97601 | -0.46088 | 0.976 | -0.46108 | 0.29596
89 | 0.0081862 | 0.0020508 | -0.0081833 | -0.0020496 | 2.9857e-06 | 1.2823e-06 | 0.01253 | 0.01253 | 0.01253 | 0.97215 | -0.53683 | 0.97177 | -0.54449 | 3.4423
90 | -0.0081862 | -0.0020508 | 0.0081863 | 0.0020509 | 1.0309e-07 | 4.4265e-08 | 0.01253 | 0.01253 | 0.01253 | 0.97215 | -0.53683 | 0.97217 | -0.53657 | 3.4423
91 | 0.0062848 | 0.0015742 | -0.0062817 | -0.0015734 | 3.1284e-06 | 8.8681e-07 | 0.0096233 | 0.0096237 | 0.0096237 | 0.97177 | -0.54449 | 0.97124 | -0.55495 | 2.6439
92 | 0.0018984 | 0.00047531 | -0.0018984 | -0.00047553 | 6.7136e-08 | -2.1951e-07 | 0.0029068 | 0.0029069 | 0.0029069 | 0.97177 | -0.54449 | 0.97173 | -0.54524 | 0.7986
93 | -0.0098272 | -0.0024621 | 0.0098279 | 0.0024625 | 6.71e-07 | 3.3137e-07 | 0.015041 | 0.015041 | 0.015041 | 0.97217 | -0.53657 | 0.97224 | -0.53514 | 4.1323
94 | 0.0012067 | 0.00030224 | -0.0012067 | -0.00030242 | 1.9891e-08 | -1.7933e-07 | 0.0018487 | 0.0018487 | 0.0018487 | 0.97124 | -0.55495 | 0.97122 | -0.5553 | 0.50789
95 | 0.005075 | 0.0012711 | -0.0050746 | -0.0012711 | 3.8272e-07 | 3.6029e-08 | 0.0077751 | 0.0077751 | 0.0077751 | 0.97124 | -0.55495 | 0.97116 | -0.55653 | 2.136
96 | 0.0010441 | 0.00026143 | -0.0010441 | -0.00026167 | 1.9596e-08 | -2.4071e-07 | 0.0015987 | 0.0015988 | 0.0015988 | 0.97173 | -0.54524 | 0.97171 | -0.54563 | 0.43924
97 | 0.001732 | 0.00043385 | -0.001732 | -0.00043407 | 5.4978e-08 | -2.2742e-07 | 0.0026409 | 0.002641 | 0.002641 | 0.97586 | -0.46384 | 0.97583 | -0.46451 | 0.72556
98 | -0.028792 | -0.007234 | 0.028799 | 0.0072385 | 7.1791e-06 | 4.4713e-06 | 0.043979 | 0.043979 | 0.043979 | 0.97432 | -0.49407 | 0.97458 | -0.48885 | 12.0821
99 | 0.028792 | 0.007234 | -0.028774 | -0.0072226 | 1.8291e-05 | 1.1392e-05 | 0.043979 | 0.043979 | 0.043979 | 0.97432 | -0.49407 | 0.97364 | -0.50739 | 12.0822
100 | 0.02705 | 0.0067906 | -0.027034 | -0.0067805 | 1.6306e-05 | 1.0119e-05 | 0.041345 | 0.041345 | 0.041345 | 0.97364 | -0.50739 | 0.973 | -0.52004 | 11.3584
101 | 0.0037389 | 0.00093632 | -0.0037388 | -0.00093635 | 9.1338e-08 | -3.3378e-08 | 0.0057285 | 0.0057286 | 0.0057286 | 0.97116 | -0.55653 | 0.97113 | -0.55705 | 1.5738
102 | 0.0023258 | 0.00058231 | -0.0023258 | -0.00058236 | 2.7491e-08 | -5.5002e-08 | 0.0035491 | 0.0035491 | 0.0035491 | 0.97509 | -0.47912 | 0.97507 | -0.47937 | 0.97503
103 | 0.0016565 | 0.00041502 | -0.0016564 | -0.00041514 | 2.7389e-08 | -1.2504e-07 | 0.0025278 | 0.0025278 | 0.0025278 | 0.97509 | -0.47912 | 0.97507 | -0.47947 | 0.69446
104 | 0.0014075 | 0.00035237 | -0.0014074 | -0.00035273 | 5.6371e-08 | -3.6212e-07 | 0.0021588 | 0.0021589 | 0.0021589 | 0.97009 | -0.57766 | 0.97005 | -0.5785 | 0.5931
105 | -0.007675 | -0.0019222 | 0.007679 | 0.0019238 | 3.9948e-06 | 1.6028e-06 | 0.011759 | 0.011759 | 0.011759 | 0.97118 | -0.55606 | 0.97173 | -0.54513 | 3.2305
106 | 0.00098911 | 0.00024761 | -0.00098911 | -0.00024773 | 8.2397e-09 | -1.1553e-07 | 0.0015078 | 0.0015078 | 0.0015078 | 0.9761 | -0.45916 | 0.97609 | -0.45934 | 0.41423
107 | 0.00043851 | 0.00010943 | -0.0004385 | -0.00010966 | 3.0018e-09 | -2.3315e-07 | 0.0006603 | 0.00066038 | 0.00066038 | 0.98795 | -0.22898 | 0.98794 | -0.22912 | 0.18142
108 | 0.0004385 | 0.00010966 | -0.0004385 | -0.0001099 | 3.0913e-09 | -2.4003e-07 | 0.00066038 | 0.00066046 | 0.00066046 | 0.98794 | -0.22912 | 0.98793 | -0.22927 | 0.18145
109 | -0.0059943 | -0.0015023 | 0.005995 | 0.0015025 | 7.024e-07 | 1.5961e-07 | 0.0090621 | 0.009062 | 0.0090621 | 0.98427 | -0.30114 | 0.98439 | -0.29868 | 2.4896
110 | -0.013539 | -0.0033931 | 0.013542 | 0.0033951 | 3.6606e-06 | 2.0464e-06 | 0.020465 | 0.020465 | 0.020465 | 0.98439 | -0.29868 | 0.98468 | -0.293 | 5.6223
111 | 0.25706 | 0.066128 | -0.25634 | -0.065669 | 0.00071817 | 0.00045895 | 0.38422 | 0.38422 | 0.38422 | 0.9971 | -0.054611 | 0.99406 | -0.11225 | 52.7778
112 | -0.028836 | -0.0072402 | 0.028852 | 0.0072505 | 1.6575e-05 | 1.031e-05 | 0.043519 | 0.043519 | 0.043519 | 0.98606 | -0.26611 | 0.98668 | -0.25407 | 11.9558
113 | 0.0019307 | 0.00048376 | -0.0019307 | -0.00048387 | 3.6176e-08 | -1.1799e-07 | 0.002933 | 0.0029331 | 0.0029331 | 0.9795 | -0.39297 | 0.97948 | -0.39336 | 0.80579
114 | 0.00020515 | 5.0646e-05 | -0.00020514 | -5.1414e-05 | 2.1849e-09 | -7.6747e-07 | 0.00031004 | 0.00031031 | 0.00031031 | 0.98373 | -0.31095 | 0.98372 | -0.31118 | 0.08525
115 | 0.00051006 | 0.00012722 | -0.00051005 | -0.00012783 | 1.0641e-08 | -6.1328e-07 | 0.0007667 | 0.00076692 | 0.00076692 | 0.98965 | -0.19651 | 0.98963 | -0.19695 | 0.21069
116 | 0.030683 | 0.0077302 | -0.030666 | -0.0077197 | 1.6867e-05 | 1.0525e-05 | 0.046193 | 0.046194 | 0.046194 | 0.98869 | -0.21515 | 0.98809 | -0.22665 | 12.6905
117 | -0.014503 | -0.0036368 | 0.014507 | 0.0036393 | 4.3131e-06 | 2.4703e-06 | 0.022187 | 0.022187 | 0.022187 | 0.97269 | -0.52627 | 0.973 | -0.52004 | 6.0953
118 | 0.002102 | 0.00052642 | -0.0021019 | -0.00052654 | 4.7947e-08 | -1.2281e-07 | 0.0032154 | 0.0032155 | 0.0032155 | 0.97269 | -0.52627 | 0.97266 | -0.52675 | 0.88338
119 | 0.012401 | 0.0031104 | -0.01239 | -0.0031043 | 1.1139e-05 | 6.1057e-06 | 0.018971 | 0.018972 | 0.018972 | 0.97269 | -0.52627 | 0.97173 | -0.54513 | 5.212
120 | 0.012527 | 0.0031412 | -0.012522 | -0.0031388 | 4.32e-06 | 2.3751e-06 | 0.019158 | 0.019158 | 0.019158 | 0.973 | -0.52004 | 0.97264 | -0.52727 | 5.2632
121 | 0.0011281 | 0.00028248 | -0.0011281 | -0.00028273 | 2.3361e-08 | -2.4465e-07 | 0.0017257 | 0.0017258 | 0.0017258 | 0.97266 | -0.52675 | 0.97264 | -0.52719 | 0.47413
122 | 0.0047105 | 0.0011805 | -0.0047104 | -0.0011805 | 1.1065e-07 | 5.6389e-10 | 0.0072132 | 0.0072132 | 0.0072132 | 0.97173 | -0.54513 | 0.97171 | -0.54563 | 1.9816
123 | 0.010904 | 0.0027333 | -0.010902 | -0.0027319 | 2.5429e-06 | 1.3251e-06 | 0.016682 | 0.016683 | 0.016683 | 0.97264 | -0.52727 | 0.97239 | -0.53217 | 4.5831
124 | -0.0098279 | -0.0024625 | 0.0098293 | 0.0024631 | 1.389e-06 | 6.8592e-07 | 0.015041 | 0.015041 | 0.015041 | 0.97224 | -0.53514 | 0.97239 | -0.53217 | 4.1323
125 | 0.0023515 | 0.00058887 | -0.0023514 | -0.00058895 | 3.8524e-08 | -7.3261e-08 | 0.0036029 | 0.0036029 | 0.0036029 | 0.97113 | -0.55705 | 0.97111 | -0.55739 | 0.98981
126 | 0.0013874 | 0.00034748 | -0.0013873 | -0.0003477 | 3.2314e-08 | -2.1526e-07 | 0.0021257 | 0.0021258 | 0.0021258 | 0.97113 | -0.55705 | 0.97111 | -0.55754 | 0.584
127 | 0.00098782 | 0.00024748 | -0.00098782 | -0.00024757 | 6.3605e-09 | -8.903e-08 | 0.0015074 | 0.0015075 | 0.0015075 | 0.97507 | -0.47937 | 0.97507 | -0.47951 | 0.41414
128 | 0.001338 | 0.00033488 | -0.0013379 | -0.00033521 | 4.5259e-08 | -3.3214e-07 | 0.0020417 | 0.0020418 | 0.0020418 | 0.97507 | -0.47937 | 0.97504 | -0.48008 | 0.56094
129 | 0.0013379 | 0.00033521 | -0.0013379 | -0.00033532 | 1.4307e-08 | -1.0498e-07 | 0.0020418 | 0.0020419 | 0.0020419 | 0.97504 | -0.48008 | 0.97503 | -0.48031 | 0.56095
130 | 0.0012415 | 0.00031088 | -0.0012415 | -0.00031115 | 3.1182e-08 | -2.6433e-07 | 0.0019023 | 0.0019024 | 0.0019024 | 0.97111 | -0.55739 | 0.97109 | -0.55792 | 0.52263
131 | 0.0011099 | 0.00027806 | -0.0011099 | -0.00027817 | 9.6716e-09 | -1.0413e-07 | 0.0017007 | 0.0017007 | 0.0017007 | 0.97111 | -0.55739 | 0.97111 | -0.55757 | 0.46723
132 | 0.00098911 | 0.00024773 | -0.00098909 | -0.00024789 | 1.1622e-08 | -1.6295e-07 | 0.0015078 | 0.0015079 | 0.0015079 | 0.97609 | -0.45934 | 0.97607 | -0.45958 | 0.41425
133 | -0.02943 | -0.0073953 | 0.029446 | 0.0074053 | 1.6081e-05 | 1.0013e-05 | 0.04439 | 0.04439 | 0.04439 | 0.98668 | -0.25407 | 0.98727 | -0.24263 | 12.195
134 | -0.030057 | -0.0075586 | 0.03008 | 0.0075729 | 2.2965e-05 | 1.4316e-05 | 0.045311 | 0.045311 | 0.045311 | 0.98727 | -0.24263 | 0.98809 | -0.22665 | 12.4482

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.27411 | 0.070259

## res_load
| p_mw | q_mvar
0 | 0.0044984 | 0.0011274
1 | 0.00077471 | 0.00019416
2 | 0.00060261 | 0.00015103
3 | 0.0028146 | 0.0007054
4 | 0.0014772 | 0.00037022
5 | 0.0019255 | 0.00048258
6 | 0.0018358 | 0.00046009
7 | 0.0019199 | 0.00048118
8 | 0.0090666 | 0.0022723
9 | 0.0043288 | 0.0010849
10 | 0.0027612 | 0.00069201
11 | 0.0045105 | 0.0011304
12 | 0.00279 | 0.00069923
13 | 0.002843 | 0.00071252
14 | 0.053735 | 0.013467
15 | 0.00037364 | 9.3642e-05
16 | 0.00049508 | 0.00012408
17 | 0.00034003 | 8.522e-05
18 | 0.0019848 | 0.00049744
19 | 0.0013301 | 0.00033335
20 | 0.0015679 | 0.00039296
21 | 0.051962 | 0.013023
22 | 0.00045857 | 0.00011493
23 | 0.0016119 | 0.00040398
24 | 0.0027555 | 0.0006906
25 | 0.00332 | 0.00083206
26 | 0.0028664 | 0.00071839
27 | 0.0020105 | 0.00050387
28 | 0.0019426 | 0.00048686
29 | 0.0018423 | 0.00046172
30 | 0.00060346 | 0.00015124
31 | 0.00090144 | 0.00022592
32 | 0.0016409 | 0.00041124
33 | 0.00085427 | 0.0002141
34 | 0.001732 | 0.00043407
35 | 0.0017238 | 0.00043204
36 | 0.0012067 | 0.00030242
37 | 0.0013357 | 0.00033476
38 | 0.00060827 | 0.00015245
39 | 0.0013392 | 0.00033562
40 | 0.011084 | 0.002778
41 | 0.00094237 | 0.00023618
42 | 0.0010281 | 0.00025767
43 | 0.0004385 | 0.0001099
44 | 0.0059943 | 0.0015023
45 | 0.0075436 | 0.0018906
46 | 0.0031156 | 0.00078084
47 | 0.0043206 | 0.0010828
48 | 0.00092132 | 0.0002309
49 | 0.00031622 | 7.9252e-05
50 | 0.00066193 | 0.0001659
51 | 0.0019211 | 0.00048148
52 | 0.013741 | 0.0034438
53 | 0.0031417 | 0.00078738
54 | 0.0019266 | 0.00048284
55 | 0.0011544 | 0.00028932
56 | 0.00051735 | 0.00012966
57 | 0.00070659 | 0.00017709
58 | 0.0009738 | 0.00024406
59 | 0.0016181 | 0.00040554
60 | 0.0010725 | 0.00026879
61 | 0.0014074 | 0.00035273
62 | 0.0010441 | 0.00026167
63 | 0.0016564 | 0.00041514
64 | 0.0013379 | 0.00033532
65 | 0.00098782 | 0.00024757
66 | 0.00020514 | 5.1414e-05
67 | 0.0019307 | 0.00048387
68 | 0.0013873 | 0.0003477
69 | 0.0012415 | 0.00031115
70 | 0.0011099 | 0.00027817
71 | 0.00098909 | 0.00024789
72 | 0.0047104 | 0.0011805
73 | 0.0011281 | 0.00028273
74 | 0.00057764 | 0.00014477
75 | 0.00061139 | 0.00015323
76 | 0.00058592 | 0.00014685
77 | 0.00051005 | 0.00012783

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1