## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-484_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-484_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-484_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-484_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-484_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-484_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-484_0_4_node_21 | 0.4 | n |  | TRUE
7 | bus_LV_261-484_0_4_node_18 | 0.4 | n |  | TRUE
8 | bus_LV_261-484_0_4_node_23 | 0.4 | n |  | TRUE
9 | bus_LV_261-484_0_4_node_19 | 0.4 | n |  | TRUE
10 | bus_LV_261-484_0_4_node_16 | 0.4 | n |  | TRUE
11 | bus_LV_261-484_0_4_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_261-484_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_261-484_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_261-484_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_261-484_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_261-484_0_4_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_261-484_0_4_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_261-484_0_4_node_123 | 0.4 | n |  | TRUE
19 | bus_LV_261-484_0_4_node_124 | 0.4 | n |  | TRUE
20 | bus_LV_261-484_0_4_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_261-484_0_4_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_261-484_0_4_node_120 | 0.4 | n |  | TRUE
23 | bus_LV_261-484_0_4_node_125 | 0.4 | n |  | TRUE
24 | bus_LV_261-484_0_4_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_261-484_0_4_node_113 | 0.4 | n |  | TRUE
26 | bus_LV_261-484_0_4_node_126 | 0.4 | n |  | TRUE
27 | bus_LV_261-484_0_4_node_46 | 0.4 | n |  | TRUE
28 | bus_LV_261-484_0_4_node_55 | 0.4 | n |  | TRUE
29 | bus_LV_261-484_0_4_node_122 | 0.4 | n |  | TRUE
30 | bus_LV_261-484_0_4_node_118 | 0.4 | n |  | TRUE
31 | bus_LV_261-484_0_4_node_112 | 0.4 | n |  | TRUE
32 | bus_LV_261-484_0_4_node_48 | 0.4 | n |  | TRUE
33 | bus_LV_261-484_0_4_node_53 | 0.4 | n |  | TRUE
34 | bus_LV_261-484_0_4_node_20 | 0.4 | n |  | TRUE
35 | bus_LV_261-484_0_4_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_261-484_0_4_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_261-484_0_4_node_76 | 0.4 | n |  | TRUE
38 | bus_LV_261-484_0_4_node_26 | 0.4 | n |  | TRUE
39 | bus_LV_261-484_0_4_node_47 | 0.4 | n |  | TRUE
40 | bus_LV_261-484_0_4_node_27 | 0.4 | n |  | TRUE
41 | bus_LV_261-484_0_4_node_69 | 0.4 | n |  | TRUE
42 | bus_LV_261-484_0_4_node_42 | 0.4 | n |  | TRUE
43 | bus_LV_261-484_0_4_node_39 | 0.4 | n |  | TRUE
44 | bus_LV_261-484_0_4_node_28 | 0.4 | n |  | TRUE
45 | bus_LV_261-484_0_4_node_33 | 0.4 | n |  | TRUE
46 | bus_LV_261-484_0_4_node_40 | 0.4 | n |  | TRUE
47 | bus_LV_261-484_0_4_node_81 | 0.4 | n |  | TRUE
48 | bus_LV_261-484_0_4_node_29 | 0.4 | n |  | TRUE
49 | bus_LV_261-484_0_4_node_98 | 0.4 | n |  | TRUE
50 | bus_LV_261-484_0_4_node_45 | 0.4 | n |  | TRUE
51 | bus_LV_261-484_0_4_node_87 | 0.4 | n |  | TRUE
52 | bus_LV_261-484_0_4_node_30 | 0.4 | n |  | TRUE
53 | bus_LV_261-484_0_4_node_102 | 0.4 | n |  | TRUE
54 | bus_LV_261-484_0_4_node_38 | 0.4 | n |  | TRUE
55 | bus_LV_261-484_0_4_node_99 | 0.4 | n |  | TRUE
56 | bus_LV_261-484_0_4_node_31 | 0.4 | n |  | TRUE
57 | bus_LV_261-484_0_4_node_71 | 0.4 | n |  | TRUE
58 | bus_LV_261-484_0_4_node_85 | 0.4 | n |  | TRUE
59 | bus_LV_261-484_0_4_node_32 | 0.4 | n |  | TRUE
60 | bus_LV_261-484_0_4_node_35 | 0.4 | n |  | TRUE
61 | bus_LV_261-484_0_4_node_128 | 0.4 | n |  | TRUE
62 | bus_LV_261-484_0_4_node_127 | 0.4 | n |  | TRUE
63 | bus_LV_261-484_0_4_node_129 | 0.4 | n |  | TRUE
64 | bus_LV_261-484_0_4_node_36 | 0.4 | n |  | TRUE
65 | bus_LV_261-484_0_4_node_92 | 0.4 | n |  | TRUE
66 | bus_LV_261-484_0_4_node_44 | 0.4 | n |  | TRUE
67 | bus_LV_261-484_0_4_node_94 | 0.4 | n |  | TRUE
68 | bus_LV_261-484_0_4_node_74 | 0.4 | n |  | TRUE
69 | bus_LV_261-484_0_4_node_68 | 0.4 | n |  | TRUE
70 | bus_LV_261-484_0_4_node_65 | 0.4 | n |  | TRUE
71 | bus_LV_261-484_0_4_node_77 | 0.4 | n |  | TRUE
72 | bus_LV_261-484_0_4_node_41 | 0.4 | n |  | TRUE
73 | bus_LV_261-484_0_4_node_70 | 0.4 | n |  | TRUE
74 | bus_LV_261-484_0_4_node_75 | 0.4 | n |  | TRUE
75 | bus_LV_261-484_0_4_node_97 | 0.4 | n |  | TRUE
76 | bus_LV_261-484_0_4_node_110 | 0.4 | n |  | TRUE
77 | bus_LV_261-484_0_4_node_106 | 0.4 | n |  | TRUE
78 | bus_LV_261-484_0_4_node_49 | 0.4 | n |  | TRUE
79 | bus_LV_261-484_0_4_node_121 | 0.4 | n |  | TRUE
80 | bus_LV_261-484_0_4_node_79 | 0.4 | n |  | TRUE
81 | bus_LV_261-484_0_4_node_104 | 0.4 | n |  | TRUE
82 | bus_LV_261-484_0_4_node_105 | 0.4 | n |  | TRUE
83 | bus_LV_261-484_0_4_node_100 | 0.4 | n |  | TRUE
84 | bus_LV_261-484_0_4_node_83 | 0.4 | n |  | TRUE
85 | bus_LV_261-484_0_4_node_90 | 0.4 | n |  | TRUE
86 | bus_LV_261-484_0_4_node_95 | 0.4 | n |  | TRUE
87 | bus_LV_261-484_0_4_node_73 | 0.4 | n |  | TRUE
88 | bus_LV_261-484_0_4_node_66 | 0.4 | n |  | TRUE
89 | bus_LV_261-484_0_4_node_78 | 0.4 | n |  | TRUE
90 | bus_LV_261-484_0_4_node_72 | 0.4 | n |  | TRUE
91 | bus_LV_261-484_0_4_node_60 | 0.4 | n |  | TRUE
92 | bus_LV_261-484_0_4_node_61 | 0.4 | n |  | TRUE
93 | bus_LV_261-484_0_4_node_96 | 0.4 | n |  | TRUE
94 | bus_LV_261-484_0_4_node_103 | 0.4 | n |  | TRUE
95 | bus_LV_261-484_0_4_node_50 | 0.4 | n |  | TRUE
96 | bus_LV_261-484_0_4_node_59 | 0.4 | n |  | TRUE
97 | bus_LV_261-484_0_4_node_58 | 0.4 | n |  | TRUE
98 | bus_LV_261-484_0_4_node_51 | 0.4 | n |  | TRUE
99 | bus_LV_261-484_0_4_node_52 | 0.4 | n |  | TRUE
100 | bus_LV_261-484_0_4_node_54 | 0.4 | n |  | TRUE
101 | bus_LV_261-484_0_4_node_56 | 0.4 | n |  | TRUE
102 | bus_LV_261-484_0_4_node_57 | 0.4 | n |  | TRUE
103 | bus_LV_261-484_0_4_node_62 | 0.4 | n |  | TRUE
104 | bus_LV_261-484_0_4_node_63 | 0.4 | n |  | TRUE
105 | bus_LV_261-484_0_4_node_64 | 0.4 | n |  | TRUE
106 | bus_LV_261-484_0_4_node_67 | 0.4 | n |  | TRUE
107 | bus_LV_261-484_0_4_node_80 | 0.4 | n |  | TRUE
108 | bus_LV_261-484_0_4_node_82 | 0.4 | n |  | TRUE
109 | bus_LV_261-484_0_4_node_84 | 0.4 | n |  | TRUE
110 | bus_LV_261-484_0_4_node_86 | 0.4 | n |  | TRUE
111 | bus_LV_261-484_0_4_node_88 | 0.4 | n |  | TRUE
112 | bus_LV_261-484_0_4_node_89 | 0.4 | n |  | TRUE
113 | bus_LV_261-484_0_4_node_91 | 0.4 | n |  | TRUE
114 | bus_LV_261-484_0_4_node_93 | 0.4 | n |  | TRUE
115 | bus_LV_261-484_0_4_node_101 | 0.4 | n |  | TRUE
116 | bus_LV_261-484_0_4_node_114 | 0.4 | n |  | TRUE
117 | bus_LV_261-484_0_4_node_107 | 0.4 | n |  | TRUE
118 | bus_LV_261-484_0_4_node_119 | 0.4 | n |  | TRUE
119 | bus_LV_261-484_0_4_node_108 | 0.4 | n |  | TRUE
120 | bus_LV_261-484_0_4_node_109 | 0.4 | n |  | TRUE
121 | bus_LV_261-484_0_4_node_111 | 0.4 | n |  | TRUE
122 | bus_LV_261-484_0_4_node_117 | 0.4 | n |  | TRUE
123 | bus_LV_261-484_0_4_node_115 | 0.4 | n |  | TRUE
124 | bus_LV_261-484_0_4_node_116 | 0.4 | n |  | TRUE
125 | bus_MV_528_0_node_25 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-484_0_4_load_0 | 0 | 0.010955 | 0.0027456 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-484_0_4_load_1 | 1 | 0.0013779 | 0.00034533 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-484_0_4_load_2 | 2 | 0.0025993 | 0.00065146 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-484_0_4_load_3 | 3 | 0.0018881 | 0.00047321 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-484_0_4_load_4 | 4 | 0.0026132 | 0.00065492 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-484_0_4_load_5 | 5 | 0.001688 | 0.00042305 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-484_0_4_load_18 | 7 | 0.0073764 | 0.0018487 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-484_0_4_load_23 | 8 | 0.0065474 | 0.0016409 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-484_0_4_load_19 | 9 | 0.001912 | 0.00047919 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-484_0_4_load_6 | 11 | 0.01786 | 0.0044763 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-484_0_4_load_7 | 12 | 0.006574 | 0.0016476 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-484_0_4_load_9 | 14 | 0.0084331 | 0.0021135 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-484_0_4_load_10 | 15 | 0.0014761 | 0.00036996 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-484_0_4_load_17 | 17 | 0.0005982 | 0.00014992 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-484_0_4_load_124 | 19 | 0.00070109 | 0.00017571 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-484_0_4_load_120 | 22 | 0.003521 | 0.00088244 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-484_0_4_load_125 | 23 | 0.001792 | 0.00044912 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-484_0_4_load_113 | 25 | 0.0045153 | 0.0011316 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-484_0_4_load_126 | 26 | 0.0013213 | 0.00033115 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-484_0_4_load_46 | 27 | 0.0010693 | 0.00026799 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-484_0_4_load_55 | 28 | 0.0010801 | 0.0002707 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-484_0_4_load_122 | 29 | 0.00060713 | 0.00015216 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-484_0_4_load_118 | 30 | 0.0021014 | 0.00052665 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-484_0_4_load_112 | 31 | 0.0037631 | 0.00094312 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-484_0_4_load_48 | 32 | 0.0055519 | 0.0013914 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-484_0_4_load_53 | 33 | 0.00076118 | 0.00019077 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-484_0_4_load_20 | 34 | 0.0016964 | 0.00042515 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-484_0_4_load_22 | 35 | 0.0023878 | 0.00059843 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-484_0_4_load_25 | 36 | 0.0013656 | 0.00034225 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-484_0_4_load_76 | 37 | 0.0014754 | 0.00036977 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-484_0_4_load_26 | 38 | 0.0014032 | 0.00035168 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-484_0_4_load_69 | 41 | 0.0025482 | 0.00063864 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-484_0_4_load_81 | 47 | 0.0051834 | 0.0012991 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-484_0_4_load_98 | 49 | 0.0034781 | 0.00087168 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-484_0_4_load_87 | 51 | 0.005097 | 0.0012774 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-484_0_4_load_99 | 55 | 0.0042419 | 0.0010631 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-484_0_4_load_71 | 57 | 0.0041307 | 0.0010352 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-484_0_4_load_85 | 58 | 0.0036444 | 0.00091337 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-484_0_4_load_128 | 61 | 0.0033417 | 0.00083751 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-484_0_4_load_127 | 62 | 0.0085843 | 0.0021514 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-484_0_4_load_129 | 63 | 0.0054426 | 0.001364 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-484_0_4_load_92 | 65 | 0.0027456 | 0.0006881 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-484_0_4_load_94 | 67 | 0.0015286 | 0.00038309 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-484_0_4_load_74 | 68 | 0.0067288 | 0.0016864 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-484_0_4_load_68 | 69 | 0.0039475 | 0.00098933 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-484_0_4_load_65 | 70 | 0.0096437 | 0.0024169 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-484_0_4_load_77 | 71 | 0.0068847 | 0.0017255 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-484_0_4_load_75 | 74 | 0.0040763 | 0.0010216 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-484_0_4_load_97 | 75 | 0.0036016 | 0.00090263 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-484_0_4_load_110 | 76 | 0.0023417 | 0.0005869 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-484_0_4_load_106 | 77 | 0.0048066 | 0.0012046 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-484_0_4_load_49 | 78 | 0.0016062 | 0.00040255 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-484_0_4_load_121 | 79 | 0.0022166 | 0.00055553 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-484_0_4_load_79 | 80 | 0.001591 | 0.00039873 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-484_0_4_load_104 | 81 | 0.002374 | 0.00059499 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-484_0_4_load_105 | 82 | 0.0038339 | 0.00096088 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-484_0_4_load_100 | 83 | 0.0039894 | 0.00099984 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-484_0_4_load_83 | 84 | 0.0058362 | 0.0014627 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-484_0_4_load_90 | 85 | 0.0033038 | 0.00082802 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-484_0_4_load_95 | 86 | 0.0049982 | 0.0012527 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-484_0_4_load_73 | 87 | 0.012224 | 0.0030637 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-484_0_4_load_66 | 88 | 0.0021697 | 0.00054378 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-484_0_4_load_78 | 89 | 0.006696 | 0.0016782 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-484_0_4_load_72 | 90 | 0.0091932 | 0.002304 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-484_0_4_load_60 | 91 | 0.0065483 | 0.0016412 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-484_0_4_load_96 | 93 | 0.0035311 | 0.00088497 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-484_0_4_load_103 | 94 | 0.001879 | 0.00047091 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-484_0_4_load_50 | 95 | 0.0011634 | 0.00029158 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-484_0_4_load_59 | 96 | 0.0021591 | 0.00054111 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-484_0_4_load_58 | 97 | 0.0012436 | 0.00031168 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-484_0_4_load_51 | 98 | 0.00067994 | 0.00017041 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-484_0_4_load_52 | 99 | 0.0012068 | 0.00030246 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-484_0_4_load_54 | 100 | 0.0010615 | 0.00026605 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-484_0_4_load_56 | 101 | 0.0010845 | 0.0002718 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-484_0_4_load_57 | 102 | 0.0022799 | 0.0005714 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-484_0_4_load_62 | 103 | 0.0022123 | 0.00055445 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-484_0_4_load_63 | 104 | 0.0031265 | 0.00078356 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-484_0_4_load_67 | 106 | 0.0033001 | 0.00082709 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-484_0_4_load_80 | 107 | 0.0044823 | 0.0011234 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-484_0_4_load_82 | 108 | 0.005095 | 0.0012769 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-484_0_4_load_84 | 109 | 0.0036253 | 0.00090858 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-484_0_4_load_86 | 110 | 0.0043493 | 0.00109 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_261-484_0_4_load_88 | 111 | 0.0070465 | 0.001766 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_261-484_0_4_load_91 | 113 | 0.0017996 | 0.00045102 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_261-484_0_4_load_93 | 114 | 0.0045075 | 0.0011297 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_261-484_0_4_load_101 | 115 | 0.0059636 | 0.0014946 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_261-484_0_4_load_114 | 116 | 0.0033367 | 0.00083626 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_261-484_0_4_load_107 | 117 | 0.0033638 | 0.00084306 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_261-484_0_4_load_119 | 118 | 0.0042503 | 0.0010652 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_261-484_0_4_load_108 | 119 | 0.0046372 | 0.0011622 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_261-484_0_4_load_109 | 120 | 0.010909 | 0.002734 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_261-484_0_4_load_111 | 121 | 0.0023593 | 0.0005913 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_261-484_0_4_load_117 | 122 | 0.0016618 | 0.00041649 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_261-484_0_4_load_115 | 123 | 0.0068246 | 0.0017104 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_261-484_0_4_load_116 | 124 | 0.0035558 | 0.00089116 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 68 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-484_0_4_line_0 |  | 0 | 1 | 0.01121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-484_0_4_line_1 |  | 0 | 2 | 0.0055855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-484_0_4_line_2 |  | 1 | 3 | 0.0225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-484_0_4_line_3 |  | 2 | 4 | 0.010523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-484_0_4_line_4 |  | 3 | 5 | 0.020504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-484_0_4_line_5 |  | 4 | 6 | 0.029753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-484_0_4_line_6 |  | 5 | 7 | 0.018744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-484_0_4_line_7 |  | 6 | 8 | 0.0059094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-484_0_4_line_8 |  | 6 | 9 | 0.011715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-484_0_4_line_9 |  | 7 | 10 | 0.035083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-484_0_4_line_10 |  | 8 | 36 | 0.020317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-484_0_4_line_11 |  | 9 | 34 | 0.017951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-484_0_4_line_12 |  | 10 | 27 | 0.011509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-484_0_4_line_13 |  | 10 | 14 | 0.0049675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-484_0_4_line_14 |  | 11 | 12 | 0.0030498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-484_0_4_line_15 |  | 11 | 13 | 0.0067732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-484_0_4_line_16 |  | 12 | 14 | 0.015208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-484_0_4_line_17 |  | 13 | 15 | 0.06038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-484_0_4_line_18 |  | 13 | 16 | 0.18871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-484_0_4_line_19 |  | 15 | 17 | 0.018859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-484_0_4_line_20 |  | 16 | 18 | 0.0043908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-484_0_4_line_21 |  | 16 | 19 | 0.014124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-484_0_4_line_22 |  | 17 | 28 | 0.0068506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-484_0_4_line_23 |  | 18 | 29 | 0.0071978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-484_0_4_line_24 |  | 20 | 21 | 0.027326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-484_0_4_line_25 |  | 20 | 22 | 0.0085165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-484_0_4_line_26 |  | 21 | 23 | 0.019149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-484_0_4_line_27 |  | 22 | 30 | 0.010977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-484_0_4_line_28 |  | 23 | 26 | 0.0028498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-484_0_4_line_29 |  | 24 | 25 | 0.043936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-484_0_4_line_30 |  | 24 | 26 | 0.020038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-484_0_4_line_31 |  | 25 | 31 | 0.024167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-484_0_4_line_32 |  | 27 | 32 | 0.0014136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-484_0_4_line_33 |  | 28 | 33 | 0.017072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-484_0_4_line_34 |  | 30 | 124 | 0.022694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-484_0_4_line_35 |  | 31 | 121 | 0.0015484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-484_0_4_line_36 |  | 32 | 39 | 0.019135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-484_0_4_line_37 |  | 33 | 98 | 0.0067635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-484_0_4_line_38 |  | 34 | 35 | 0.020034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-484_0_4_line_39 |  | 36 | 37 | 0.0011146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-484_0_4_line_40 |  | 37 | 74 | 0.0036411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-484_0_4_line_41 |  | 38 | 39 | 0.010458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-484_0_4_line_42 |  | 39 | 78 | 0.0074038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-484_0_4_line_43 |  | 40 | 41 | 0.018621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-484_0_4_line_44 |  | 40 | 42 | 0.021718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-484_0_4_line_45 |  | 40 | 43 | 0.018374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-484_0_4_line_46 |  | 41 | 79 | 0.0070646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-484_0_4_line_47 |  | 42 | 74 | 0.017316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-484_0_4_line_48 |  | 43 | 69 | 0.011968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-484_0_4_line_49 |  | 43 | 70 | 0.016366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-484_0_4_line_50 |  | 44 | 45 | 0.02245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-484_0_4_line_51 |  | 44 | 46 | 0.061511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-484_0_4_line_52 |  | 44 | 47 | 0.032741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-484_0_4_line_53 |  | 45 | 62 | 0.044502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-484_0_4_line_54 |  | 45 | 60 | 0.006551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-484_0_4_line_55 |  | 46 | 71 | 0.030752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-484_0_4_line_56 |  | 47 | 80 | 0.035248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-484_0_4_line_57 |  | 48 | 49 | 0.040934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-484_0_4_line_58 |  | 48 | 50 | 0.0081559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-484_0_4_line_59 |  | 48 | 51 | 0.011996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-484_0_4_line_60 |  | 49 | 66 | 0.028339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-484_0_4_line_61 |  | 50 | 76 | 0.0093604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-484_0_4_line_62 |  | 50 | 77 | 0.0016414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-484_0_4_line_63 |  | 52 | 53 | 0.035229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-484_0_4_line_64 |  | 52 | 54 | 0.007358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-484_0_4_line_65 |  | 52 | 55 | 0.021534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-484_0_4_line_66 |  | 53 | 81 | 0.0038378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-484_0_4_line_67 |  | 53 | 82 | 0.016402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-484_0_4_line_68 |  | 54 | 68 | 0.0073753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_261-484_0_4_line_69 |  | 54 | 56 | 0.0081617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_261-484_0_4_line_70 |  | 55 | 83 | 0.025038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-484_0_4_line_71 |  | 56 | 57 | 0.0087295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_261-484_0_4_line_72 |  | 56 | 58 | 0.00023408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-484_0_4_line_73 |  | 57 | 72 | 0.015574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
74 | LV_261-484_0_4_line_74 |  | 58 | 84 | 0.028658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-484_0_4_line_75 |  | 59 | 60 | 0.047068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-484_0_4_line_76 |  | 59 | 61 | 0.061353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-484_0_4_line_77 |  | 60 | 63 | 0.061581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-484_0_4_line_78 |  | 64 | 65 | 0.013911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-484_0_4_line_79 |  | 64 | 66 | 0.054632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-484_0_4_line_80 |  | 64 | 67 | 0.018476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_261-484_0_4_line_81 |  | 65 | 85 | 0.00021704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-484_0_4_line_82 |  | 66 | 75 | 0.015837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_261-484_0_4_line_83 |  | 67 | 86 | 0.00091759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_261-484_0_4_line_84 |  | 68 | 87 | 0.029188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_261-484_0_4_line_85 |  | 69 | 72 | 0.018255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
86 | LV_261-484_0_4_line_86 |  | 70 | 88 | 0.0056824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_261-484_0_4_line_87 |  | 71 | 89 | 0.02388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_261-484_0_4_line_88 |  | 72 | 73 | 0.014935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_261-484_0_4_line_89 |  | 73 | 90 | 0.01022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_261-484_0_4_line_90 |  | 75 | 93 | 0.022457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_261-484_0_4_line_91 |  | 77 | 94 | 0.012787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_261-484_0_4_line_92 |  | 78 | 95 | 0.030861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_261-484_0_4_line_93 |  | 80 | 107 | 0.021131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_261-484_0_4_line_94 |  | 81 | 116 | 0.014918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_261-484_0_4_line_95 |  | 82 | 117 | 0.02844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_261-484_0_4_line_96 |  | 83 | 115 | 0.02657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_261-484_0_4_line_97 |  | 84 | 109 | 0.015765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_261-484_0_4_line_98 |  | 85 | 112 | 0.014329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_261-484_0_4_line_99 |  | 88 | 106 | 0.00065312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_261-484_0_4_line_100 |  | 89 | 90 | 0.024653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_261-484_0_4_line_101 |  | 91 | 92 | 0.013897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_261-484_0_4_line_102 |  | 92 | 103 | 0.0031506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_261-484_0_4_line_103 |  | 92 | 104 | 0.018222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_261-484_0_4_line_104 |  | 94 | 115 | 0.021287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_261-484_0_4_line_105 |  | 95 | 96 | 0.010264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_261-484_0_4_line_106 |  | 96 | 97 | 0.0098084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_261-484_0_4_line_107 |  | 97 | 102 | 0.014791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_261-484_0_4_line_108 |  | 99 | 100 | 0.0062207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_261-484_0_4_line_109 |  | 100 | 101 | 0.019699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-484_0_4_line_110 |  | 101 | 102 | 0.0015194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_261-484_0_4_line_111 |  | 104 | 105 | 0.010422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_261-484_0_4_line_112 |  | 105 | 106 | 0.005318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_261-484_0_4_line_113 |  | 107 | 108 | 0.022811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_261-484_0_4_line_114 |  | 109 | 110 | 0.02489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_261-484_0_4_line_115 |  | 111 | 112 | 0.011228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_261-484_0_4_line_116 |  | 112 | 113 | 0.0030879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_261-484_0_4_line_117 |  | 113 | 114 | 0.010831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_261-484_0_4_line_118 |  | 116 | 118 | 0.013048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_261-484_0_4_line_119 |  | 117 | 119 | 0.0068275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_261-484_0_4_line_120 |  | 118 | 122 | 0.011981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_261-484_0_4_line_121 |  | 119 | 120 | 0.00019149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_261-484_0_4_line_122 |  | 122 | 123 | 0.021742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_261-484_0_4_line_123 |  | 123 | 124 | 0.010936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-484_0_4_trafo_74 | 0.63 MVA 20/0.4 kV | 125 | 68 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2681829.6208 | 1251615.808 | 2681829.6208 | 1251615.808 | 2681825.6029 | 1251619.244 | 2681821.3845 | 1251623.4023
1 | 2681834.1947 | 1251619.0137 | 2681829.6208 | 1251615.808
2 | 2681821.3845 | 1251623.4023 | 2681805.361 | 1251639.1979
3 | 2681841.3042 | 1251626.6979 | 2681835.8032 | 1251620.141 | 2681834.1947 | 1251619.0137
4 | 2681790.7592 | 1251653.592 | 2681805.361 | 1251639.1979
5 | 2681860.4274 | 1251649.4919 | 2681841.3042 | 1251626.6979
6 | 2681790.7592 | 1251653.592 | 2681781.9079 | 1251662.3174 | 2681777.1912 | 1251666.5165
7 | 2681860.4274 | 1251649.4919 | 2681865.2038 | 1251652.9713
8 | 2681860.4274 | 1251649.4919 | 2681851.469 | 1251657.0404
9 | 2681750.9881 | 1251689.8446 | 2681777.1912 | 1251666.5165
10 | 2681865.2038 | 1251652.9713 | 2681881.6258 | 1251664.9343
11 | 2681851.469 | 1251657.0404 | 2681851.469 | 1251657.0404 | 2681841.3766 | 1251671.8852
12 | 2681750.9881 | 1251689.8446 | 2681758.8675 | 1251698.2335
13 | 2681750.9881 | 1251689.8446 | 2681747.4641 | 1251686.3435
14 | 2681734.5123 | 1251673.4758 | 2681736.6758 | 1251675.6252
15 | 2681729.7073 | 1251668.702 | 2681734.5123 | 1251673.4758
16 | 2681736.6758 | 1251675.6252 | 2681747.4641 | 1251686.3435
17 | 2681729.7073 | 1251668.702 | 2681679.3217 | 1251701.975
18 | 2681581.1196 | 1251704.5148 | 2681588.4886 | 1251715.8691 | 2681603.5656 | 1251706.3029 | 2681618.2965 | 1251696.1093 | 2681636.9351 | 1251682.8005 | 2681680.8923 | 1251652.3724 | 2681692.664 | 1251644.4176 | 2681700.0719 | 1251640.906 | 2681714.2147 | 1251654.2109 | 2681729.7073 | 1251668.702
19 | 2681679.3217 | 1251701.975 | 2681676.301 | 1251703.9698 | 2681663.7595 | 1251712.6274
20 | 2681578.7247 | 1251700.8346 | 2681579.4935 | 1251702.0127 | 2681581.1196 | 1251704.5148
21 | 2681581.1196 | 1251704.5148 | 2681592.742 | 1251696.4885
22 | 2681658.1217 | 1251716.5192 | 2681663.7595 | 1251712.6274
23 | 2681578.7247 | 1251700.8346 | 2681572.853 | 1251704.9977
24 | 2681806.6424 | 1251497.347 | 2681812.7412 | 1251503.3801 | 2681816.5387 | 1251511.5275 | 2681820.2878 | 1251513.3362 | 2681824.4328 | 1251517.0962
25 | 2681824.4328 | 1251517.0962 | 2681830.7402 | 1251522.8187
26 | 2681806.6424 | 1251497.347 | 2681809.7767 | 1251495.033 | 2681812.8726 | 1251488.4041 | 2681816.8268 | 1251484.1111 | 2681817.9234 | 1251482.3193
27 | 2681830.7402 | 1251522.8187 | 2681838.87 | 1251530.1947
28 | 2681817.9234 | 1251482.3193 | 2681819.4109 | 1251479.8886
29 | 2681829.8705 | 1251462.7975 | 2681852.1416 | 1251461.4707 | 2681869.51 | 1251455.4951 | 2681872.0259 | 1251453.4255
30 | 2681829.8705 | 1251462.7975 | 2681819.4109 | 1251479.8886
31 | 2681890.6896 | 1251438.0726 | 2681872.0259 | 1251453.4255
32 | 2681759.8353 | 1251699.2639 | 2681758.8675 | 1251698.2335
33 | 2681658.1217 | 1251716.5192 | 2681644.0724 | 1251726.2177
34 | 2681855.6772 | 1251545.4434 | 2681838.87 | 1251530.1947
35 | 2681891.8854 | 1251437.0889 | 2681890.6896 | 1251438.0726
36 | 2681773.3992 | 1251712.7486 | 2681765.5904 | 1251705.391 | 2681759.8353 | 1251699.2639
37 | 2681638.5063 | 1251730.06 | 2681644.0724 | 1251726.2177
38 | 2681841.3766 | 1251671.8852 | 2681840.2201 | 1251673.5863 | 2681829.2589 | 1251687.8348
39 | 2681882.5267 | 1251665.5906 | 2681881.6258 | 1251664.9343
40 | 2681885.4697 | 1251667.7345 | 2681882.5267 | 1251665.5906
41 | 2681773.3992 | 1251712.7486 | 2681783.8121 | 1251713.7206
42 | 2681773.3992 | 1251712.7486 | 2681766.1216 | 1251714.1104
43 | 2681907.8198 | 1251693.3349 | 2681899.4019 | 1251709.9441
44 | 2681899.4657 | 1251677.9302 | 2681898.0481 | 1251680.0121 | 2681900.4453 | 1251682.4137 | 2681902.1867 | 1251685.3066 | 2681902.7575 | 1251687.1492 | 2681901.336 | 1251690.0539 | 2681904.9415 | 1251691.8718 | 2681907.8198 | 1251693.3349
45 | 2681917.2543 | 1251677.5535 | 2681907.8198 | 1251693.3349
46 | 2681896.2403 | 1251716.2607 | 2681896.4594 | 1251715.7501 | 2681899.4019 | 1251709.9441
47 | 2681899.4657 | 1251677.9302 | 2681885.4697 | 1251667.7345
48 | 2681917.2543 | 1251677.5535 | 2681920.4765 | 1251672.1607 | 2681923.3929 | 1251667.2797
49 | 2681917.2543 | 1251677.5535 | 2681930.3091 | 1251687.4244
50 | 2682059.8484 | 1251720.9697 | 2682076.2967 | 1251705.6416
51 | 2682014.291 | 1251720.2163 | 2682038.8179 | 1251741.2381 | 2682059.8484 | 1251720.9697
52 | 2682059.8484 | 1251720.9697 | 2682037.7011 | 1251696.8559
53 | 2682047.0532 | 1251672.0227 | 2682076.2967 | 1251705.6416
54 | 2682076.2967 | 1251705.6416 | 2682081.0989 | 1251701.1714
55 | 2682014.291 | 1251720.2163 | 2681990.7633 | 1251700.4143
56 | 2682014.7733 | 1251670.2069 | 2682021.1365 | 1251679.3917 | 2682027.442 | 1251685.7281 | 2682031.919 | 1251690.5604 | 2682037.7011 | 1251696.8559
57 | 2682001.2839 | 1251533.3637 | 2682003.2618 | 1251530.6224 | 2682004.6347 | 1251529.5962 | 2682006.1795 | 1251529.2395 | 2682007.9717 | 1251529.0086 | 2682009.4553 | 1251529.2515 | 2682011.5133 | 1251529.9916 | 2682013.667 | 1251531.4559 | 2682023.3151 | 1251541.1633 | 2682032.4678 | 1251549.626
58 | 2681994.5543 | 1251528.7561 | 2681997.7098 | 1251530.9124 | 2682001.2839 | 1251533.3637
59 | 2682001.2839 | 1251533.3637 | 2681995.3362 | 1251543.7809
60 | 2682053.2755 | 1251568.8653 | 2682032.4678 | 1251549.626
61 | 2681994.5543 | 1251528.7561 | 2681999.2117 | 1251520.6366
62 | 2681994.5543 | 1251528.7561 | 2681993.7413 | 1251530.182
63 | 2681912.3022 | 1251596.8249 | 2681938.2927 | 1251620.6909
64 | 2681938.2927 | 1251620.6909 | 2681936.9648 | 1251622.8297 | 2681937.4384 | 1251624.0593 | 2681937.4356 | 1251625.9051 | 2681937.2238 | 1251627.5701
65 | 2681938.2927 | 1251620.6909 | 2681940.9024 | 1251616.4683 | 2681942.4663 | 1251616.3676 | 2681943.7283 | 1251615.7179 | 2681945.176 | 1251613.1026 | 2681950.0909 | 1251603.7172
66 | 2681912.3022 | 1251596.8249 | 2681909.4607 | 1251594.2452
67 | 2681912.3022 | 1251596.8249 | 2681921.2284 | 1251583.064
68 | 2681937.2238 | 1251627.5701 | 2681936.8582 | 1251628.8994 | 2681933.9205 | 1251634.1271
69 | 2681937.2238 | 1251627.5701 | 2681940.5392 | 1251629.6286 | 2681944.1615 | 1251631.8692
70 | 2681950.0909 | 1251603.7172 | 2681952.8128 | 1251598.5196 | 2681960.6419 | 1251584.7731 | 2681962.2727 | 1251581.8452
71 | 2681944.1615 | 1251631.8692 | 2681939.8281 | 1251639.4472
72 | 2681944.1615 | 1251631.8692 | 2681944.28 | 1251631.6674
73 | 2681934.0126 | 1251653.445 | 2681935.9767 | 1251649.5137 | 2681935.5533 | 1251647.9288 | 2681936.0217 | 1251646.2563 | 2681936.9444 | 1251644.49 | 2681939.8281 | 1251639.4472
74 | 2681958.79 | 1251606.9543 | 2681944.28 | 1251631.6674
75 | 2682081.0989 | 1251701.1714 | 2682115.5865 | 1251669.0363
76 | 2682076.3571 | 1251621.7688 | 2682115.5865 | 1251669.0363
77 | 2682043.8369 | 1251653.0084 | 2682049.0498 | 1251658.6626 | 2682050.2014 | 1251662.1701 | 2682055.1312 | 1251667.0086 | 2682059.762 | 1251677.6362 | 2682081.0989 | 1251701.1714
78 | 2682030.4586 | 1251606.3552 | 2682020.0873 | 1251615.6259
79 | 2682030.4586 | 1251606.3552 | 2682032.5913 | 1251602.7931 | 2682056.6577 | 1251578.6305 | 2682059.3516 | 1251573.2416 | 2682055.2503 | 1251566.8912 | 2682053.2755 | 1251568.8653
80 | 2682030.4586 | 1251606.3552 | 2682039.6537 | 1251613.8881 | 2682044.8368 | 1251616.2505 | 2682045.4122 | 1251615.5674
81 | 2682020.0873 | 1251615.6259 | 2682019.9255 | 1251615.7705
82 | 2682053.2755 | 1251568.8653 | 2682054.6663 | 1251570.3635 | 2682055.5276 | 1251571.3984 | 2682055.9713 | 1251573.6951 | 2682055.7241 | 1251575.1928 | 2682054.3576 | 1251577.3866 | 2682050.1004 | 1251581.622
83 | 2682046.0033 | 1251614.8656 | 2682045.4122 | 1251615.5674
84 | 2681919.3737 | 1251659.4315 | 2681929.6844 | 1251641.6653 | 2681933.9205 | 1251634.1271
85 | 2681934.0126 | 1251653.445 | 2681932.5999 | 1251656.2609 | 2681931.1195 | 1251656.3294 | 2681929.2931 | 1251657.4049 | 2681923.3929 | 1251667.2797
86 | 2681930.3091 | 1251687.4244 | 2681934.8416 | 1251690.8516
87 | 2681990.7633 | 1251700.4143 | 2681972.4935 | 1251685.0376
88 | 2681945.8123 | 1251662.5816 | 2681936.4545 | 1251654.802 | 2681934.0126 | 1251653.445
89 | 2681945.8123 | 1251662.5816 | 2681953.6318 | 1251669.1629
90 | 2682034.1799 | 1251597.4608 | 2682050.1004 | 1251581.622
91 | 2681987.4081 | 1251541.2905 | 2681993.7413 | 1251530.182
92 | 2681738.1881 | 1251725.9902 | 2681748.6283 | 1251718.6224 | 2681760.8369 | 1251715.0993 | 2681766.1216 | 1251714.1104
93 | 2682014.7733 | 1251670.2069 | 2682002.7395 | 1251652.837
94 | 2681909.4607 | 1251594.2452 | 2681900.3002 | 1251585.9287 | 2681898.4153 | 1251584.2186
95 | 2681921.6244 | 1251558.3496 | 2681926.451 | 1251562.2058 | 2681927.0903 | 1251570.0094 | 2681924.5192 | 1251577.9909 | 2681921.2284 | 1251583.064
96 | 2681962.2727 | 1251581.8452 | 2681966.9969 | 1251573.3636 | 2681973.3263 | 1251565.9901 | 2681976.8648 | 1251559.7836
97 | 2681958.79 | 1251606.9543 | 2681963.5571 | 1251598.8351 | 2681966.7883 | 1251593.3691
98 | 2682009.2421 | 1251625.3201 | 2682019.9255 | 1251615.7705
99 | 2681935.3626 | 1251691.2455 | 2681934.8416 | 1251690.8516
100 | 2681972.4935 | 1251685.0376 | 2681953.6318 | 1251669.1629
101 | 2681962.6553 | 1251711.4398 | 2681954.3311 | 1251720.6204 | 2681953.4783 | 1251721.8601
102 | 2681962.6553 | 1251711.4398 | 2681965.2126 | 1251713.2802
103 | 2681962.6553 | 1251711.4398 | 2681960.5148 | 1251709.5755 | 2681948.0497 | 1251700.5605
104 | 2681976.8648 | 1251559.7836 | 2681987.4081 | 1251541.2905
105 | 2681729.8021 | 1251731.9083 | 2681738.1881 | 1251725.9902
106 | 2681729.8021 | 1251731.9083 | 2681721.7883 | 1251737.5638
107 | 2681709.7033 | 1251746.0924 | 2681721.7883 | 1251737.5638
108 | 2681687.0354 | 1251761.5268 | 2681691.8195 | 1251758.7133 | 2681692.3675 | 1251758.3266
109 | 2681708.4619 | 1251746.9685 | 2681692.3675 | 1251758.3266
110 | 2681709.7033 | 1251746.0924 | 2681708.4619 | 1251746.9685
111 | 2681939.6045 | 1251694.4529 | 2681948.0497 | 1251700.5605
112 | 2681939.6045 | 1251694.4529 | 2681935.3626 | 1251691.2455
113 | 2682002.7395 | 1251652.837 | 2681991.7353 | 1251636.9532 | 2681990.5961 | 1251633.6568
114 | 2681979.3063 | 1251571.8568 | 2681973.6824 | 1251581.7068 | 2681966.7883 | 1251593.3691
115 | 2682009.2421 | 1251625.3201 | 2682001.8473 | 1251616.8714
116 | 2682009.2421 | 1251625.3201 | 2682011.2746 | 1251627.6448
117 | 2682018.4039 | 1251635.7992 | 2682011.2746 | 1251627.6448
118 | 2681898.4153 | 1251584.2186 | 2681888.7522 | 1251575.4514
119 | 2681921.6244 | 1251558.3496 | 2681916.2904 | 1251554.0878
120 | 2681879.879 | 1251567.401 | 2681888.7522 | 1251575.4514
121 | 2681916.1408 | 1251553.9683 | 2681916.2904 | 1251554.0878
122 | 2681863.7764 | 1251552.7916 | 2681879.879 | 1251567.401
123 | 2681863.7764 | 1251552.7916 | 2681860.3129 | 1251549.6492 | 2681855.6772 | 1251545.4434

## bus_geodata
| x | y | coords
0 | 2681829.6208 | 1251615.808
1 | 2681821.3845 | 1251623.4023
2 | 2681834.1947 | 1251619.0137
3 | 2681805.361 | 1251639.1979
4 | 2681841.3042 | 1251626.6979
5 | 2681790.7592 | 1251653.592
6 | 2681860.4274 | 1251649.4919
7 | 2681777.1912 | 1251666.5165
8 | 2681865.2038 | 1251652.9713
9 | 2681851.469 | 1251657.0404
10 | 2681750.9881 | 1251689.8446
11 | 2681734.5123 | 1251673.4758
12 | 2681736.6758 | 1251675.6252
13 | 2681729.7073 | 1251668.702
14 | 2681747.4641 | 1251686.3435
15 | 2681679.3217 | 1251701.975
16 | 2681581.1196 | 1251704.5148
17 | 2681663.7595 | 1251712.6274
18 | 2681578.7247 | 1251700.8346
19 | 2681592.742 | 1251696.4885
20 | 2681824.4328 | 1251517.0962
21 | 2681806.6424 | 1251497.347
22 | 2681830.7402 | 1251522.8187
23 | 2681817.9234 | 1251482.3193
24 | 2681829.8705 | 1251462.7975
25 | 2681872.0259 | 1251453.4255
26 | 2681819.4109 | 1251479.8886
27 | 2681758.8675 | 1251698.2335
28 | 2681658.1217 | 1251716.5192
29 | 2681572.853 | 1251704.9977
30 | 2681838.87 | 1251530.1947
31 | 2681890.6896 | 1251438.0726
32 | 2681759.8353 | 1251699.2639
33 | 2681644.0724 | 1251726.2177
34 | 2681841.3766 | 1251671.8852
35 | 2681829.2589 | 1251687.8348
36 | 2681881.6258 | 1251664.9343
37 | 2681882.5267 | 1251665.5906
38 | 2681783.8121 | 1251713.7206
39 | 2681773.3992 | 1251712.7486
40 | 2681907.8198 | 1251693.3349
41 | 2681899.4019 | 1251709.9441
42 | 2681899.4657 | 1251677.9302
43 | 2681917.2543 | 1251677.5535
44 | 2682059.8484 | 1251720.9697
45 | 2682076.2967 | 1251705.6416
46 | 2682014.291 | 1251720.2163
47 | 2682037.7011 | 1251696.8559
48 | 2682001.2839 | 1251533.3637
49 | 2682032.4678 | 1251549.626
50 | 2681994.5543 | 1251528.7561
51 | 2681995.3362 | 1251543.7809
52 | 2681938.2927 | 1251620.6909
53 | 2681912.3022 | 1251596.8249
54 | 2681937.2238 | 1251627.5701
55 | 2681950.0909 | 1251603.7172
56 | 2681944.1615 | 1251631.8692
57 | 2681939.8281 | 1251639.4472
58 | 2681944.28 | 1251631.6674
59 | 2682115.5865 | 1251669.0363
60 | 2682081.0989 | 1251701.1714
61 | 2682076.3571 | 1251621.7688
62 | 2682047.0532 | 1251672.0227
63 | 2682043.8369 | 1251653.0084
64 | 2682030.4586 | 1251606.3552
65 | 2682020.0873 | 1251615.6259
66 | 2682053.2755 | 1251568.8653
67 | 2682045.4122 | 1251615.5674
68 | 2681933.9205 | 1251634.1271
69 | 2681923.3929 | 1251667.2797
70 | 2681930.3091 | 1251687.4244
71 | 2681990.7633 | 1251700.4143
72 | 2681934.0126 | 1251653.445
73 | 2681945.8123 | 1251662.5816
74 | 2681885.4697 | 1251667.7345
75 | 2682050.1005 | 1251581.622
76 | 2681999.2117 | 1251520.6366
77 | 2681993.7413 | 1251530.182
78 | 2681766.1216 | 1251714.1104
79 | 2681896.2403 | 1251716.2607
80 | 2682014.7733 | 1251670.2069
81 | 2681909.4607 | 1251594.2452
82 | 2681921.2284 | 1251583.064
83 | 2681962.2727 | 1251581.8452
84 | 2681958.79 | 1251606.9543
85 | 2682019.9255 | 1251615.7705
86 | 2682046.0033 | 1251614.8656
87 | 2681919.3737 | 1251659.4315
88 | 2681934.8416 | 1251690.8516
89 | 2681972.4935 | 1251685.0376
90 | 2681953.6318 | 1251669.1629
91 | 2681953.4783 | 1251721.8601
92 | 2681962.6553 | 1251711.4398
93 | 2682034.1799 | 1251597.4608
94 | 2681987.4081 | 1251541.2905
95 | 2681738.1881 | 1251725.9902
96 | 2681729.8021 | 1251731.9083
97 | 2681721.7883 | 1251737.5638
98 | 2681638.5063 | 1251730.06
99 | 2681687.0354 | 1251761.5268
100 | 2681692.3675 | 1251758.3266
101 | 2681708.4619 | 1251746.9685
102 | 2681709.7033 | 1251746.0924
103 | 2681965.2126 | 1251713.2802
104 | 2681948.0497 | 1251700.5605
105 | 2681939.6045 | 1251694.4529
106 | 2681935.3626 | 1251691.2455
107 | 2682002.7395 | 1251652.837
108 | 2681990.5961 | 1251633.6568
109 | 2681966.7883 | 1251593.3691
110 | 2681979.3063 | 1251571.8568
111 | 2682001.8473 | 1251616.8714
112 | 2682009.2421 | 1251625.3201
113 | 2682011.2746 | 1251627.6448
114 | 2682018.4039 | 1251635.7992
115 | 2681976.8648 | 1251559.7836
116 | 2681898.4153 | 1251584.2186
117 | 2681921.6244 | 1251558.3496
118 | 2681888.7522 | 1251575.4514
119 | 2681916.2904 | 1251554.0878
120 | 2681916.1408 | 1251553.9683
121 | 2681891.8854 | 1251437.0889
122 | 2681879.879 | 1251567.401
123 | 2681863.7764 | 1251552.7916
124 | 2681855.6772 | 1251545.4434
125 | 2681937.2238 | 1251627.5701

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98218 | -0.34145 | 0.010955 | 0.0027456
1 | 0.98144 | -0.35584 | 0.0013779 | 0.00034533
2 | 0.98261 | -0.33319 | 0.0025993 | 0.00065146
3 | 0.97999 | -0.3842 | 0.0018881 | 0.00047321
4 | 0.98343 | -0.31715 | 0.0026132 | 0.00065492
5 | 0.9787 | -0.40942 | 0.001688 | 0.00042305
6 | 0.98584 | -0.27055 | 0 | 0
7 | 0.97755 | -0.43196 | 0.0073764 | 0.0018487
8 | 0.98635 | -0.26069 | 0.0065474 | 0.0016409
9 | 0.98578 | -0.27181 | 0.001912 | 0.00047919
10 | 0.97564 | -0.46954 | 0 | 0
11 | 0.97496 | -0.48285 | 0.01786 | 0.0044763
12 | 0.97503 | -0.48152 | 0.006574 | 0.0016476
13 | 0.97492 | -0.48359 | 0 | 0
14 | 0.97546 | -0.47307 | 0.0084331 | 0.0021135
15 | 0.97467 | -0.48868 | 0.0014761 | 0.00036996
16 | 0.97469 | -0.48813 | 0 | 0
17 | 0.97461 | -0.48976 | 0.0005982 | 0.00014992
18 | 0.97469 | -0.48818 | 0 | 0
19 | 0.97469 | -0.48831 | 0.00070109 | 0.00017571
20 | 0.99334 | -0.12799 | 0 | 0
21 | 0.993 | -0.13464 | 0 | 0
22 | 0.99345 | -0.12593 | 0.003521 | 0.00088244
23 | 0.99276 | -0.13929 | 0.001792 | 0.00044912
24 | 0.99253 | -0.14367 | 0 | 0
25 | 0.9921 | -0.15194 | 0.0045153 | 0.0011316
26 | 0.99272 | -0.1399 | 0.0013213 | 0.00033115
27 | 0.97542 | -0.47372 | 0.0010693 | 0.00026799
28 | 0.9746 | -0.49008 | 0.0010801 | 0.0002707
29 | 0.97469 | -0.48826 | 0.00060713 | 0.00015216
30 | 0.99362 | -0.12258 | 0.0021014 | 0.00052665
31 | 0.99197 | -0.15456 | 0.0037631 | 0.00094312
32 | 0.9754 | -0.4742 | 0.0055519 | 0.0013914
33 | 0.97457 | -0.49053 | 0.00076118 | 0.00019077
34 | 0.98571 | -0.27313 | 0.0016964 | 0.00042515
35 | 0.98566 | -0.27399 | 0.0023878 | 0.00059843
36 | 0.98823 | -0.22448 | 0.0013656 | 0.00034225
37 | 0.98833 | -0.22247 | 0.0014754 | 0.00036977
38 | 0.97515 | -0.47911 | 0.0014032 | 0.00035168
39 | 0.97516 | -0.47884 | 0 | 0
40 | 0.99254 | -0.14192 | 0 | 0
41 | 0.99246 | -0.14349 | 0.0025482 | 0.00063864
42 | 0.99039 | -0.18296 | 0 | 0
43 | 0.99443 | -0.10579 | 0 | 0
44 | 0.99106 | -0.1715 | 0 | 0
45 | 0.99071 | -0.17842 | 0 | 0
46 | 0.99296 | -0.13475 | 0 | 0
47 | 0.99057 | -0.18101 | 0.0051834 | 0.0012991
48 | 0.99236 | -0.14653 | 0 | 0
49 | 0.99099 | -0.17304 | 0.0034781 | 0.00087168
50 | 0.99267 | -0.14052 | 0 | 0
51 | 0.99231 | -0.14761 | 0.005097 | 0.0012774
52 | 0.99834 | -0.031568 | 0 | 0
53 | 0.99628 | -0.071159 | 0 | 0
54 | 0.99921 | -0.014984 | 0 | 0
55 | 0.99707 | -0.056029 | 0.0042419 | 0.0010631
56 | 0.99866 | -0.025457 | 0 | 0
57 | 0.99812 | -0.035783 | 0.0041307 | 0.0010352
58 | 0.99866 | -0.025529 | 0.0036444 | 0.00091337
59 | 0.99051 | -0.18224 | 0 | 0
60 | 0.99065 | -0.17945 | 0 | 0
61 | 0.99032 | -0.18589 | 0.0033417 | 0.00083751
62 | 0.99036 | -0.18521 | 0.0085843 | 0.0021514
63 | 0.99035 | -0.1854 | 0.0054426 | 0.001364
64 | 0.98883 | -0.21491 | 0 | 0
65 | 0.98858 | -0.21972 | 0.0027456 | 0.0006881
66 | 0.99013 | -0.18969 | 0 | 0
67 | 0.98872 | -0.21706 | 0.0015286 | 0.00038309
68 | 1 | 0 | -0.36683 | -0.092906
69 | 0.99597 | -0.076652 | 0.0039475 | 0.00098933
70 | 0.99403 | -0.11358 | 0.0096437 | 0.0024169
71 | 0.99391 | -0.11643 | 0.0068847 | 0.0017255
72 | 0.99717 | -0.053857 | 0 | 0
73 | 0.99639 | -0.068663 | 0 | 0
74 | 0.98868 | -0.21582 | 0.0040763 | 0.0010216
75 | 0.99003 | -0.1917 | 0.0036016 | 0.00090263
76 | 0.99265 | -0.1409 | 0.0023417 | 0.0005869
77 | 0.99274 | -0.13924 | 0.0048066 | 0.0012046
78 | 0.97508 | -0.48044 | 0.0016062 | 0.00040255
79 | 0.99244 | -0.14377 | 0.0022166 | 0.00055553
80 | 0.99021 | -0.188 | 0.001591 | 0.00039873
81 | 0.99614 | -0.073948 | 0.002374 | 0.00059499
82 | 0.99594 | -0.077712 | 0.0038339 | 0.00096088
83 | 0.99568 | -0.08268 | 0.0039894 | 0.00099984
84 | 0.9983 | -0.032449 | 0.0058362 | 0.0014627
85 | 0.98858 | -0.21979 | 0.0033038 | 0.00082802
86 | 0.98872 | -0.21714 | 0.0049982 | 0.0012527
87 | 0.99968 | -0.0062212 | 0.012224 | 0.0030637
88 | 0.99394 | -0.11532 | 0.0021697 | 0.00054378
89 | 0.9948 | -0.09933 | 0.006696 | 0.0016782
90 | 0.99587 | -0.078808 | 0.0091932 | 0.002304
91 | 0.99353 | -0.12323 | 0.0065483 | 0.0016412
92 | 0.99362 | -0.12162 | 0 | 0
93 | 0.98996 | -0.19311 | 0.0035311 | 0.00088497
94 | 0.99331 | -0.12821 | 0.001879 | 0.00047091
95 | 0.97479 | -0.48621 | 0.0011634 | 0.00029158
96 | 0.9747 | -0.48791 | 0.0021591 | 0.00054111
97 | 0.97464 | -0.48915 | 0.0012436 | 0.00031168
98 | 0.97457 | -0.49061 | 0.00067994 | 0.00017041
99 | 0.97451 | -0.49173 | 0.0012068 | 0.00030246
100 | 0.97452 | -0.4916 | 0.0010615 | 0.00026605
101 | 0.97456 | -0.49077 | 0.0010845 | 0.0002718
102 | 0.97456 | -0.49068 | 0.0022799 | 0.0005714
103 | 0.99361 | -0.12174 | 0.0022123 | 0.00055445
104 | 0.99376 | -0.1188 | 0.0031265 | 0.00078356
105 | 0.99388 | -0.11661 | 0 | 0
106 | 0.99393 | -0.1155 | 0.0033001 | 0.00082709
107 | 0.99003 | -0.1916 | 0.0044823 | 0.0011234
108 | 0.98992 | -0.19367 | 0.005095 | 0.0012769
109 | 0.99818 | -0.034648 | 0.0036253 | 0.00090858
110 | 0.99808 | -0.036542 | 0.0043493 | 0.00109
111 | 0.98833 | -0.22461 | 0.0070465 | 0.001766
112 | 0.98841 | -0.2232 | 0 | 0
113 | 0.98839 | -0.22355 | 0.0017996 | 0.00045102
114 | 0.98834 | -0.22442 | 0.0045075 | 0.0011297
115 | 0.9943 | -0.10917 | 0.0059636 | 0.0014946
116 | 0.99561 | -0.084175 | 0.0033367 | 0.00083626
117 | 0.99545 | -0.087167 | 0.0033638 | 0.00084306
118 | 0.99518 | -0.092363 | 0.0042503 | 0.0010652
119 | 0.99536 | -0.089034 | 0.0046372 | 0.0011622
120 | 0.99536 | -0.089071 | 0.010909 | 0.002734
121 | 0.99196 | -0.15463 | 0.0023593 | 0.0005913
122 | 0.99484 | -0.098991 | 0.0016618 | 0.00041649
123 | 0.99425 | -0.11039 | 0.0068246 | 0.0017104
124 | 0.99402 | -0.11482 | 0.0035558 | 0.00089116
125 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.071369 | 0.018049 | -0.071319 | -0.018018 | 4.9199e-05 | 3.1346e-05 | 0.10818 | 0.10818 | 0.10818 | 0.98218 | -0.34145 | 0.98144 | -0.35584 | 29.7205
1 | -0.082324 | -0.020795 | 0.082356 | 0.020816 | 3.2612e-05 | 2.0801e-05 | 0.12478 | 0.12478 | 0.12478 | 0.98218 | -0.34145 | 0.98261 | -0.33319 | 34.2801
2 | 0.069942 | 0.017673 | -0.069847 | -0.017612 | 9.4971e-05 | 6.0498e-05 | 0.10609 | 0.10609 | 0.10609 | 0.98144 | -0.35584 | 0.97999 | -0.3842 | 29.1466
3 | -0.084956 | -0.021467 | 0.085021 | 0.021509 | 6.5379e-05 | 4.1709e-05 | 0.12872 | 0.12872 | 0.12872 | 0.98261 | -0.33319 | 0.98343 | -0.31715 | 35.3615
4 | 0.067958 | 0.017139 | -0.067877 | -0.017087 | 8.1931e-05 | 5.2178e-05 | 0.10323 | 0.10323 | 0.10323 | 0.97999 | -0.3842 | 0.9787 | -0.40942 | 28.359
5 | -0.087634 | -0.022164 | 0.087831 | 0.022289 | 0.00019639 | 0.00012531 | 0.13267 | 0.13267 | 0.13267 | 0.98343 | -0.31715 | 0.98584 | -0.27055 | 36.4478
6 | 0.066189 | 0.016664 | -0.066117 | -0.016618 | 7.1221e-05 | 4.5346e-05 | 0.10066 | 0.10066 | 0.10066 | 0.9787 | -0.40942 | 0.97755 | -0.43196 | 27.654
7 | -0.093828 | -0.023792 | 0.093872 | 0.02382 | 4.4509e-05 | 2.841e-05 | 0.14172 | 0.14172 | 0.14172 | 0.98584 | -0.27055 | 0.98635 | -0.26069 | 38.9344
8 | 0.0059968 | 0.0015026 | -0.0059965 | -0.0015025 | 3.5991e-07 | 8.0986e-08 | 0.0090514 | 0.0090514 | 0.0090514 | 0.98584 | -0.27055 | 0.98578 | -0.27181 | 2.4867
9 | 0.058741 | 0.01477 | -0.058636 | -0.014703 | 0.00010522 | 6.6904e-05 | 0.089432 | 0.089432 | 0.089432 | 0.97755 | -0.43196 | 0.97564 | -0.46954 | 24.5693
10 | -0.10042 | -0.025461 | 0.10059 | 0.025573 | 0.0001751 | 0.0001118 | 0.1516 | 0.1516 | 0.1516 | 0.98635 | -0.26069 | 0.98823 | -0.22448 | 41.6479
11 | 0.0040845 | 0.0010233 | -0.0040842 | -0.0010234 | 2.5588e-07 | -6.507e-08 | 0.0061653 | 0.0061654 | 0.0061654 | 0.98578 | -0.27181 | 0.98571 | -0.27313 | 1.6938
12 | 0.019842 | 0.0049761 | -0.019838 | -0.0049737 | 3.953e-06 | 2.3862e-06 | 0.030264 | 0.030264 | 0.030264 | 0.97564 | -0.46954 | 0.97542 | -0.47372 | 8.3143
13 | 0.038794 | 0.0097268 | -0.038787 | -0.0097227 | 6.5215e-06 | 4.1117e-06 | 0.059168 | 0.059168 | 0.059168 | 0.97564 | -0.46954 | 0.97546 | -0.47307 | 16.2551
14 | -0.023766 | -0.0059529 | 0.023768 | 0.0059539 | 1.5046e-06 | 9.2492e-07 | 0.036271 | 0.036271 | 0.036271 | 0.97496 | -0.48285 | 0.97503 | -0.48152 | 9.9647
15 | 0.0059056 | 0.0014767 | -0.0059054 | -0.0014766 | 2.0629e-07 | 4.7564e-08 | 0.0090121 | 0.0090122 | 0.0090122 | 0.97496 | -0.48285 | 0.97492 | -0.48359 | 2.4759
16 | -0.030342 | -0.0076015 | 0.030354 | 0.0076091 | 1.2227e-05 | 7.6357e-06 | 0.046304 | 0.046304 | 0.046304 | 0.97503 | -0.48152 | 0.97546 | -0.47307 | 12.7209
17 | 0.0045969 | 0.0011512 | -0.0045958 | -0.0011513 | 1.1146e-06 | -3.9386e-08 | 0.0070159 | 0.0070162 | 0.0070162 | 0.97492 | -0.48359 | 0.97467 | -0.48868 | 1.9275
18 | 0.0013085 | 0.00032538 | -0.0013082 | -0.00032755 | 2.8211e-07 | -2.172e-06 | 0.0019962 | 0.0019971 | 0.0019971 | 0.97492 | -0.48359 | 0.97469 | -0.48813 | 0.54865
19 | 0.0031197 | 0.00078133 | -0.0031195 | -0.00078146 | 1.6042e-07 | -1.3237e-07 | 0.0047626 | 0.0047626 | 0.0047626 | 0.97467 | -0.48868 | 0.97461 | -0.48976 | 1.3084
20 | 0.00060713 | 0.00015202 | -0.00060713 | -0.00015207 | 1.4144e-09 | -5.382e-08 | 0.00092682 | 0.00092684 | 0.00092684 | 0.97469 | -0.48813 | 0.97469 | -0.48818 | 0.25463
21 | 0.00070109 | 0.00017554 | -0.00070109 | -0.00017571 | 6.0675e-09 | -1.7216e-07 | 0.0010703 | 0.0010703 | 0.0010703 | 0.97469 | -0.48813 | 0.97469 | -0.48831 | 0.29405
22 | 0.0025213 | 0.00063154 | -0.0025213 | -0.0006316 | 3.8066e-08 | -6.1006e-08 | 0.0038493 | 0.0038494 | 0.0038494 | 0.97461 | -0.48976 | 0.9746 | -0.49008 | 1.0575
23 | 0.00060713 | 0.00015207 | -0.00060713 | -0.00015216 | 2.3188e-09 | -8.8227e-08 | 0.00092684 | 0.00092687 | 0.00092687 | 0.97469 | -0.48818 | 0.97469 | -0.48826 | 0.25464
24 | 0.013766 | 0.0034539 | -0.013761 | -0.0034515 | 4.358e-06 | 2.4355e-06 | 0.020622 | 0.020622 | 0.020622 | 0.99334 | -0.12799 | 0.993 | -0.13464 | 5.6655
25 | -0.013766 | -0.0034539 | 0.013767 | 0.0034547 | 1.3582e-06 | 7.5899e-07 | 0.020622 | 0.020622 | 0.020622 | 0.99334 | -0.12799 | 0.99345 | -0.12593 | 5.6655
26 | 0.013761 | 0.0034515 | -0.013758 | -0.0034498 | 3.054e-06 | 1.7069e-06 | 0.020622 | 0.020622 | 0.020622 | 0.993 | -0.13464 | 0.99276 | -0.13929 | 5.6655
27 | -0.017288 | -0.0043371 | 0.017291 | 0.0043387 | 2.7605e-06 | 1.6246e-06 | 0.025896 | 0.025896 | 0.025896 | 0.99345 | -0.12593 | 0.99362 | -0.12258 | 7.1143
28 | 0.011966 | 0.0030006 | -0.011966 | -0.0030004 | 3.438e-07 | 1.8319e-07 | 0.017936 | 0.017936 | 0.017936 | 0.99276 | -0.13929 | 0.99272 | -0.1399 | 4.9276
29 | 0.010643 | 0.0026683 | -0.010638 | -0.0026662 | 4.1947e-06 | 2.117e-06 | 0.015956 | 0.015956 | 0.015956 | 0.99253 | -0.14367 | 0.9921 | -0.15194 | 4.3836
30 | -0.010643 | -0.0026683 | 0.010645 | 0.0026693 | 1.913e-06 | 9.6533e-07 | 0.015956 | 0.015956 | 0.015956 | 0.99253 | -0.14367 | 0.99272 | -0.1399 | 4.3835
31 | 0.0061232 | 0.0015346 | -0.0061224 | -0.0015344 | 7.6439e-07 | 1.7718e-07 | 0.0091839 | 0.009184 | 0.009184 | 0.9921 | -0.15194 | 0.99197 | -0.15456 | 2.5231
32 | 0.018769 | 0.0047057 | -0.018768 | -0.0047054 | 4.346e-07 | 2.605e-07 | 0.028633 | 0.028633 | 0.028633 | 0.97542 | -0.47372 | 0.9754 | -0.4742 | 7.8661
33 | 0.0014412 | 0.0003609 | -0.0014411 | -0.0003611 | 3.0993e-08 | -1.9289e-07 | 0.0022003 | 0.0022003 | 0.0022003 | 0.9746 | -0.49008 | 0.97457 | -0.49053 | 0.60449
34 | -0.019392 | -0.0048654 | 0.019399 | 0.0048697 | 7.1782e-06 | 4.3e-06 | 0.029043 | 0.029043 | 0.029043 | 0.99362 | -0.12258 | 0.99402 | -0.11482 | 7.9788
35 | 0.0023593 | 0.00059128 | -0.0023593 | -0.0005913 | 7.2728e-09 | -1.5334e-08 | 0.0035391 | 0.0035391 | 0.0035391 | 0.99197 | -0.15456 | 0.99196 | -0.15463 | 0.97229
36 | 0.013217 | 0.003314 | -0.013214 | -0.0033124 | 2.9173e-06 | 1.6283e-06 | 0.020163 | 0.020163 | 0.020163 | 0.9754 | -0.4742 | 0.97516 | -0.47884 | 5.5393
37 | 0.00067994 | 0.00017033 | -0.00067994 | -0.00017041 | 2.7335e-09 | -8.2527e-08 | 0.0010381 | 0.0010382 | 0.0010382 | 0.97457 | -0.49053 | 0.97457 | -0.49061 | 0.28521
38 | 0.0023878 | 0.00059823 | -0.0023878 | -0.00059843 | 9.7616e-08 | -1.9289e-07 | 0.0036046 | 0.0036047 | 0.0036047 | 0.98571 | -0.27313 | 0.98566 | -0.27399 | 0.9903
39 | -0.10196 | -0.025915 | 0.10197 | 0.025922 | 9.868e-06 | 6.3012e-06 | 0.15365 | 0.15365 | 0.15365 | 0.98823 | -0.22448 | 0.98833 | -0.22247 | 42.2128
40 | -0.10345 | -0.026291 | 0.10348 | 0.026312 | 3.3176e-05 | 2.1186e-05 | 0.15588 | 0.15588 | 0.15588 | 0.98833 | -0.22247 | 0.98868 | -0.21582 | 42.823
41 | -0.0014032 | -0.00035168 | 0.0014032 | 0.00035156 | 1.798e-08 | -1.1897e-07 | 0.0021412 | 0.0021412 | 0.0021412 | 0.97515 | -0.47911 | 0.97516 | -0.47884 | 0.58825
42 | 0.01181 | 0.0029608 | -0.011809 | -0.0029603 | 9.0176e-07 | 4.8477e-07 | 0.018022 | 0.018022 | 0.018022 | 0.97516 | -0.47884 | 0.97508 | -0.48044 | 4.9511
43 | 0.0047652 | 0.0011941 | -0.0047648 | -0.0011941 | 3.5637e-07 | -1.2562e-08 | 0.0071439 | 0.007144 | 0.007144 | 0.99254 | -0.14192 | 0.99246 | -0.14349 | 1.9626
44 | 0.10794 | 0.027579 | -0.10773 | -0.027443 | 0.00021377 | 0.00013653 | 0.16201 | 0.16201 | 0.16201 | 0.99254 | -0.14192 | 0.99039 | -0.18296 | 44.5085
45 | -0.1127 | -0.028774 | 0.1129 | 0.028899 | 0.00019715 | 0.00012594 | 0.16915 | 0.16915 | 0.16915 | 0.99254 | -0.14192 | 0.99443 | -0.10579 | 46.471
46 | 0.0022166 | 0.00055545 | -0.0022166 | -0.00055553 | 2.9261e-08 | -7.2562e-08 | 0.0033234 | 0.0033234 | 0.0033234 | 0.99246 | -0.14349 | 0.99244 | -0.14377 | 0.91303
47 | 0.10773 | 0.027443 | -0.10755 | -0.027334 | 0.00017044 | 0.00010886 | 0.16201 | 0.16201 | 0.16201 | 0.99039 | -0.18296 | 0.98868 | -0.21582 | 44.5085
48 | -0.13992 | -0.035675 | 0.14011 | 0.035801 | 0.00019713 | 0.00012601 | 0.20958 | 0.20958 | 0.20958 | 0.99443 | -0.10579 | 0.99597 | -0.076652 | 57.5771
49 | 0.027016 | 0.0067757 | -0.027006 | -0.0067695 | 1.0031e-05 | 6.2073e-06 | 0.040427 | 0.040427 | 0.040427 | 0.99443 | -0.10579 | 0.99403 | -0.11358 | 11.1062
50 | 0.01738 | 0.0043572 | -0.017374 | -0.0043538 | 5.733e-06 | 3.3799e-06 | 0.026096 | 0.026096 | 0.026096 | 0.99106 | -0.1715 | 0.99071 | -0.17842 | 7.1691
51 | -0.033745 | -0.0084624 | 0.033804 | 0.0084995 | 5.9216e-05 | 3.7104e-05 | 0.050668 | 0.050667 | 0.050668 | 0.99106 | -0.1715 | 0.99296 | -0.13475 | 13.9197
52 | 0.016365 | 0.0041052 | -0.016358 | -0.0041008 | 7.4133e-06 | 4.3228e-06 | 0.024572 | 0.024572 | 0.024572 | 0.99106 | -0.1715 | 0.99057 | -0.18101 | 6.7506
53 | 0.0085871 | 0.0021526 | -0.0085843 | -0.0021514 | 2.7762e-06 | 1.2039e-06 | 0.012898 | 0.012898 | 0.012898 | 0.99071 | -0.17842 | 0.99036 | -0.18521 | 3.5434
54 | 0.0087872 | 0.0022012 | -0.0087868 | -0.002201 | 4.279e-07 | 1.8951e-07 | 0.013198 | 0.013198 | 0.013198 | 0.99071 | -0.17842 | 0.99065 | -0.17945 | 3.6258
55 | -0.033804 | -0.0084995 | 0.033834 | 0.008518 | 2.9604e-05 | 1.8549e-05 | 0.050667 | 0.050667 | 0.050667 | 0.99296 | -0.13475 | 0.99391 | -0.11643 | 13.9196
56 | 0.011174 | 0.0028018 | -0.01117 | -0.0027998 | 3.7245e-06 | 1.9301e-06 | 0.016786 | 0.016786 | 0.016786 | 0.99057 | -0.18101 | 0.99021 | -0.188 | 4.6116
57 | 0.036653 | 0.0092272 | -0.036607 | -0.009198 | 4.6392e-05 | 2.9163e-05 | 0.054975 | 0.054975 | 0.054975 | 0.99236 | -0.14653 | 0.99099 | -0.17304 | 15.1031
58 | -0.041751 | -0.010505 | 0.041763 | 0.010512 | 1.1992e-05 | 7.5697e-06 | 0.062618 | 0.062618 | 0.062618 | 0.99236 | -0.14653 | 0.99267 | -0.14052 | 17.2028
59 | 0.0050972 | 0.0012774 | -0.005097 | -0.0012774 | 2.6278e-07 | 1.321e-08 | 0.0076431 | 0.0076432 | 0.0076432 | 0.99236 | -0.14653 | 0.99231 | -0.14761 | 2.0998
60 | 0.033129 | 0.0083263 | -0.033103 | -0.0083098 | 2.6306e-05 | 1.6471e-05 | 0.049753 | 0.049753 | 0.049753 | 0.99099 | -0.17304 | 0.99013 | -0.18969 | 13.6684
61 | 0.0023418 | 0.0005868 | -0.0023417 | -0.0005869 | 4.3253e-08 | -9.3324e-08 | 0.0035103 | 0.0035103 | 0.0035103 | 0.99267 | -0.14052 | 0.99265 | -0.1409 | 0.96438
62 | -0.044104 | -0.011099 | 0.044107 | 0.011101 | 2.6917e-06 | 1.7015e-06 | 0.066128 | 0.066128 | 0.066128 | 0.99267 | -0.14052 | 0.99274 | -0.13924 | 18.1671
63 | 0.064355 | 0.016215 | -0.064233 | -0.016138 | 0.00012162 | 7.738e-05 | 0.09595 | 0.09595 | 0.09595 | 0.99834 | -0.031568 | 0.99628 | -0.071159 | 26.3599
64 | -0.12964 | -0.032739 | 0.12974 | 0.032805 | 0.00010311 | 6.5897e-05 | 0.19331 | 0.19331 | 0.19331 | 0.99834 | -0.031568 | 0.99921 | -0.014984 | 53.1084
65 | 0.065286 | 0.016523 | -0.065209 | -0.016475 | 7.6553e-05 | 4.8713e-05 | 0.097365 | 0.097365 | 0.097365 | 0.99834 | -0.031568 | 0.99707 | -0.056029 | 26.7486
66 | 0.041472 | 0.010428 | -0.041467 | -0.010424 | 5.5239e-06 | 3.4853e-06 | 0.061953 | 0.061953 | 0.061953 | 0.99628 | -0.071159 | 0.99614 | -0.073948 | 17.0201
67 | 0.022761 | 0.0057104 | -0.022754 | -0.005706 | 7.1092e-06 | 4.3363e-06 | 0.033997 | 0.033997 | 0.033997 | 0.99628 | -0.071159 | 0.99594 | -0.077712 | 9.3398
68 | -0.3527 | -0.089677 | 0.35296 | 0.08984 | 0.00025477 | 0.00016276 | 0.52569 | 0.52569 | 0.52569 | 0.99921 | -0.014984 | 1 | 0 | 48.1404
69 | 0.22296 | 0.056872 | -0.22285 | -0.056801 | 0.00011271 | 7.1814e-05 | 0.33238 | 0.33238 | 0.33238 | 0.99921 | -0.014984 | 0.99866 | -0.025457 | 30.4377
70 | 0.060968 | 0.015412 | -0.06089 | -0.015362 | 7.7812e-05 | 4.9473e-05 | 0.091034 | 0.091034 | 0.091034 | 0.99707 | -0.056029 | 0.99568 | -0.08268 | 25.0094
71 | 0.20538 | 0.052423 | -0.20528 | -0.052358 | 0.00010242 | 6.5204e-05 | 0.30636 | 0.30636 | 0.30636 | 0.99866 | -0.025457 | 0.99812 | -0.035783 | 28.0551
72 | 0.017461 | 0.0043775 | -0.017461 | -0.0043775 | 5.942e-08 | 3.4966e-08 | 0.026018 | 0.026018 | 0.026018 | 0.99866 | -0.025457 | 0.99866 | -0.025529 | 7.1477
73 | 0.20115 | 0.051323 | -0.20098 | -0.051211 | 0.00017544 | 0.00011167 | 0.3002 | 0.3002 | 0.3002 | 0.99812 | -0.035783 | 0.99717 | -0.053857 | 27.4912
74 | 0.013817 | 0.0034641 | -0.013812 | -0.0034616 | 4.555e-06 | 2.5404e-06 | 0.020588 | 0.020588 | 0.020588 | 0.99866 | -0.025529 | 0.9983 | -0.032449 | 5.656
75 | -0.0033423 | -0.00083709 | 0.0033427 | 0.00083677 | 4.4492e-07 | -3.2117e-07 | 0.0050208 | 0.0050206 | 0.0050208 | 0.99051 | -0.18224 | 0.99065 | -0.17945 | 1.3793
76 | 0.0033423 | 0.00083709 | -0.0033417 | -0.00083751 | 5.8001e-07 | -4.1834e-07 | 0.0050208 | 0.0050211 | 0.0050211 | 0.99051 | -0.18224 | 0.99032 | -0.18589 | 1.3794
77 | 0.0054441 | 0.0013642 | -0.0054426 | -0.001364 | 1.5442e-06 | 1.9568e-07 | 0.0081773 | 0.0081775 | 0.0081775 | 0.99065 | -0.17945 | 0.99035 | -0.1854 | 2.2466
78 | 0.01941 | 0.0048669 | -0.019406 | -0.0048642 | 4.4509e-06 | 2.6702e-06 | 0.02921 | 0.02921 | 0.02921 | 0.98883 | -0.21491 | 0.98858 | -0.21972 | 8.0247
79 | -0.025938 | -0.0065029 | 0.025969 | 0.0065221 | 3.1212e-05 | 1.9274e-05 | 0.039033 | 0.039032 | 0.039033 | 0.98883 | -0.21491 | 0.99013 | -0.18969 | 10.7232
80 | 0.0065275 | 0.001636 | -0.0065268 | -0.0016358 | 6.685e-07 | 1.9086e-07 | 0.0098227 | 0.0098227 | 0.0098227 | 0.98883 | -0.21491 | 0.98872 | -0.21706 | 2.6986
81 | 0.01666 | 0.0041761 | -0.01666 | -0.0041761 | 5.1183e-08 | 2.9975e-08 | 0.025077 | 0.025077 | 0.025077 | 0.98858 | -0.21972 | 0.98858 | -0.21979 | 6.8894
82 | 0.0071336 | 0.0017877 | -0.0071329 | -0.0017875 | 6.8259e-07 | 2.3318e-07 | 0.010721 | 0.010721 | 0.010721 | 0.99013 | -0.18969 | 0.99003 | -0.1917 | 2.9452
83 | 0.0049982 | 0.0012527 | -0.0049982 | -0.0012527 | 1.9471e-08 | 6.9317e-10 | 0.0075223 | 0.0075223 | 0.0075223 | 0.98872 | -0.21706 | 0.98872 | -0.21714 | 2.0666
84 | 0.012228 | 0.0030657 | -0.012224 | -0.0030637 | 3.624e-06 | 1.9366e-06 | 0.018196 | 0.018196 | 0.018196 | 1 | 0 | 0.99968 | -0.0062212 | 4.9989
85 | -0.14406 | -0.036791 | 0.14422 | 0.036892 | 0.00015893 | 0.00010124 | 0.21548 | 0.21548 | 0.21548 | 0.99597 | -0.076652 | 0.99717 | -0.053857 | 29.5987
86 | 0.017362 | 0.0043526 | -0.017361 | -0.0043517 | 1.4394e-06 | 8.4758e-07 | 0.025991 | 0.025991 | 0.025991 | 0.99403 | -0.11358 | 0.99394 | -0.11532 | 7.1403
87 | -0.040719 | -0.010243 | 0.040752 | 0.010264 | 3.3293e-05 | 2.0998e-05 | 0.060975 | 0.060974 | 0.060975 | 0.99391 | -0.11643 | 0.9948 | -0.09933 | 16.7512
88 | 0.056755 | 0.014319 | -0.056715 | -0.014294 | 4.0204e-05 | 2.5536e-05 | 0.084726 | 0.084726 | 0.084726 | 0.99717 | -0.053857 | 0.99639 | -0.068663 | 23.2765
89 | 0.056715 | 0.014294 | -0.056688 | -0.014276 | 2.7513e-05 | 1.7475e-05 | 0.084726 | 0.084727 | 0.084727 | 0.99639 | -0.068663 | 0.99587 | -0.078808 | 23.2765
90 | 0.0035313 | 0.00088484 | -0.0035311 | -0.00088497 | 2.3724e-07 | -1.3692e-07 | 0.0053075 | 0.0053076 | 0.0053076 | 0.99003 | -0.1917 | 0.98996 | -0.19311 | 1.4581
91 | -0.048914 | -0.012305 | 0.048939 | 0.012322 | 2.5787e-05 | 1.6338e-05 | 0.073333 | 0.073333 | 0.073333 | 0.99274 | -0.13924 | 0.99331 | -0.12821 | 20.1464
92 | 0.010203 | 0.0025578 | -0.0102 | -0.0025564 | 2.8059e-06 | 1.411e-06 | 0.015571 | 0.015571 | 0.015571 | 0.97508 | -0.48044 | 0.97479 | -0.48621 | 4.2777
93 | 0.0095794 | 0.0024011 | -0.0095778 | -0.0024003 | 1.6421e-06 | 7.7917e-07 | 0.014395 | 0.014395 | 0.014395 | 0.99021 | -0.188 | 0.99003 | -0.1916 | 3.9548
94 | 0.039093 | 0.0098293 | -0.039073 | -0.0098173 | 1.9084e-05 | 1.2019e-05 | 0.058407 | 0.058407 | 0.058407 | 0.99614 | -0.073948 | 0.99561 | -0.084175 | 16.0459
95 | 0.01892 | 0.0047451 | -0.018911 | -0.0047401 | 8.5227e-06 | 5.0846e-06 | 0.028269 | 0.028269 | 0.028269 | 0.99594 | -0.077712 | 0.99545 | -0.087167 | 7.7662
96 | 0.0569 | 0.014362 | -0.056828 | -0.014317 | 7.2112e-05 | 4.5806e-05 | 0.085072 | 0.085072 | 0.085072 | 0.99568 | -0.08268 | 0.9943 | -0.10917 | 23.3715
97 | 0.0079759 | 0.0019989 | -0.007975 | -0.0019986 | 8.3555e-07 | 3.2866e-07 | 0.011888 | 0.011889 | 0.011889 | 0.9983 | -0.032449 | 0.99818 | -0.034648 | 3.2661
98 | 0.013356 | 0.0033481 | -0.013354 | -0.0033469 | 2.1719e-06 | 1.2063e-06 | 0.020104 | 0.020104 | 0.020104 | 0.98858 | -0.21979 | 0.98841 | -0.2232 | 5.5232
99 | 0.015191 | 0.003808 | -0.015191 | -0.0038079 | 1.2668e-07 | 7.2608e-08 | 0.022742 | 0.022742 | 0.022742 | 0.99394 | -0.11532 | 0.99393 | -0.1155 | 6.2479
100 | -0.047448 | -0.011943 | 0.047494 | 0.011972 | 4.6591e-05 | 2.9498e-05 | 0.07099 | 0.07099 | 0.07099 | 0.9948 | -0.09933 | 0.99587 | -0.078808 | 19.5028
101 | -0.0065483 | -0.0016412 | 0.0065488 | 0.0016413 | 5.0127e-07 | 1.4082e-07 | 0.0098075 | 0.0098074 | 0.0098075 | 0.99353 | -0.12323 | 0.99362 | -0.12162 | 2.6944
102 | 0.0022123 | 0.00055442 | -0.0022123 | -0.00055445 | 1.2968e-08 | -3.2508e-08 | 0.0033131 | 0.0033131 | 0.0033131 | 0.99362 | -0.12162 | 0.99361 | -0.12174 | 0.91018
103 | -0.0087611 | -0.0021957 | 0.0087623 | 0.0021962 | 1.1763e-06 | 5.1678e-07 | 0.01312 | 0.01312 | 0.01312 | 0.99362 | -0.12162 | 0.99376 | -0.1188 | 3.6045
104 | -0.050818 | -0.012793 | 0.050865 | 0.012822 | 4.6288e-05 | 2.9348e-05 | 0.076148 | 0.076148 | 0.076148 | 0.99331 | -0.12821 | 0.9943 | -0.10917 | 20.9197
105 | 0.0090371 | 0.0022648 | -0.0090364 | -0.0022644 | 7.3248e-07 | 3.4084e-07 | 0.013795 | 0.013795 | 0.013795 | 0.97479 | -0.48621 | 0.9747 | -0.48791 | 3.7899
106 | 0.0068773 | 0.0017233 | -0.0068769 | -0.0017232 | 4.0544e-07 | 1.3724e-07 | 0.010499 | 0.010499 | 0.010499 | 0.9747 | -0.48791 | 0.97464 | -0.48915 | 2.8844
107 | 0.0056333 | 0.0014115 | -0.0056329 | -0.0014114 | 4.1028e-07 | 7.8259e-08 | 0.0086004 | 0.0086005 | 0.0086005 | 0.97464 | -0.48915 | 0.97456 | -0.49068 | 2.3628
108 | -0.0012068 | -0.00030246 | 0.0012068 | 0.00030239 | 7.9215e-09 | -7.2435e-08 | 0.0018428 | 0.0018427 | 0.0018428 | 0.97451 | -0.49173 | 0.97452 | -0.4916 | 0.50626
109 | -0.0022684 | -0.00056844 | 0.0022685 | 0.00056825 | 8.8618e-08 | -1.8872e-07 | 0.0034636 | 0.0034636 | 0.0034636 | 0.97452 | -0.4916 | 0.97456 | -0.49077 | 0.95155
110 | -0.003353 | -0.00084005 | 0.003353 | 0.00084004 | 1.4933e-08 | -9.375e-09 | 0.0051194 | 0.0051194 | 0.0051194 | 0.97456 | -0.49077 | 0.97456 | -0.49068 | 1.4064
111 | -0.011889 | -0.0029798 | 0.01189 | 0.0029805 | 1.2386e-06 | 6.5764e-07 | 0.017802 | 0.017802 | 0.017802 | 0.99376 | -0.1188 | 0.99388 | -0.11661 | 4.8906
112 | -0.01189 | -0.0029805 | 0.011891 | 0.0029808 | 6.3198e-07 | 3.3555e-07 | 0.017802 | 0.017802 | 0.017802 | 0.99388 | -0.11661 | 0.99393 | -0.1155 | 4.8906
113 | 0.0050955 | 0.0012769 | -0.005095 | -0.0012769 | 5.0172e-07 | 2.7809e-08 | 0.0076585 | 0.0076586 | 0.0076586 | 0.99003 | -0.1916 | 0.98992 | -0.19367 | 2.104
114 | 0.0043497 | 0.00109 | -0.0043493 | -0.00109 | 3.9244e-07 | -7.4157e-08 | 0.0064842 | 0.0064843 | 0.0064843 | 0.99818 | -0.034648 | 0.99808 | -0.036542 | 1.7814
115 | -0.0070465 | -0.001766 | 0.0070469 | 0.0017662 | 4.7389e-07 | 1.5939e-07 | 0.010609 | 0.010609 | 0.010609 | 0.98833 | -0.22461 | 0.98841 | -0.2232 | 2.9146
116 | 0.0063073 | 0.0015807 | -0.0063072 | -0.0015807 | 1.0441e-07 | 2.7244e-08 | 0.0094955 | 0.0094955 | 0.0094955 | 0.98841 | -0.2232 | 0.98839 | -0.22355 | 2.6087
117 | 0.0045077 | 0.0011297 | -0.0045075 | -0.0011297 | 1.8706e-07 | -1.9096e-08 | 0.0067862 | 0.0067863 | 0.0067863 | 0.98839 | -0.22355 | 0.98834 | -0.22442 | 1.8644
118 | 0.035737 | 0.008981 | -0.035723 | -0.0089722 | 1.3963e-05 | 8.7666e-06 | 0.05342 | 0.05342 | 0.05342 | 0.99561 | -0.084175 | 0.99518 | -0.092363 | 14.6759
119 | 0.015547 | 0.003897 | -0.015546 | -0.0038962 | 1.3829e-06 | 7.963e-07 | 0.023241 | 0.023241 | 0.023241 | 0.99545 | -0.087167 | 0.99536 | -0.089034 | 6.3848
120 | 0.031472 | 0.007907 | -0.031463 | -0.0079008 | 9.9522e-06 | 6.2138e-06 | 0.047065 | 0.047065 | 0.047065 | 0.99518 | -0.092363 | 0.99484 | -0.098991 | 12.93
121 | 0.010909 | 0.002734 | -0.010909 | -0.002734 | 1.9097e-08 | 9.7338e-09 | 0.016308 | 0.016308 | 0.016308 | 0.99536 | -0.089034 | 0.99536 | -0.089071 | 4.4803
122 | 0.029801 | 0.0074843 | -0.029785 | -0.0074742 | 1.6203e-05 | 1.0088e-05 | 0.044579 | 0.04458 | 0.04458 | 0.99484 | -0.098991 | 0.99425 | -0.11039 | 12.2471
123 | 0.02296 | 0.0057638 | -0.022955 | -0.0057608 | 4.8432e-06 | 2.9579e-06 | 0.034366 | 0.034366 | 0.034366 | 0.99425 | -0.11039 | 0.99402 | -0.11482 | 9.4411

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.37356 | 0.094592

## res_load
| p_mw | q_mvar
0 | 0.010955 | 0.0027456
1 | 0.0013779 | 0.00034533
2 | 0.0025993 | 0.00065146
3 | 0.0018881 | 0.00047321
4 | 0.0026132 | 0.00065492
5 | 0.001688 | 0.00042305
6 | 0.0073764 | 0.0018487
7 | 0.0065474 | 0.0016409
8 | 0.001912 | 0.00047919
9 | 0.01786 | 0.0044763
10 | 0.006574 | 0.0016476
11 | 0.0084331 | 0.0021135
12 | 0.0014761 | 0.00036996
13 | 0.0005982 | 0.00014992
14 | 0.00070109 | 0.00017571
15 | 0.003521 | 0.00088244
16 | 0.001792 | 0.00044912
17 | 0.0045153 | 0.0011316
18 | 0.0013213 | 0.00033115
19 | 0.0010693 | 0.00026799
20 | 0.0010801 | 0.0002707
21 | 0.00060713 | 0.00015216
22 | 0.0021014 | 0.00052665
23 | 0.0037631 | 0.00094312
24 | 0.0055519 | 0.0013914
25 | 0.00076118 | 0.00019077
26 | 0.0016964 | 0.00042515
27 | 0.0023878 | 0.00059843
28 | 0.0013656 | 0.00034225
29 | 0.0014754 | 0.00036977
30 | 0.0014032 | 0.00035168
31 | 0.0025482 | 0.00063864
32 | 0.0051834 | 0.0012991
33 | 0.0034781 | 0.00087168
34 | 0.005097 | 0.0012774
35 | 0.0042419 | 0.0010631
36 | 0.0041307 | 0.0010352
37 | 0.0036444 | 0.00091337
38 | 0.0033417 | 0.00083751
39 | 0.0085843 | 0.0021514
40 | 0.0054426 | 0.001364
41 | 0.0027456 | 0.0006881
42 | 0.0015286 | 0.00038309
43 | 0.0067288 | 0.0016864
44 | 0.0039475 | 0.00098933
45 | 0.0096437 | 0.0024169
46 | 0.0068847 | 0.0017255
47 | 0.0040763 | 0.0010216
48 | 0.0036016 | 0.00090263
49 | 0.0023417 | 0.0005869
50 | 0.0048066 | 0.0012046
51 | 0.0016062 | 0.00040255
52 | 0.0022166 | 0.00055553
53 | 0.001591 | 0.00039873
54 | 0.002374 | 0.00059499
55 | 0.0038339 | 0.00096088
56 | 0.0039894 | 0.00099984
57 | 0.0058362 | 0.0014627
58 | 0.0033038 | 0.00082802
59 | 0.0049982 | 0.0012527
60 | 0.012224 | 0.0030637
61 | 0.0021697 | 0.00054378
62 | 0.006696 | 0.0016782
63 | 0.0091932 | 0.002304
64 | 0.0065483 | 0.0016412
65 | 0.0035311 | 0.00088497
66 | 0.001879 | 0.00047091
67 | 0.0011634 | 0.00029158
68 | 0.0021591 | 0.00054111
69 | 0.0012436 | 0.00031168
70 | 0.00067994 | 0.00017041
71 | 0.0012068 | 0.00030246
72 | 0.0010615 | 0.00026605
73 | 0.0010845 | 0.0002718
74 | 0.0022799 | 0.0005714
75 | 0.0022123 | 0.00055445
76 | 0.0031265 | 0.00078356
77 | 0.0033001 | 0.00082709
78 | 0.0044823 | 0.0011234
79 | 0.005095 | 0.0012769
80 | 0.0036253 | 0.00090858
81 | 0.0043493 | 0.00109
82 | 0.0070465 | 0.001766
83 | 0.0017996 | 0.00045102
84 | 0.0045075 | 0.0011297
85 | 0.0059636 | 0.0014946
86 | 0.0033367 | 0.00083626
87 | 0.0033638 | 0.00084306
88 | 0.0042503 | 0.0010652
89 | 0.0046372 | 0.0011622
90 | 0.010909 | 0.002734
91 | 0.0023593 | 0.0005913
92 | 0.0016618 | 0.00041649
93 | 0.0068246 | 0.0017104
94 | 0.0035558 | 0.00089116

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1