## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-489_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-489_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_261-489_0_4_node_34 | 0.4 | n |  | TRUE
3 | bus_LV_261-489_0_4_node_35 | 0.4 | n |  | TRUE
4 | bus_LV_261-489_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-489_0_4_node_138 | 0.4 | n |  | TRUE
6 | bus_LV_261-489_0_4_node_101 | 0.4 | n |  | TRUE
7 | bus_LV_261-489_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_261-489_0_4_node_126 | 0.4 | n |  | TRUE
9 | bus_LV_261-489_0_4_node_122 | 0.4 | n |  | TRUE
10 | bus_LV_261-489_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_261-489_0_4_node_159 | 0.4 | n |  | TRUE
12 | bus_LV_261-489_0_4_node_160 | 0.4 | n |  | TRUE
13 | bus_LV_261-489_0_4_node_147 | 0.4 | n |  | TRUE
14 | bus_LV_261-489_0_4_node_23 | 0.4 | n |  | TRUE
15 | bus_LV_261-489_0_4_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_261-489_0_4_node_29 | 0.4 | n |  | TRUE
17 | bus_LV_261-489_0_4_node_30 | 0.4 | n |  | TRUE
18 | bus_LV_261-489_0_4_node_113 | 0.4 | n |  | TRUE
19 | bus_LV_261-489_0_4_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_261-489_0_4_node_40 | 0.4 | n |  | TRUE
21 | bus_LV_261-489_0_4_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_261-489_0_4_node_37 | 0.4 | n |  | TRUE
23 | bus_LV_261-489_0_4_node_149 | 0.4 | n |  | TRUE
24 | bus_LV_261-489_0_4_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_261-489_0_4_node_133 | 0.4 | n |  | TRUE
26 | bus_LV_261-489_0_4_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_261-489_0_4_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_261-489_0_4_node_155 | 0.4 | n |  | TRUE
29 | bus_LV_261-489_0_4_node_156 | 0.4 | n |  | TRUE
30 | bus_LV_261-489_0_4_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_261-489_0_4_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_261-489_0_4_node_157 | 0.4 | n |  | TRUE
33 | bus_LV_261-489_0_4_node_158 | 0.4 | n |  | TRUE
34 | bus_LV_261-489_0_4_node_154 | 0.4 | n |  | TRUE
35 | bus_LV_261-489_0_4_node_152 | 0.4 | n |  | TRUE
36 | bus_LV_261-489_0_4_node_18 | 0.4 | n |  | TRUE
37 | bus_LV_261-489_0_4_node_20 | 0.4 | n |  | TRUE
38 | bus_LV_261-489_0_4_node_21 | 0.4 | n |  | TRUE
39 | bus_LV_261-489_0_4_node_62 | 0.4 | n |  | TRUE
40 | bus_LV_261-489_0_4_node_66 | 0.4 | n |  | TRUE
41 | bus_LV_261-489_0_4_node_53 | 0.4 | n |  | TRUE
42 | bus_LV_261-489_0_4_node_125 | 0.4 | n |  | TRUE
43 | bus_LV_261-489_0_4_node_121 | 0.4 | n |  | TRUE
44 | bus_LV_261-489_0_4_node_130 | 0.4 | n |  | TRUE
45 | bus_LV_261-489_0_4_node_25 | 0.4 | n |  | TRUE
46 | bus_LV_261-489_0_4_node_52 | 0.4 | n |  | TRUE
47 | bus_LV_261-489_0_4_node_48 | 0.4 | n |  | TRUE
48 | bus_LV_261-489_0_4_node_51 | 0.4 | n |  | TRUE
49 | bus_LV_261-489_0_4_node_26 | 0.4 | n |  | TRUE
50 | bus_LV_261-489_0_4_node_145 | 0.4 | n |  | TRUE
51 | bus_LV_261-489_0_4_node_31 | 0.4 | n |  | TRUE
52 | bus_LV_261-489_0_4_node_116 | 0.4 | n |  | TRUE
53 | bus_LV_261-489_0_4_node_27 | 0.4 | n |  | TRUE
54 | bus_LV_261-489_0_4_node_32 | 0.4 | n |  | TRUE
55 | bus_LV_261-489_0_4_node_55 | 0.4 | n |  | TRUE
56 | bus_LV_261-489_0_4_node_58 | 0.4 | n |  | TRUE
57 | bus_LV_261-489_0_4_node_28 | 0.4 | n |  | TRUE
58 | bus_LV_261-489_0_4_node_61 | 0.4 | n |  | TRUE
59 | bus_LV_261-489_0_4_node_57 | 0.4 | n |  | TRUE
60 | bus_LV_261-489_0_4_node_150 | 0.4 | n |  | TRUE
61 | bus_LV_261-489_0_4_node_151 | 0.4 | n |  | TRUE
62 | bus_LV_261-489_0_4_node_143 | 0.4 | n |  | TRUE
63 | bus_LV_261-489_0_4_node_148 | 0.4 | n |  | TRUE
64 | bus_LV_261-489_0_4_node_33 | 0.4 | n |  | TRUE
65 | bus_LV_261-489_0_4_node_137 | 0.4 | n |  | TRUE
66 | bus_LV_261-489_0_4_node_39 | 0.4 | n |  | TRUE
67 | bus_LV_261-489_0_4_node_36 | 0.4 | n |  | TRUE
68 | bus_LV_261-489_0_4_node_99 | 0.4 | n |  | TRUE
69 | bus_LV_261-489_0_4_node_100 | 0.4 | n |  | TRUE
70 | bus_LV_261-489_0_4_node_98 | 0.4 | n |  | TRUE
71 | bus_LV_261-489_0_4_node_136 | 0.4 | n |  | TRUE
72 | bus_LV_261-489_0_4_node_120 | 0.4 | n |  | TRUE
73 | bus_LV_261-489_0_4_node_162 | 0.4 | n |  | TRUE
74 | bus_LV_261-489_0_4_node_117 | 0.4 | n |  | TRUE
75 | bus_LV_261-489_0_4_node_163 | 0.4 | n |  | TRUE
76 | bus_LV_261-489_0_4_node_110 | 0.4 | n |  | TRUE
77 | bus_LV_261-489_0_4_node_112 | 0.4 | n |  | TRUE
78 | bus_LV_261-489_0_4_node_38 | 0.4 | n |  | TRUE
79 | bus_LV_261-489_0_4_node_41 | 0.4 | n |  | TRUE
80 | bus_LV_261-489_0_4_node_134 | 0.4 | n |  | TRUE
81 | bus_LV_261-489_0_4_node_127 | 0.4 | n |  | TRUE
82 | bus_LV_261-489_0_4_node_128 | 0.4 | n |  | TRUE
83 | bus_LV_261-489_0_4_node_153 | 0.4 | n |  | TRUE
84 | bus_LV_261-489_0_4_node_50 | 0.4 | n |  | TRUE
85 | bus_LV_261-489_0_4_node_68 | 0.4 | n |  | TRUE
86 | bus_LV_261-489_0_4_node_54 | 0.4 | n |  | TRUE
87 | bus_LV_261-489_0_4_node_84 | 0.4 | n |  | TRUE
88 | bus_LV_261-489_0_4_node_83 | 0.4 | n |  | TRUE
89 | bus_LV_261-489_0_4_node_123 | 0.4 | n |  | TRUE
90 | bus_LV_261-489_0_4_node_119 | 0.4 | n |  | TRUE
91 | bus_LV_261-489_0_4_node_46 | 0.4 | n |  | TRUE
92 | bus_LV_261-489_0_4_node_115 | 0.4 | n |  | TRUE
93 | bus_LV_261-489_0_4_node_56 | 0.4 | n |  | TRUE
94 | bus_LV_261-489_0_4_node_139 | 0.4 | n |  | TRUE
95 | bus_LV_261-489_0_4_node_60 | 0.4 | n |  | TRUE
96 | bus_LV_261-489_0_4_node_144 | 0.4 | n |  | TRUE
97 | bus_LV_261-489_0_4_node_111 | 0.4 | n |  | TRUE
98 | bus_LV_261-489_0_4_node_106 | 0.4 | n |  | TRUE
99 | bus_LV_261-489_0_4_node_105 | 0.4 | n |  | TRUE
100 | bus_LV_261-489_0_4_node_107 | 0.4 | n |  | TRUE
101 | bus_LV_261-489_0_4_node_104 | 0.4 | n |  | TRUE
102 | bus_LV_261-489_0_4_node_108 | 0.4 | n |  | TRUE
103 | bus_LV_261-489_0_4_node_42 | 0.4 | n |  | TRUE
104 | bus_LV_261-489_0_4_node_43 | 0.4 | n |  | TRUE
105 | bus_LV_261-489_0_4_node_44 | 0.4 | n |  | TRUE
106 | bus_LV_261-489_0_4_node_45 | 0.4 | n |  | TRUE
107 | bus_LV_261-489_0_4_node_47 | 0.4 | n |  | TRUE
108 | bus_LV_261-489_0_4_node_49 | 0.4 | n |  | TRUE
109 | bus_LV_261-489_0_4_node_103 | 0.4 | n |  | TRUE
110 | bus_LV_261-489_0_4_node_59 | 0.4 | n |  | TRUE
111 | bus_LV_261-489_0_4_node_65 | 0.4 | n |  | TRUE
112 | bus_LV_261-489_0_4_node_70 | 0.4 | n |  | TRUE
113 | bus_LV_261-489_0_4_node_72 | 0.4 | n |  | TRUE
114 | bus_LV_261-489_0_4_node_141 | 0.4 | n |  | TRUE
115 | bus_LV_261-489_0_4_node_64 | 0.4 | n |  | TRUE
116 | bus_LV_261-489_0_4_node_69 | 0.4 | n |  | TRUE
117 | bus_LV_261-489_0_4_node_78 | 0.4 | n |  | TRUE
118 | bus_LV_261-489_0_4_node_71 | 0.4 | n |  | TRUE
119 | bus_LV_261-489_0_4_node_142 | 0.4 | n |  | TRUE
120 | bus_LV_261-489_0_4_node_140 | 0.4 | n |  | TRUE
121 | bus_LV_261-489_0_4_node_63 | 0.4 | n |  | TRUE
122 | bus_LV_261-489_0_4_node_67 | 0.4 | n |  | TRUE
123 | bus_LV_261-489_0_4_node_73 | 0.4 | n |  | TRUE
124 | bus_LV_261-489_0_4_node_76 | 0.4 | n |  | TRUE
125 | bus_LV_261-489_0_4_node_79 | 0.4 | n |  | TRUE
126 | bus_LV_261-489_0_4_node_74 | 0.4 | n |  | TRUE
127 | bus_LV_261-489_0_4_node_75 | 0.4 | n |  | TRUE
128 | bus_LV_261-489_0_4_node_77 | 0.4 | n |  | TRUE
129 | bus_LV_261-489_0_4_node_81 | 0.4 | n |  | TRUE
130 | bus_LV_261-489_0_4_node_85 | 0.4 | n |  | TRUE
131 | bus_LV_261-489_0_4_node_80 | 0.4 | n |  | TRUE
132 | bus_LV_261-489_0_4_node_86 | 0.4 | n |  | TRUE
133 | bus_LV_261-489_0_4_node_82 | 0.4 | n |  | TRUE
134 | bus_LV_261-489_0_4_node_87 | 0.4 | n |  | TRUE
135 | bus_LV_261-489_0_4_node_88 | 0.4 | n |  | TRUE
136 | bus_LV_261-489_0_4_node_97 | 0.4 | n |  | TRUE
137 | bus_LV_261-489_0_4_node_90 | 0.4 | n |  | TRUE
138 | bus_LV_261-489_0_4_node_92 | 0.4 | n |  | TRUE
139 | bus_LV_261-489_0_4_node_93 | 0.4 | n |  | TRUE
140 | bus_LV_261-489_0_4_node_94 | 0.4 | n |  | TRUE
141 | bus_LV_261-489_0_4_node_95 | 0.4 | n |  | TRUE
142 | bus_LV_261-489_0_4_node_96 | 0.4 | n |  | TRUE
143 | bus_LV_261-489_0_4_node_89 | 0.4 | n |  | TRUE
144 | bus_LV_261-489_0_4_node_91 | 0.4 | n |  | TRUE
145 | bus_LV_261-489_0_4_node_146 | 0.4 | n |  | TRUE
146 | bus_LV_261-489_0_4_node_118 | 0.4 | n |  | TRUE
147 | bus_LV_261-489_0_4_node_109 | 0.4 | n |  | TRUE
148 | bus_LV_261-489_0_4_node_161 | 0.4 | n |  | TRUE
149 | bus_LV_261-489_0_4_node_114 | 0.4 | n |  | TRUE
150 | bus_LV_261-489_0_4_node_124 | 0.4 | n |  | TRUE
151 | bus_LV_261-489_0_4_node_132 | 0.4 | n |  | TRUE
152 | bus_LV_261-489_0_4_node_135 | 0.4 | n |  | TRUE
153 | bus_LV_261-489_0_4_node_131 | 0.4 | n |  | TRUE
154 | bus_MV_528_0_node_26 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-489_0_4_load_0 | 0 | 0.0029463 | 0.00073842 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-489_0_4_load_34 | 2 | 0.0060856 | 0.0015252 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-489_0_4_load_35 | 3 | 0.0069207 | 0.0017345 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-489_0_4_load_138 | 5 | 0.0017517 | 0.00043903 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-489_0_4_load_126 | 8 | 0.0020497 | 0.00051369 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-489_0_4_load_122 | 9 | 0.00153 | 0.00038346 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-489_0_4_load_159 | 11 | 0.012991 | 0.0032558 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-489_0_4_load_113 | 18 | 0.0057352 | 0.0014374 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-489_0_4_load_40 | 20 | 0.001031 | 0.00025839 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-489_0_4_load_37 | 22 | 0.0034674 | 0.00086901 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-489_0_4_load_149 | 23 | 0.0014536 | 0.00036431 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-489_0_4_load_133 | 25 | 0.0017831 | 0.00044688 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-489_0_4_load_155 | 28 | 0.0052338 | 0.0013117 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-489_0_4_load_156 | 29 | 0.010465 | 0.0026227 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-489_0_4_load_157 | 32 | 0.0054429 | 0.0013641 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-489_0_4_load_158 | 33 | 0.017373 | 0.0043541 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-489_0_4_load_154 | 34 | 0.0072779 | 0.001824 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-489_0_4_load_62 | 39 | 0.0021702 | 0.0005439 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-489_0_4_load_66 | 40 | 0.0024097 | 0.00060392 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-489_0_4_load_53 | 41 | 0.0039136 | 0.00098083 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-489_0_4_load_125 | 42 | 0.007675 | 0.0019235 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-489_0_4_load_130 | 44 | 0.0014408 | 0.00036109 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-489_0_4_load_52 | 46 | 0.0066295 | 0.0016615 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-489_0_4_load_48 | 47 | 0.0012582 | 0.00031534 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-489_0_4_load_51 | 48 | 0.0015013 | 0.00037626 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-489_0_4_load_145 | 50 | 0.012218 | 0.0030621 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-489_0_4_load_55 | 55 | 0.003806 | 0.00095387 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-489_0_4_load_57 | 59 | 0.0055216 | 0.0013838 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-489_0_4_load_150 | 60 | 0.005515 | 0.0013822 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-489_0_4_load_151 | 61 | 0.0069191 | 0.0017341 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-489_0_4_load_143 | 62 | 0.0061005 | 0.0015289 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-489_0_4_load_148 | 63 | 0.012498 | 0.0031322 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-489_0_4_load_137 | 65 | 0.010001 | 0.0025065 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-489_0_4_load_99 | 68 | 0.0017497 | 0.00043852 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-489_0_4_load_100 | 69 | 0.0017583 | 0.00044068 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-489_0_4_load_98 | 70 | 0.0016348 | 0.00040972 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-489_0_4_load_136 | 71 | 0.0015673 | 0.00039281 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-489_0_4_load_120 | 72 | 0.0029399 | 0.00073681 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-489_0_4_load_162 | 73 | 0.010431 | 0.0026142 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-489_0_4_load_163 | 75 | 0.010899 | 0.0027316 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-489_0_4_load_112 | 77 | 0.0074342 | 0.0018632 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-489_0_4_load_38 | 78 | 0.0050037 | 0.0012541 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-489_0_4_load_134 | 80 | 0.0014491 | 0.00036319 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-489_0_4_load_127 | 81 | 0.00088403 | 0.00022156 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-489_0_4_load_153 | 83 | 0.0071546 | 0.0017931 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-489_0_4_load_50 | 84 | 0.0032534 | 0.00081539 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-489_0_4_load_68 | 85 | 0.0028712 | 0.00071958 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-489_0_4_load_54 | 86 | 0.0034289 | 0.00085936 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-489_0_4_load_84 | 87 | 0.00098578 | 0.00024706 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-489_0_4_load_83 | 88 | 0.0019 | 0.00047619 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-489_0_4_load_123 | 89 | 0.0047616 | 0.0011934 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-489_0_4_load_119 | 90 | 0.0015189 | 0.00038067 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-489_0_4_load_115 | 92 | 0.0095188 | 0.0023856 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-489_0_4_load_56 | 93 | 0.0054109 | 0.0013561 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-489_0_4_load_139 | 94 | 0.005496 | 0.0013774 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-489_0_4_load_144 | 96 | 0.0057259 | 0.001435 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-489_0_4_load_106 | 98 | 0.0049878 | 0.0012501 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-489_0_4_load_105 | 99 | 0.0049657 | 0.0012445 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-489_0_4_load_107 | 100 | 0.0017484 | 0.0004382 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-489_0_4_load_104 | 101 | 0.0050089 | 0.0012553 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-489_0_4_load_108 | 102 | 0.0016513 | 0.00041386 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-489_0_4_load_42 | 103 | 0.0017585 | 0.00044073 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-489_0_4_load_43 | 104 | 0.0011718 | 0.00029368 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-489_0_4_load_44 | 105 | 0.0013472 | 0.00033764 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-489_0_4_load_45 | 106 | 0.0014465 | 0.00036253 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-489_0_4_load_47 | 107 | 0.0016109 | 0.00040373 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-489_0_4_load_49 | 108 | 0.0010485 | 0.00026279 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-489_0_4_load_103 | 109 | 0.0011341 | 0.00028422 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-489_0_4_load_65 | 111 | 0.001882 | 0.00047166 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-489_0_4_load_141 | 114 | 0.0055801 | 0.0013985 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-489_0_4_load_64 | 115 | 0.0013297 | 0.00033324 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-489_0_4_load_69 | 116 | 0.0023901 | 0.00059902 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-489_0_4_load_78 | 117 | 0.0019374 | 0.00048556 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-489_0_4_load_142 | 119 | 0.0053675 | 0.0013452 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-489_0_4_load_140 | 120 | 0.0053509 | 0.0013411 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-489_0_4_load_63 | 121 | 0.0058748 | 0.0014724 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-489_0_4_load_67 | 122 | 0.0023791 | 0.00059627 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-489_0_4_load_73 | 123 | 0.0030579 | 0.00076638 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-489_0_4_load_79 | 125 | 0.0022992 | 0.00057624 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-489_0_4_load_74 | 126 | 0.0032526 | 0.00081518 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-489_0_4_load_75 | 127 | 0.002004 | 0.00050224 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-489_0_4_load_77 | 128 | 0.0015059 | 0.00037741 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_261-489_0_4_load_81 | 129 | 0.00097165 | 0.00024352 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_261-489_0_4_load_85 | 130 | 0.0019076 | 0.00047809 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_261-489_0_4_load_80 | 131 | 0.0020812 | 0.0005216 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_261-489_0_4_load_86 | 132 | 0.00091418 | 0.00022912 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_261-489_0_4_load_82 | 133 | 0.00098113 | 0.00024589 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_261-489_0_4_load_87 | 134 | 0.0036772 | 0.00092159 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_261-489_0_4_load_88 | 135 | 0.002346 | 0.00058797 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_261-489_0_4_load_97 | 136 | 0.0055182 | 0.001383 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_261-489_0_4_load_90 | 137 | 0.0010577 | 0.00026509 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_261-489_0_4_load_92 | 138 | 0.00093054 | 0.00023321 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_261-489_0_4_load_93 | 139 | 0.0008343 | 0.0002091 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_261-489_0_4_load_94 | 140 | 0.00070101 | 0.00017569 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_261-489_0_4_load_95 | 141 | 0.0011727 | 0.0002939 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_261-489_0_4_load_96 | 142 | 0.0029992 | 0.00075166 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_261-489_0_4_load_89 | 143 | 0.0022521 | 0.00056442 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_261-489_0_4_load_91 | 144 | 0.0024047 | 0.00060268 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_261-489_0_4_load_146 | 145 | 0.012709 | 0.0031852 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_261-489_0_4_load_109 | 147 | 0.0017153 | 0.00042988 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_261-489_0_4_load_161 | 148 | 0.010227 | 0.0025631 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_261-489_0_4_load_124 | 150 | 0.0052259 | 0.0013097 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_261-489_0_4_load_132 | 151 | 0.004224 | 0.0010586 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_261-489_0_4_load_135 | 152 | 0.00088315 | 0.00022134 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_261-489_0_4_load_131 | 153 | 0.001901 | 0.00047644 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 18 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-489_0_4_line_0 |  | 0 | 1 | 0.014065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-489_0_4_line_1 |  | 1 | 2 | 0.011048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-489_0_4_line_2 |  | 1 | 3 | 0.018171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-489_0_4_line_3 |  | 3 | 67 | 0.024871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-489_0_4_line_4 |  | 4 | 5 | 0.019257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-489_0_4_line_5 |  | 4 | 6 | 0.004176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-489_0_4_line_6 |  | 6 | 67 | 0.013175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-489_0_4_line_7 |  | 6 | 68 | 0.018934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-489_0_4_line_8 |  | 7 | 8 | 0.025227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-489_0_4_line_9 |  | 7 | 9 | 0.01916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-489_0_4_line_10 |  | 8 | 71 | 0.015884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-489_0_4_line_11 |  | 9 | 72 | 0.016761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-489_0_4_line_12 |  | 10 | 11 | 0.007269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-489_0_4_line_13 |  | 10 | 12 | 0.042219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-489_0_4_line_14 |  | 10 | 13 | 0.08052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-489_0_4_line_15 |  | 10 | 14 | 0.059689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-489_0_4_line_16 |  | 12 | 73 | 0.001953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-489_0_4_line_17 |  | 12 | 74 | 0.025468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-489_0_4_line_18 |  | 13 | 75 | 0.007732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-489_0_4_line_19 |  | 13 | 76 | 0.027475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-489_0_4_line_20 |  | 14 | 42 | 0.017413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-489_0_4_line_21 |  | 14 | 43 | 0.031921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-489_0_4_line_22 |  | 15 | 16 | 0.098007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-489_0_4_line_23 |  | 15 | 17 | 0.04682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_261-489_0_4_line_24 |  | 15 | 18 | 0.038941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_261-489_0_4_line_25 |  | 16 | 60 | 0.018913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-489_0_4_line_26 |  | 16 | 61 | 0.011993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-489_0_4_line_27 |  | 16 | 35 | 0.025735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-489_0_4_line_28 |  | 17 | 62 | 0.020454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-489_0_4_line_29 |  | 17 | 57 | 0.053375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_261-489_0_4_line_30 |  | 18 | 77 | 0.018849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_261-489_0_4_line_31 |  | 19 | 20 | 0.024267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-489_0_4_line_32 |  | 19 | 21 | 0.028585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-489_0_4_line_33 |  | 19 | 22 | 0.025543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-489_0_4_line_34 |  | 21 | 23 | 0.025611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-489_0_4_line_35 |  | 22 | 78 | 0.016093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-489_0_4_line_36 |  | 24 | 25 | 0.025418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-489_0_4_line_37 |  | 24 | 26 | 0.006534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-489_0_4_line_38 |  | 25 | 80 | 0.017892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-489_0_4_line_39 |  | 26 | 44 | 0.011288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-489_0_4_line_40 |  | 27 | 28 | 0.007843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-489_0_4_line_41 |  | 27 | 29 | 0.009382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-489_0_4_line_42 |  | 27 | 30 | 0.088168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-489_0_4_line_43 |  | 27 | 31 | 0.030256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-489_0_4_line_44 |  | 30 | 32 | 0.013411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-489_0_4_line_45 |  | 30 | 33 | 0.01383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-489_0_4_line_46 |  | 31 | 34 | 0.026242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-489_0_4_line_47 |  | 31 | 35 | 0.036314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-489_0_4_line_48 |  | 35 | 83 | 0.025825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-489_0_4_line_49 |  | 36 | 37 | 0.004859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-489_0_4_line_50 |  | 36 | 38 | 0.05244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-489_0_4_line_51 |  | 36 | 39 | 0.014257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-489_0_4_line_52 |  | 37 | 40 | 0.02161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-489_0_4_line_53 |  | 38 | 41 | 0.030159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-489_0_4_line_54 |  | 40 | 85 | 0.0072216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-489_0_4_line_55 |  | 41 | 86 | 0.016316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-489_0_4_line_56 |  | 43 | 89 | 0.017263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-489_0_4_line_57 |  | 43 | 90 | 0.041994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-489_0_4_line_58 |  | 44 | 82 | 0.016029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-489_0_4_line_59 |  | 45 | 46 | 0.022896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-489_0_4_line_60 |  | 45 | 47 | 0.011187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-489_0_4_line_61 |  | 45 | 48 | 0.015891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-489_0_4_line_62 |  | 46 | 54 | 0.018499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-489_0_4_line_63 |  | 47 | 91 | 0.023513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-489_0_4_line_64 |  | 48 | 84 | 0.023678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-489_0_4_line_65 |  | 49 | 50 | 0.008274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-489_0_4_line_66 |  | 49 | 51 | 0.03334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
67 | LV_261-489_0_4_line_67 |  | 49 | 52 | 0.007782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
68 | LV_261-489_0_4_line_68 |  | 51 | 63 | 0.001402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-489_0_4_line_69 |  | 51 | 64 | 0.008553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
70 | LV_261-489_0_4_line_70 |  | 52 | 92 | 0.005471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
71 | LV_261-489_0_4_line_71 |  | 53 | 54 | 0.031198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-489_0_4_line_72 |  | 53 | 55 | 0.029328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
73 | LV_261-489_0_4_line_73 |  | 53 | 56 | 0.020841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_261-489_0_4_line_74 |  | 55 | 86 | 0.016193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-489_0_4_line_75 |  | 56 | 93 | 0.014373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
76 | LV_261-489_0_4_line_76 |  | 57 | 58 | 0.011333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-489_0_4_line_77 |  | 57 | 59 | 0.00085811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
78 | LV_261-489_0_4_line_78 |  | 58 | 94 | 0.016644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-489_0_4_line_79 |  | 58 | 95 | 0.035409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-489_0_4_line_80 |  | 59 | 93 | 0.021635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
81 | LV_261-489_0_4_line_81 |  | 62 | 96 | 0.020241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-489_0_4_line_82 |  | 64 | 65 | 0.036568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
83 | LV_261-489_0_4_line_83 |  | 64 | 66 | 0.032698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_261-489_0_4_line_84 |  | 65 | 97 | 0.013818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_261-489_0_4_line_85 |  | 66 | 79 | 0.018813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_261-489_0_4_line_86 |  | 66 | 78 | 0.018702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_261-489_0_4_line_87 |  | 67 | 98 | 0.014937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_261-489_0_4_line_88 |  | 68 | 70 | 0.018428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_261-489_0_4_line_89 |  | 69 | 70 | 0.0065107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_261-489_0_4_line_90 |  | 71 | 152 | 0.013345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_261-489_0_4_line_91 |  | 72 | 90 | 0.010065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_261-489_0_4_line_92 |  | 74 | 148 | 0.002432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_261-489_0_4_line_93 |  | 76 | 145 | 0.014631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_261-489_0_4_line_94 |  | 77 | 149 | 0.01691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
95 | LV_261-489_0_4_line_95 |  | 79 | 100 | 0.025284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_261-489_0_4_line_96 |  | 79 | 101 | 0.010114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_261-489_0_4_line_97 |  | 80 | 152 | 0.003228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_261-489_0_4_line_98 |  | 81 | 82 | 0.014822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_261-489_0_4_line_99 |  | 82 | 153 | 0.002714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_261-489_0_4_line_100 |  | 85 | 122 | 0.014579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_261-489_0_4_line_101 |  | 87 | 88 | 0.0074081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_261-489_0_4_line_102 |  | 88 | 133 | 0.00010627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_261-489_0_4_line_103 |  | 89 | 150 | 0.02178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_261-489_0_4_line_104 |  | 91 | 107 | 0.018537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_261-489_0_4_line_105 |  | 91 | 106 | 0.0049255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_261-489_0_4_line_106 |  | 92 | 149 | 0.0025211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
107 | LV_261-489_0_4_line_107 |  | 94 | 120 | 0.020867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_261-489_0_4_line_108 |  | 95 | 114 | 0.0091172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_261-489_0_4_line_109 |  | 97 | 146 | 0.031528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-489_0_4_line_110 |  | 98 | 99 | 0.016019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_261-489_0_4_line_111 |  | 99 | 101 | 0.01599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_261-489_0_4_line_112 |  | 100 | 102 | 0.0065036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_261-489_0_4_line_113 |  | 102 | 147 | 0.00644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_261-489_0_4_line_114 |  | 103 | 104 | 0.0091572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_261-489_0_4_line_115 |  | 103 | 105 | 0.012982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_261-489_0_4_line_116 |  | 105 | 106 | 0.0026918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_261-489_0_4_line_117 |  | 107 | 108 | 0.015045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_261-489_0_4_line_118 |  | 108 | 109 | 0.0057835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_261-489_0_4_line_119 |  | 110 | 111 | 0.01074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_261-489_0_4_line_120 |  | 110 | 112 | 0.004493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_261-489_0_4_line_121 |  | 110 | 113 | 0.00436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_261-489_0_4_line_122 |  | 111 | 115 | 0.0086814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_261-489_0_4_line_123 |  | 112 | 116 | 0.022368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_261-489_0_4_line_124 |  | 113 | 117 | 0.013811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_261-489_0_4_line_125 |  | 113 | 118 | 0.0084962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_261-489_0_4_line_126 |  | 114 | 119 | 0.023612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_261-489_0_4_line_127 |  | 115 | 121 | 0.014181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_261-489_0_4_line_128 |  | 116 | 122 | 0.0074067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_261-489_0_4_line_129 |  | 117 | 124 | 0.012648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_261-489_0_4_line_130 |  | 118 | 123 | 0.024417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_261-489_0_4_line_131 |  | 123 | 126 | 0.00064784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_261-489_0_4_line_132 |  | 124 | 125 | 0.01341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_261-489_0_4_line_133 |  | 125 | 130 | 0.0043816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_261-489_0_4_line_134 |  | 126 | 127 | 0.016849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_261-489_0_4_line_135 |  | 127 | 128 | 0.00057096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_261-489_0_4_line_136 |  | 128 | 129 | 0.0070499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_261-489_0_4_line_137 |  | 129 | 131 | 0.00020989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_261-489_0_4_line_138 |  | 130 | 132 | 0.0051284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_261-489_0_4_line_139 |  | 131 | 133 | 0.014312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_261-489_0_4_line_140 |  | 132 | 134 | 0.040258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_261-489_0_4_line_141 |  | 134 | 135 | 0.015655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_261-489_0_4_line_142 |  | 134 | 136 | 0.045846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_261-489_0_4_line_143 |  | 135 | 137 | 0.0099077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_261-489_0_4_line_144 |  | 136 | 142 | 0.013923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_261-489_0_4_line_145 |  | 137 | 143 | 0.0073642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_261-489_0_4_line_146 |  | 138 | 139 | 0.0030465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_261-489_0_4_line_147 |  | 138 | 140 | 0.0035357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_261-489_0_4_line_148 |  | 139 | 141 | 0.012306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_261-489_0_4_line_149 |  | 141 | 142 | 0.0072263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_261-489_0_4_line_150 |  | 143 | 144 | 0.017603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_261-489_0_4_line_151 |  | 145 | 146 | 0.019761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_261-489_0_4_line_152 |  | 150 | 151 | 0.010632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-489_0_4_trafo_113 | 0.63 MVA 20/0.4 kV | 154 | 18 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2682299.1491 | 1252032.4427 | 2682298.434 | 1252028.5076 | 2682298.1844 | 1252018.4451
1 | 2682299.1491 | 1252032.4427 | 2682300.8188 | 1252041.5616 | 2682301.4898 | 1252043.2071
2 | 2682299.1491 | 1252032.4427 | 2682317.2348 | 1252030.6844
3 | 2682341.1415 | 1252033.2044 | 2682332.5702 | 1252029.1934 | 2682317.2348 | 1252030.6844
4 | 2682358.3067 | 1252032.5313 | 2682357.4558 | 1252031.3075 | 2682357.3807 | 1252015.5391 | 2682356.8265 | 1252013.6196
5 | 2682358.3067 | 1252032.5313 | 2682354.1183 | 1252032.4953
6 | 2682341.1415 | 1252033.2044 | 2682342.4359 | 1252032.3884 | 2682354.1183 | 1252032.4953
7 | 2682354.1183 | 1252032.4953 | 2682358.0012 | 1252051.0265
8 | 2682418.0177 | 1252110.542 | 2682442.7678 | 1252105.6595
9 | 2682418.0177 | 1252110.542 | 2682421.3305 | 1252129.4133
10 | 2682458.3519 | 1252102.5852 | 2682442.7678 | 1252105.6595
11 | 2682425.7716 | 1252145.0645 | 2682425.7716 | 1252145.0645 | 2682425.2557 | 1252141.4546 | 2682424.7188 | 1252137.7333 | 2682423.6127 | 1252136.9506 | 2682422.5029 | 1252135.3451 | 2682421.9058 | 1252132.6904 | 2682421.3305 | 1252129.4133
12 | 2682430.7231 | 1252225.2823 | 2682423.5782 | 1252226.7284
13 | 2682430.7231 | 1252225.2823 | 2682427.9401 | 1252209.9543 | 2682420.5457 | 1252211.4303 | 2682414.2679 | 1252211.3096 | 2682408.1892 | 1252208.8121 | 2682401.95 | 1252209.17
14 | 2682416.3459 | 1252146.0564 | 2682418.9467 | 1252160.381 | 2682427.9401 | 1252209.9543 | 2682430.7231 | 1252225.2823
15 | 2682430.7231 | 1252225.2823 | 2682435.5038 | 1252251.624 | 2682439.0234 | 1252251.4395 | 2682443.8196 | 1252251.1838 | 2682439.1896 | 1252227.0347
16 | 2682401.6372 | 1252207.242 | 2682401.95 | 1252209.17
17 | 2682401.95 | 1252209.17 | 2682398.2132 | 1252214.6555 | 2682393.9118 | 1252217.3199 | 2682389.2329 | 1252215.6536 | 2682384.8718 | 1252207.965
18 | 2682408.7326 | 1252147.5294 | 2682416.3459 | 1252146.0564
19 | 2682416.3459 | 1252146.0564 | 2682413.7381 | 1252131.6983 | 2682411.4389 | 1252119.0235
20 | 2682439.1896 | 1252227.0347 | 2682456.3539 | 1252224.1052
21 | 2682439.1896 | 1252227.0347 | 2682433.574 | 1252195.6108
22 | 2682362.9006 | 1252285.5954 | 2682395.3186 | 1252266.4651 | 2682401.6931 | 1252260.1713 | 2682397.3614 | 1252259.0547 | 2682380.9486 | 1252254.512 | 2682361.6767 | 1252247.6945 | 2682358.3526 | 1252246.3028 | 2682359.444 | 1252240.547
23 | 2682323.6244 | 1252236.7131 | 2682343.8835 | 1252248.5257 | 2682348.0006 | 1252241.1996 | 2682350.5777 | 1252236.6098 | 2682359.444 | 1252240.547
24 | 2682359.444 | 1252240.547 | 2682360.8534 | 1252233.0944 | 2682355.61 | 1252202.1798
25 | 2682362.9006 | 1252285.5954 | 2682343.9358 | 1252286.01
26 | 2682354.5651 | 1252277.1399 | 2682357.4799 | 1252281.3725 | 2682362.9006 | 1252285.5954
27 | 2682352.6133 | 1252308.9477 | 2682353.8884 | 1252302.4606 | 2682356.7123 | 1252296.9513 | 2682362.9006 | 1252285.5954
28 | 2682323.6244 | 1252236.7131 | 2682319.6809 | 1252256.7834
29 | 2682283.5522 | 1252235.8337 | 2682294.8291 | 1252242.2729 | 2682298.2511 | 1252236.6273 | 2682303.4344 | 1252236.7549 | 2682308.5176 | 1252227.2518 | 2682323.6244 | 1252236.7131
30 | 2682352.4579 | 1252183.5958 | 2682355.61 | 1252202.1798
31 | 2682276.0752 | 1252077.5783 | 2682276.281 | 1252101.8445
32 | 2682250.5051 | 1252078.5685 | 2682261.9307 | 1252076.5033 | 2682275.7023 | 1252074.5375 | 2682276.0752 | 1252077.5783
33 | 2682276.0752 | 1252077.5783 | 2682284.8725 | 1252094.1017 | 2682291.6949 | 1252094.2082
34 | 2682249.7647 | 1252104.1662 | 2682250.5051 | 1252078.5685
35 | 2682291.6949 | 1252094.2082 | 2682307.7856 | 1252094.4594
36 | 2682517.1032 | 1252090.9951 | 2682492.1656 | 1252095.9146
37 | 2682518.2514 | 1252097.427 | 2682517.1032 | 1252090.9951
38 | 2682492.1656 | 1252095.9146 | 2682474.6118 | 1252099.3775
39 | 2682518.2514 | 1252097.427 | 2682520.2454 | 1252108.5373
40 | 2682395.3632 | 1252294.1754 | 2682387.722 | 1252296.0372
41 | 2682395.3632 | 1252294.1754 | 2682400.6592 | 1252292.1697 | 2682403.5303 | 1252289.7745
42 | 2682411.3082 | 1252335.5725 | 2682419.2831 | 1252333.593 | 2682424.1907 | 1252330.7481 | 2682426.8906 | 1252327.6389 | 2682429.8966 | 1252322.6102 | 2682430.5468 | 1252316.5592 | 2682429.2866 | 1252300.2851 | 2682426.8445 | 1252293.546 | 2682423.3913 | 1252296.5447 | 2682419.0556 | 1252297.8854 | 2682414.4201 | 1252297.9877 | 2682407.4349 | 1252296.634 | 2682397.889 | 1252297.6131 | 2682395.3632 | 1252294.1754
43 | 2682383.3496 | 1252318.4598 | 2682386.5639 | 1252310.9211 | 2682391.1352 | 1252302.9565 | 2682397.889 | 1252297.6131 | 2682395.3632 | 1252294.1754
44 | 2682411.3082 | 1252335.5725 | 2682404.9612 | 1252335.5509 | 2682398.3167 | 1252333.0455
45 | 2682411.3082 | 1252335.5725 | 2682410.0884 | 1252332.6534 | 2682409.7983 | 1252328.0125 | 2682411.0952 | 1252322.1373
46 | 2682383.3496 | 1252318.4598 | 2682381.1145 | 1252325.0448 | 2682378.3658 | 1252330.0325 | 2682374.2988 | 1252333.7566 | 2682368.9782 | 1252333.7382 | 2682366.5444 | 1252332.37
47 | 2682383.3496 | 1252318.4598 | 2682379.7771 | 1252317.0202 | 2682374.2457 | 1252312.6178 | 2682370.3522 | 1252307.1262 | 2682362.9353 | 1252305.344 | 2682359.0248 | 1252305.9568 | 2682352.6133 | 1252308.9477
48 | 2682338.673 | 1252327.4234 | 2682343.834 | 1252326.4388 | 2682349.1622 | 1252322.1096 | 2682351.0808 | 1252318.2 | 2682352.6133 | 1252308.9477
49 | 2682189.9769 | 1252201.7318 | 2682185.2152 | 1252202.7666
50 | 2682183.5654 | 1252151.4276 | 2682182.1512 | 1252152.1752 | 2682181.0394 | 1252153.4274 | 2682180.9597 | 1252154.8162 | 2682185.7535 | 1252179.7568 | 2682189.9769 | 1252201.7318
51 | 2682189.9769 | 1252201.7318 | 2682192.6684 | 1252215.7321
52 | 2682185.2152 | 1252202.7666 | 2682189.4228 | 1252223.9631
53 | 2682183.5654 | 1252151.4276 | 2682185.9529 | 1252151.2494 | 2682188.7067 | 1252151.8659 | 2682202.5484 | 1252158.4294 | 2682205.5923 | 1252164.7875 | 2682207.789 | 1252166.1312
54 | 2682190.8289 | 1252231.0465 | 2682189.4228 | 1252223.9631
55 | 2682207.789 | 1252166.1312 | 2682221.7073 | 1252174.6446
56 | 2682433.574 | 1252195.6108 | 2682450.5994 | 1252192.7585
57 | 2682433.574 | 1252195.6108 | 2682429.0218 | 1252173.4532 | 2682427.7319 | 1252171.2336 | 2682424.8407 | 1252154.678
58 | 2682523.077 | 1252124.3143 | 2682520.2454 | 1252108.5373
59 | 2682246.7441 | 1252173.8319 | 2682256.518 | 1252179.8165 | 2682266.2491 | 1252185.8221
60 | 2682246.7441 | 1252173.8319 | 2682252.5321 | 1252164.2583
61 | 2682246.7441 | 1252173.8319 | 2682233.1895 | 1252165.5377
62 | 2682281.9913 | 1252195.5375 | 2682266.2491 | 1252185.8221
63 | 2682264.6971 | 1252144.1367 | 2682252.5321 | 1252164.2583
64 | 2682212.6104 | 1252153.8723 | 2682220.4156 | 1252157.7212 | 2682233.1895 | 1252165.5377
65 | 2682347.6662 | 1252151.2722 | 2682355.8165 | 1252149.7176
66 | 2682330.8608 | 1252130.9679 | 2682333.2133 | 1252140.9081 | 2682345.8997 | 1252140.9844 | 2682347.6662 | 1252151.2722
67 | 2682347.6662 | 1252151.2722 | 2682348.865 | 1252158.9613
68 | 2682330.8608 | 1252130.9679 | 2682329.6402 | 1252130.2727
69 | 2682330.8608 | 1252130.9679 | 2682332.6753 | 1252122.6091
70 | 2682348.865 | 1252158.9613 | 2682349.2461 | 1252161.4017 | 2682349.7629 | 1252164.3578
71 | 2682260.5393 | 1252198.3973 | 2682264.3217 | 1252190.7108 | 2682279.1761 | 1252199.8794 | 2682281.9913 | 1252195.5375
72 | 2682260.5393 | 1252198.3973 | 2682235.5209 | 1252183.0941
73 | 2682251.7033 | 1252217.2666 | 2682253.5886 | 1252212.4892 | 2682260.5393 | 1252198.3973
74 | 2682235.5209 | 1252183.0941 | 2682221.7073 | 1252174.6446
75 | 2682251.7033 | 1252217.2666 | 2682264.1201 | 1252224.5053
76 | 2682283.5522 | 1252235.8337 | 2682283.6287 | 1252247.1654
77 | 2682282.8108 | 1252235.4015 | 2682283.5522 | 1252235.8337
78 | 2682283.6287 | 1252247.1654 | 2682283.7423 | 1252263.8088
79 | 2682283.6287 | 1252247.1654 | 2682272.0418 | 1252246.7376 | 2682259.5025 | 1252248.5871 | 2682248.8921 | 1252252.2982
80 | 2682282.8108 | 1252235.4015 | 2682264.1201 | 1252224.5053
81 | 2682315.7784 | 1252276.6451 | 2682319.6809 | 1252256.7834
82 | 2682332.6753 | 1252122.6091 | 2682336.628 | 1252116.793 | 2682337.7018 | 1252111.7597 | 2682340.7506 | 1252106.9096 | 2682347.358 | 1252102.8762 | 2682354.6937 | 1252099.1197 | 2682357.3581 | 1252098.858
83 | 2682332.6753 | 1252122.6091 | 2682328.6445 | 1252107.4307 | 2682327.3114 | 1252100.7182 | 2682326.7157 | 1252097.4186 | 2682325.6164 | 1252090.7094
84 | 2682371.0208 | 1252099.547 | 2682363.9144 | 1252098.2139 | 2682357.3581 | 1252098.858
85 | 2682325.6164 | 1252090.7094 | 2682342.0297 | 1252090.3706 | 2682344.4434 | 1252089.9371
86 | 2682325.6164 | 1252090.7094 | 2682317.3202 | 1252094.6082 | 2682307.7856 | 1252094.4594
87 | 2682341.1415 | 1252033.2044 | 2682343.1794 | 1252039.7154 | 2682343.3835 | 1252047.8274
88 | 2682370.523 | 1252056.4078 | 2682359.4904 | 1252058.1336 | 2682358.0012 | 1252051.0265
89 | 2682370.523 | 1252056.4078 | 2682376.9555 | 1252055.4016
90 | 2682458.3519 | 1252102.5852 | 2682471.4449 | 1252100.0023
91 | 2682424.8407 | 1252154.678 | 2682423.9711 | 1252149.6985 | 2682424.5237 | 1252147.4156 | 2682425.7716 | 1252145.0645
92 | 2682382.4801 | 1252208.4432 | 2682384.8718 | 1252207.965
93 | 2682411.4389 | 1252119.0235 | 2682397.0538 | 1252121.6921
94 | 2682350.197 | 1252166.8412 | 2682351.6527 | 1252178.8482 | 2682352.4579 | 1252183.5958
95 | 2682344.4434 | 1252089.9371 | 2682369.3372 | 1252085.5102
96 | 2682344.4434 | 1252089.9371 | 2682344.1889 | 1252079.8267
97 | 2682474.6118 | 1252099.3775 | 2682471.4449 | 1252100.0023
98 | 2682523.077 | 1252124.3143 | 2682525.7681 | 1252138.8896
99 | 2682520.3984 | 1252124.7996 | 2682523.077 | 1252124.3143
100 | 2682193.6675 | 1252245.3466 | 2682190.8289 | 1252231.0465
101 | 2682129.8756 | 1252289.3918 | 2682137.2574 | 1252288.7681
102 | 2682137.3633 | 1252288.7592 | 2682137.2574 | 1252288.7681
103 | 2682472.0795 | 1252189.1599 | 2682450.5994 | 1252192.7585
104 | 2682264.6971 | 1252144.1367 | 2682271.0486 | 1252154.7106 | 2682276.2176 | 1252158.1377
105 | 2682264.6971 | 1252144.1367 | 2682264.7881 | 1252139.2121
106 | 2682350.197 | 1252166.8412 | 2682349.7629 | 1252164.3578
107 | 2682283.8848 | 1252284.6748 | 2682283.7423 | 1252263.8088
108 | 2682248.8921 | 1252252.2982 | 2682248.7051 | 1252261.4135
109 | 2682371.0208 | 1252099.547 | 2682372.4259 | 1252105.4265 | 2682375.7598 | 1252114.2572 | 2682374.8656 | 1252125.3642 | 2682376.4961 | 1252125.3535 | 2682377.9264 | 1252126.1629 | 2682378.7522 | 1252127.5643
110 | 2682343.7866 | 1252063.8418 | 2682343.3835 | 1252047.8274
111 | 2682344.1889 | 1252079.8267 | 2682343.7866 | 1252063.8418
112 | 2682375.7404 | 1252084.3715 | 2682369.3372 | 1252085.5102
113 | 2682375.7404 | 1252084.3715 | 2682382.0809 | 1252083.244
114 | 2682280.2737 | 1252136.8522 | 2682289.2564 | 1252135.0727
115 | 2682280.2737 | 1252136.8522 | 2682274.4734 | 1252138.0012 | 2682267.4591 | 1252138.8781
116 | 2682264.7881 | 1252139.2121 | 2682264.7881 | 1252139.2121 | 2682267.4591 | 1252138.8781
117 | 2682290.1476 | 1252159.9555 | 2682281.1896 | 1252161.4342 | 2682276.2176 | 1252158.1377
118 | 2682290.1476 | 1252159.9555 | 2682295.8538 | 1252159.0136
119 | 2682203.9708 | 1252274.5248 | 2682201.9432 | 1252263.9777
120 | 2682199.4646 | 1252274.5512 | 2682203.9708 | 1252274.5248
121 | 2682204.7944 | 1252278.8061 | 2682203.9708 | 1252274.5248
122 | 2682200.3043 | 1252255.4525 | 2682201.9432 | 1252263.9777
123 | 2682199.4646 | 1252274.5512 | 2682195.1096 | 1252252.6116
124 | 2682204.7944 | 1252278.8061 | 2682207.3983 | 1252292.3695
125 | 2682201.1916 | 1252283.3484 | 2682200.4017 | 1252279.3567 | 2682204.7944 | 1252278.8061
126 | 2682252.3099 | 1252284.4363 | 2682252.0978 | 1252270.9121 | 2682248.7051 | 1252261.4135
127 | 2682197.6272 | 1252241.527 | 2682200.3043 | 1252255.4525
128 | 2682193.6675 | 1252245.3466 | 2682195.1096 | 1252252.6116
129 | 2682204.73 | 1252301.3887 | 2682208.9682 | 1252300.5469 | 2682207.3983 | 1252292.3695
130 | 2682201.1916 | 1252283.3484 | 2682181.9305 | 1252284.9936 | 2682176.8624 | 1252285.4218
131 | 2682176.8624 | 1252285.4218 | 2682176.2168 | 1252285.4763
132 | 2682204.73 | 1252301.3887 | 2682207.4625 | 1252314.5178
133 | 2682207.4625 | 1252314.5178 | 2682208.3553 | 1252318.8075
134 | 2682176.2168 | 1252285.4763 | 2682159.4277 | 1252286.8949
135 | 2682159.4277 | 1252286.8949 | 2682158.8588 | 1252286.943
136 | 2682151.8339 | 1252287.5365 | 2682158.8588 | 1252286.943
137 | 2682151.8339 | 1252287.5365 | 2682151.6248 | 1252287.5542
138 | 2682208.3553 | 1252318.8075 | 2682209.4002 | 1252323.8283
139 | 2682151.6248 | 1252287.5542 | 2682137.3633 | 1252288.7592
140 | 2682239.954 | 1252336.0665 | 2682211.8831 | 1252335.7581 | 2682209.4002 | 1252323.8283
141 | 2682239.954 | 1252336.0665 | 2682242.5507 | 1252336.095 | 2682255.5905 | 1252336.7807
142 | 2682239.954 | 1252336.0665 | 2682218.7942 | 1252376.7374
143 | 2682265.4845 | 1252337.301 | 2682255.5905 | 1252336.7807
144 | 2682218.7942 | 1252376.7374 | 2682221.0984 | 1252390.469
145 | 2682272.8325 | 1252337.7859 | 2682267.5518 | 1252337.4097 | 2682265.4845 | 1252337.301
146 | 2682224.8349 | 1252412.7363 | 2682224.3307 | 1252409.7318
147 | 2682224.8349 | 1252412.7363 | 2682225.42 | 1252416.2232
148 | 2682222.2942 | 1252397.5956 | 2682224.3307 | 1252409.7318
149 | 2682221.0984 | 1252390.469 | 2682222.2942 | 1252397.5956
150 | 2682272.8325 | 1252337.7859 | 2682290.3909 | 1252339.0368
151 | 2682378.7522 | 1252127.5643 | 2682385.995 | 1252127.2314 | 2682390.9664 | 1252125.7772 | 2682397.0538 | 1252121.6921
152 | 2682482.5656 | 1252187.4032 | 2682472.0795 | 1252189.1599

## bus_geodata
| x | y | coords
0 | 2682298.1844 | 1252018.4451
1 | 2682299.1491 | 1252032.4427
2 | 2682301.4898 | 1252043.2071
3 | 2682317.2348 | 1252030.6844
4 | 2682358.3067 | 1252032.5313
5 | 2682356.8265 | 1252013.6196
6 | 2682354.1183 | 1252032.4953
7 | 2682418.0177 | 1252110.542
8 | 2682442.7678 | 1252105.6595
9 | 2682421.3305 | 1252129.4133
10 | 2682430.7231 | 1252225.2823
11 | 2682423.5782 | 1252226.7284
12 | 2682401.95 | 1252209.17
13 | 2682416.3459 | 1252146.0564
14 | 2682439.1896 | 1252227.0347
15 | 2682359.444 | 1252240.547
16 | 2682362.9006 | 1252285.5954
17 | 2682323.6244 | 1252236.7131
18 | 2682355.61 | 1252202.1798
19 | 2682276.0752 | 1252077.5783
20 | 2682276.281 | 1252101.8445
21 | 2682250.5051 | 1252078.5685
22 | 2682291.6949 | 1252094.2082
23 | 2682249.7647 | 1252104.1662
24 | 2682517.1032 | 1252090.9951
25 | 2682492.1656 | 1252095.9146
26 | 2682518.2514 | 1252097.427
27 | 2682395.3632 | 1252294.1754
28 | 2682387.722 | 1252296.0372
29 | 2682403.5303 | 1252289.7745
30 | 2682411.3082 | 1252335.5725
31 | 2682383.3496 | 1252318.4598
32 | 2682398.3167 | 1252333.0455
33 | 2682411.0952 | 1252322.1373
34 | 2682366.5444 | 1252332.37
35 | 2682352.6133 | 1252308.9477
36 | 2682189.9769 | 1252201.7318
37 | 2682185.2152 | 1252202.7666
38 | 2682183.5654 | 1252151.4276
39 | 2682192.6684 | 1252215.7321
40 | 2682189.4228 | 1252223.9631
41 | 2682207.789 | 1252166.1312
42 | 2682456.3539 | 1252224.1052
43 | 2682433.574 | 1252195.6108
44 | 2682520.2454 | 1252108.5373
45 | 2682246.7441 | 1252173.8319
46 | 2682266.2491 | 1252185.8221
47 | 2682252.5321 | 1252164.2583
48 | 2682233.1895 | 1252165.5377
49 | 2682347.6662 | 1252151.2722
50 | 2682355.8165 | 1252149.7176
51 | 2682330.8608 | 1252130.9679
52 | 2682348.865 | 1252158.9613
53 | 2682260.5393 | 1252198.3973
54 | 2682281.9913 | 1252195.5375
55 | 2682235.5209 | 1252183.0941
56 | 2682251.7033 | 1252217.2666
57 | 2682283.5522 | 1252235.8337
58 | 2682283.6287 | 1252247.1654
59 | 2682282.8108 | 1252235.4015
60 | 2682343.9358 | 1252286.01
61 | 2682354.5651 | 1252277.1399
62 | 2682319.6809 | 1252256.7834
63 | 2682329.6402 | 1252130.2727
64 | 2682332.6753 | 1252122.6091
65 | 2682357.3581 | 1252098.858
66 | 2682325.6164 | 1252090.7094
67 | 2682341.1415 | 1252033.2044
68 | 2682358.0012 | 1252051.0265
69 | 2682376.9555 | 1252055.4016
70 | 2682370.523 | 1252056.4078
71 | 2682458.3519 | 1252102.5852
72 | 2682425.7716 | 1252145.0645
73 | 2682401.6372 | 1252207.242
74 | 2682384.8718 | 1252207.965
75 | 2682408.7326 | 1252147.5294
76 | 2682411.4389 | 1252119.0235
77 | 2682352.4579 | 1252183.5958
78 | 2682307.7856 | 1252094.4594
79 | 2682344.4434 | 1252089.9371
80 | 2682474.6118 | 1252099.3775
81 | 2682525.7681 | 1252138.8896
82 | 2682523.077 | 1252124.3143
83 | 2682338.673 | 1252327.4234
84 | 2682212.6104 | 1252153.8723
85 | 2682190.8289 | 1252231.0465
86 | 2682221.7073 | 1252174.6446
87 | 2682129.8756 | 1252289.3918
88 | 2682137.2574 | 1252288.7681
89 | 2682450.5994 | 1252192.7585
90 | 2682424.8407 | 1252154.678
91 | 2682264.6971 | 1252144.1367
92 | 2682349.7629 | 1252164.3578
93 | 2682264.1201 | 1252224.5053
94 | 2682283.7423 | 1252263.8088
95 | 2682248.8921 | 1252252.2982
96 | 2682315.7784 | 1252276.6451
97 | 2682371.0208 | 1252099.547
98 | 2682343.3835 | 1252047.8274
99 | 2682343.7866 | 1252063.8418
100 | 2682369.3372 | 1252085.5102
101 | 2682344.1889 | 1252079.8267
102 | 2682375.7404 | 1252084.3715
103 | 2682280.2737 | 1252136.8522
104 | 2682289.2564 | 1252135.0727
105 | 2682267.4591 | 1252138.8781
106 | 2682264.7881 | 1252139.2121
107 | 2682276.2176 | 1252158.1377
108 | 2682290.1476 | 1252159.9555
109 | 2682295.8538 | 1252159.0136
110 | 2682203.9708 | 1252274.5248
111 | 2682201.9432 | 1252263.9777
112 | 2682199.4646 | 1252274.5512
113 | 2682204.7944 | 1252278.8061
114 | 2682248.7051 | 1252261.4135
115 | 2682200.3043 | 1252255.4525
116 | 2682195.1096 | 1252252.6116
117 | 2682207.3983 | 1252292.3695
118 | 2682201.1916 | 1252283.3484
119 | 2682252.3099 | 1252284.4363
120 | 2682283.8848 | 1252284.6748
121 | 2682197.6272 | 1252241.527
122 | 2682193.6675 | 1252245.3466
123 | 2682176.8624 | 1252285.4218
124 | 2682204.73 | 1252301.3887
125 | 2682207.4625 | 1252314.5178
126 | 2682176.2168 | 1252285.4763
127 | 2682159.4277 | 1252286.8949
128 | 2682158.8588 | 1252286.943
129 | 2682151.8339 | 1252287.5365
130 | 2682208.3553 | 1252318.8075
131 | 2682151.6248 | 1252287.5542
132 | 2682209.4002 | 1252323.8283
133 | 2682137.3633 | 1252288.7592
134 | 2682239.954 | 1252336.0665
135 | 2682255.5905 | 1252336.7807
136 | 2682218.7942 | 1252376.7374
137 | 2682265.4845 | 1252337.301
138 | 2682224.8349 | 1252412.7363
139 | 2682224.3307 | 1252409.7318
140 | 2682225.42 | 1252416.2232
141 | 2682222.2942 | 1252397.5956
142 | 2682221.0984 | 1252390.469
143 | 2682272.8325 | 1252337.7859
144 | 2682290.3909 | 1252339.0368
145 | 2682397.0538 | 1252121.6921
146 | 2682378.7522 | 1252127.5643
147 | 2682382.0809 | 1252083.244
148 | 2682382.4801 | 1252208.4432
149 | 2682350.197 | 1252166.8412
150 | 2682472.0795 | 1252189.1599
151 | 2682482.5656 | 1252187.4032
152 | 2682471.4449 | 1252100.0023
153 | 2682520.3984 | 1252124.7996
154 | 2682350.197 | 1252166.8412

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98757 | -0.23801 | 0.0029463 | 0.00073842
1 | 0.98761 | -0.23727 | 0 | 0
2 | 0.98755 | -0.23847 | 0.0060856 | 0.0015252
3 | 0.98776 | -0.23433 | 0.0069207 | 0.0017345
4 | 0.98804 | -0.229 | 0 | 0
5 | 0.98801 | -0.2296 | 0.0017517 | 0.00043903
6 | 0.98804 | -0.22887 | 0 | 0
7 | 0.97105 | -0.55911 | 0 | 0
8 | 0.97077 | -0.56469 | 0.0020497 | 0.00051369
9 | 0.97126 | -0.55487 | 0.00153 | 0.00038346
10 | 0.97551 | -0.47116 | 0 | 0
11 | 0.97542 | -0.47289 | 0.012991 | 0.0032558
12 | 0.9747 | -0.48715 | 0 | 0
13 | 0.98103 | -0.36337 | 0 | 0
14 | 0.97329 | -0.51482 | 0 | 0
15 | 0.99618 | -0.072321 | 0 | 0
16 | 0.99029 | -0.18555 | 0 | 0
17 | 0.993 | -0.13291 | 0 | 0
18 | 1 | 0 | -0.42305 | -0.10811
19 | 0.99009 | -0.18916 | 0 | 0
20 | 0.99007 | -0.18961 | 0.001031 | 0.00025839
21 | 0.99005 | -0.1899 | 0 | 0
22 | 0.99015 | -0.18803 | 0.0034674 | 0.00086901
23 | 0.99002 | -0.19057 | 0.0014536 | 0.00036431
24 | 0.97029 | -0.57408 | 0 | 0
25 | 0.97039 | -0.5721 | 0.0017831 | 0.00044688
26 | 0.97027 | -0.5746 | 0 | 0
27 | 0.98643 | -0.26034 | 0 | 0
28 | 0.9864 | -0.26107 | 0.0052338 | 0.0013117
29 | 0.98634 | -0.2621 | 0.010465 | 0.0026227
30 | 0.98458 | -0.29644 | 0 | 0
31 | 0.98751 | -0.23949 | 0 | 0
32 | 0.98451 | -0.29776 | 0.0054429 | 0.0013641
33 | 0.98436 | -0.30076 | 0.017373 | 0.0043541
34 | 0.98733 | -0.2429 | 0.0072779 | 0.001824
35 | 0.98904 | -0.20981 | 0 | 0
36 | 0.97818 | -0.41863 | 0 | 0
37 | 0.97788 | -0.42455 | 0 | 0
38 | 0.98156 | -0.35293 | 0 | 0
39 | 0.97815 | -0.41919 | 0.0021702 | 0.0005439
40 | 0.97653 | -0.45091 | 0.0024097 | 0.00060392
41 | 0.9835 | -0.31535 | 0.0039136 | 0.00098083
42 | 0.97317 | -0.51728 | 0.007675 | 0.0019235
43 | 0.97233 | -0.53373 | 0 | 0
44 | 0.97022 | -0.57548 | 0.0014408 | 0.00036109
45 | 0.98552 | -0.27679 | 0 | 0
46 | 0.98584 | -0.2704 | 0.0066295 | 0.0016615
47 | 0.98541 | -0.27895 | 0.0012582 | 0.00031534
48 | 0.98545 | -0.27814 | 0.0015013 | 0.00037626
49 | 0.99535 | -0.088219 | 0 | 0
50 | 0.99526 | -0.089997 | 0.012218 | 0.0030621
51 | 0.99267 | -0.13924 | 0 | 0
52 | 0.99602 | -0.075513 | 0 | 0
53 | 0.98686 | -0.25067 | 0 | 0
54 | 0.98622 | -0.26305 | 0 | 0
55 | 0.98576 | -0.27173 | 0.003806 | 0.00095387
56 | 0.98785 | -0.2316 | 0 | 0
57 | 0.98966 | -0.19685 | 0 | 0
58 | 0.98943 | -0.20124 | 0 | 0
59 | 0.98961 | -0.19771 | 0.0055216 | 0.0013838
60 | 0.99019 | -0.18741 | 0.005515 | 0.0013822
61 | 0.99021 | -0.18703 | 0.0069191 | 0.0017341
62 | 0.99278 | -0.13719 | 0.0061005 | 0.0015289
63 | 0.99266 | -0.13955 | 0.012498 | 0.0031322
64 | 0.99204 | -0.15143 | 0 | 0
65 | 0.99022 | -0.18618 | 0.010001 | 0.0025065
66 | 0.99042 | -0.18269 | 0 | 0
67 | 0.98813 | -0.22725 | 0 | 0
68 | 0.98795 | -0.23061 | 0.0017497 | 0.00043852
69 | 0.98789 | -0.23193 | 0.0017583 | 0.00044068
70 | 0.9879 | -0.23173 | 0.0016348 | 0.00040972
71 | 0.97062 | -0.5676 | 0.0015673 | 0.00039281
72 | 0.97148 | -0.55069 | 0.0029399 | 0.00073681
73 | 0.97468 | -0.48752 | 0.010431 | 0.0026142
74 | 0.97446 | -0.49193 | 0 | 0
75 | 0.98095 | -0.3649 | 0.010899 | 0.0027316
76 | 0.98318 | -0.32147 | 0 | 0
77 | 0.99824 | -0.033353 | 0.0074342 | 0.0018632
78 | 0.99023 | -0.18633 | 0.0050037 | 0.0012541
79 | 0.98968 | -0.19705 | 0 | 0
80 | 0.97049 | -0.5701 | 0.0014491 | 0.00036319
81 | 0.97017 | -0.57655 | 0.00088403 | 0.00022156
82 | 0.97018 | -0.57631 | 0 | 0
83 | 0.98887 | -0.2131 | 0.0071546 | 0.0017931
84 | 0.98538 | -0.27952 | 0.0032534 | 0.00081539
85 | 0.9761 | -0.45942 | 0.0028712 | 0.00071958
86 | 0.98461 | -0.29393 | 0.0034289 | 0.00085936
87 | 0.97244 | -0.53145 | 0.00098578 | 0.00024706
88 | 0.97245 | -0.53131 | 0.0019 | 0.00047619
89 | 0.9721 | -0.53825 | 0.0047616 | 0.0011934
90 | 0.97163 | -0.54764 | 0.0015189 | 0.00038067
91 | 0.9852 | -0.28297 | 0 | 0
92 | 0.99649 | -0.066592 | 0.0095188 | 0.0023856
93 | 0.98853 | -0.21848 | 0.0054109 | 0.0013561
94 | 0.98927 | -0.20446 | 0.005496 | 0.0013774
95 | 0.98908 | -0.20815 | 0 | 0
96 | 0.99267 | -0.13924 | 0.0057259 | 0.001435
97 | 0.98897 | -0.21006 | 0 | 0
98 | 0.98844 | -0.22116 | 0.0049878 | 0.0012501
99 | 0.98885 | -0.2132 | 0.0049657 | 0.0012445
100 | 0.98956 | -0.19935 | 0.0017484 | 0.0004382
101 | 0.98933 | -0.20386 | 0.0050089 | 0.0012553
102 | 0.98954 | -0.19974 | 0.0016513 | 0.00041386
103 | 0.98513 | -0.28436 | 0.0017585 | 0.00044073
104 | 0.98512 | -0.28456 | 0.0011718 | 0.00029368
105 | 0.98516 | -0.28368 | 0.0013472 | 0.00033764
106 | 0.98517 | -0.28347 | 0.0014465 | 0.00036253
107 | 0.98514 | -0.28423 | 0.0016109 | 0.00040373
108 | 0.98511 | -0.28482 | 0.0010485 | 0.00026279
109 | 0.9851 | -0.28494 | 0.0011341 | 0.00028422
110 | 0.97343 | -0.5119 | 0 | 0
111 | 0.97334 | -0.5137 | 0.001882 | 0.00047166
112 | 0.97367 | -0.50721 | 0 | 0
113 | 0.97324 | -0.51573 | 0 | 0
114 | 0.98899 | -0.20993 | 0.0055801 | 0.0013985
115 | 0.97328 | -0.51485 | 0.0013297 | 0.00033324
116 | 0.97485 | -0.48389 | 0.0023901 | 0.00059902
117 | 0.97284 | -0.5236 | 0.0019374 | 0.00048556
118 | 0.9731 | -0.51835 | 0 | 0
119 | 0.98887 | -0.21219 | 0.0053675 | 0.0013452
120 | 0.98916 | -0.20645 | 0.0053509 | 0.0013411
121 | 0.9732 | -0.51638 | 0.0058748 | 0.0014724
122 | 0.97526 | -0.47585 | 0.0023791 | 0.00059627
123 | 0.97272 | -0.52587 | 0.0030579 | 0.00076638
124 | 0.97249 | -0.53036 | 0 | 0
125 | 0.97213 | -0.53754 | 0.0022992 | 0.00057624
126 | 0.97271 | -0.52604 | 0.0032526 | 0.00081518
127 | 0.97255 | -0.52928 | 0.002004 | 0.00050224
128 | 0.97255 | -0.52936 | 0.0015059 | 0.00037741
129 | 0.9725 | -0.53026 | 0.00097165 | 0.00024352
130 | 0.97202 | -0.5397 | 0.0019076 | 0.00047809
131 | 0.9725 | -0.53029 | 0.0020812 | 0.0005216
132 | 0.9719 | -0.54205 | 0.00091418 | 0.00022912
133 | 0.97245 | -0.53131 | 0.00098113 | 0.00024589
134 | 0.971 | -0.55981 | 0.0036772 | 0.00092159
135 | 0.97089 | -0.56215 | 0.002346 | 0.00058797
136 | 0.97048 | -0.57012 | 0.0055182 | 0.001383
137 | 0.97083 | -0.56319 | 0.0010577 | 0.00026509
138 | 0.97034 | -0.57298 | 0.00093054 | 0.00023321
139 | 0.97034 | -0.57288 | 0.0008343 | 0.0002091
140 | 0.97034 | -0.57302 | 0.00070101 | 0.00017569
141 | 0.97037 | -0.57232 | 0.0011727 | 0.0002939
142 | 0.9704 | -0.57183 | 0.0029992 | 0.00075166
143 | 0.9708 | -0.56383 | 0.0022521 | 0.00056442
144 | 0.97076 | -0.56461 | 0.0024047 | 0.00060268
145 | 0.98433 | -0.29923 | 0.012709 | 0.0031852
146 | 0.98612 | -0.26478 | 0 | 0
147 | 0.98953 | -0.19994 | 0.0017153 | 0.00042988
148 | 0.97443 | -0.49238 | 0.010227 | 0.0025631
149 | 0.99671 | -0.062273 | 0 | 0
150 | 0.97191 | -0.54205 | 0.0052259 | 0.0013097
151 | 0.97187 | -0.54288 | 0.004224 | 0.0010586
152 | 0.97052 | -0.56966 | 0.00088315 | 0.00022134
153 | 0.97018 | -0.5764 | 0.001901 | 0.00047644
154 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0029463 | -0.00073842 | 0.0029464 | 0.0007383 | 1.0395e-07 | -1.1345e-07 | 0.0044393 | 0.0044393 | 0.0044393 | 0.98757 | -0.23801 | 0.98761 | -0.23727 | 1.2196
1 | 0.0060859 | 0.0015253 | -0.0060856 | -0.0015252 | 3.4833e-07 | 8.1574e-08 | 0.0091695 | 0.0091696 | 0.0091696 | 0.98761 | -0.23727 | 0.98755 | -0.23847 | 2.5191
2 | -0.0090323 | -0.0022636 | 0.0090336 | 0.0022641 | 1.262e-06 | 5.751e-07 | 0.013609 | 0.013609 | 0.013609 | 0.98761 | -0.23727 | 0.98776 | -0.23433 | 3.7387
3 | -0.015954 | -0.0039986 | 0.01596 | 0.0040018 | 5.3875e-06 | 3.1296e-06 | 0.024034 | 0.024034 | 0.024034 | 0.98776 | -0.23433 | 0.98813 | -0.22725 | 6.6029
4 | 0.0017518 | 0.00043881 | -0.0017517 | -0.00043903 | 5.0263e-08 | -2.1446e-07 | 0.0026382 | 0.0026383 | 0.0026383 | 0.98804 | -0.229 | 0.98801 | -0.2296 | 0.7248
5 | -0.0017518 | -0.00043881 | 0.0017518 | 0.00043877 | 1.0899e-08 | -4.6508e-08 | 0.0026382 | 0.0026382 | 0.0026382 | 0.98804 | -0.229 | 0.98804 | -0.22887 | 0.72477
6 | -0.0068953 | -0.0017275 | 0.0068958 | 0.0017277 | 5.3276e-07 | 1.7221e-07 | 0.010384 | 0.010384 | 0.010384 | 0.98804 | -0.22887 | 0.98813 | -0.22725 | 2.8528
7 | 0.0051435 | 0.0012888 | -0.0051431 | -0.0012887 | 4.2603e-07 | 3.0188e-08 | 0.0077461 | 0.0077462 | 0.0077462 | 0.98804 | -0.22887 | 0.98795 | -0.23061 | 2.1281
8 | 0.011965 | 0.0029995 | -0.011962 | -0.0029978 | 3.1804e-06 | 1.7235e-06 | 0.018335 | 0.018335 | 0.018335 | 0.97105 | -0.55911 | 0.97077 | -0.56469 | 5.0372
9 | -0.011965 | -0.0029995 | 0.011968 | 0.0030009 | 2.4155e-06 | 1.3088e-06 | 0.018335 | 0.018335 | 0.018335 | 0.97105 | -0.55911 | 0.97126 | -0.55487 | 5.0372
10 | 0.0099123 | 0.0024841 | -0.0099109 | -0.0024834 | 1.3751e-06 | 6.837e-07 | 0.015194 | 0.015194 | 0.015194 | 0.97077 | -0.56469 | 0.97062 | -0.5676 | 4.1741
11 | -0.013498 | -0.0033843 | 0.0135 | 0.0033858 | 2.6879e-06 | 1.5128e-06 | 0.020679 | 0.020679 | 0.020679 | 0.97126 | -0.55487 | 0.97148 | -0.55069 | 5.6811
12 | 0.012992 | 0.0032564 | -0.012991 | -0.0032558 | 1.0705e-06 | 5.944e-07 | 0.019817 | 0.019817 | 0.019817 | 0.97551 | -0.47116 | 0.97542 | -0.47289 | 5.4443
13 | 0.020676 | 0.0051882 | -0.02066 | -0.0051786 | 1.575e-05 | 9.5536e-06 | 0.031541 | 0.031541 | 0.031541 | 0.97551 | -0.47116 | 0.9747 | -0.48715 | 8.6651
14 | -0.073646 | -0.018515 | 0.074027 | 0.018758 | 0.00038119 | 0.00024295 | 0.11236 | 0.11236 | 0.11236 | 0.97551 | -0.47116 | 0.98103 | -0.36337 | 30.8676
15 | 0.039978 | 0.010071 | -0.039895 | -0.010018 | 8.3288e-05 | 5.2561e-05 | 0.061 | 0.061 | 0.061 | 0.97551 | -0.47116 | 0.97329 | -0.51482 | 16.7583
16 | 0.010431 | 0.0026142 | -0.010431 | -0.0026142 | 1.8571e-07 | 9.4515e-08 | 0.015924 | 0.015924 | 0.015924 | 0.9747 | -0.48715 | 0.97468 | -0.48752 | 4.3747
17 | 0.010229 | 0.0025644 | -0.010227 | -0.0025632 | 2.3293e-06 | 1.1734e-06 | 0.015617 | 0.015617 | 0.015617 | 0.9747 | -0.48715 | 0.97446 | -0.49193 | 4.2904
18 | 0.0109 | 0.002732 | -0.010899 | -0.0027316 | 7.9258e-07 | 4.0964e-07 | 0.016533 | 0.016533 | 0.016533 | 0.98103 | -0.36337 | 0.98095 | -0.3649 | 4.5421
19 | -0.084927 | -0.02149 | 0.085098 | 0.021599 | 0.00017116 | 0.0001092 | 0.12889 | 0.12889 | 0.12889 | 0.98103 | -0.36337 | 0.98318 | -0.32147 | 35.4096
20 | 0.0076759 | 0.0019239 | -0.007675 | -0.0019235 | 8.9926e-07 | 3.5915e-07 | 0.011735 | 0.011735 | 0.011735 | 0.97329 | -0.51482 | 0.97317 | -0.51728 | 3.224
21 | 0.032219 | 0.0080943 | -0.03219 | -0.0080761 | 2.9052e-05 | 1.8197e-05 | 0.049265 | 0.049265 | 0.049265 | 0.97329 | -0.51482 | 0.97233 | -0.53373 | 13.5343
22 | 0.065951 | 0.016746 | -0.065594 | -0.016518 | 0.00035723 | 0.00022736 | 0.098589 | 0.09859 | 0.09859 | 0.99618 | -0.072321 | 0.99029 | -0.18555 | 27.0851
23 | 0.14899 | 0.03815 | -0.14855 | -0.037872 | 0.0004359 | 0.00027776 | 0.22283 | 0.22283 | 0.22283 | 0.99618 | -0.072321 | 0.993 | -0.13291 | 30.6088
24 | -0.21494 | -0.054896 | 0.21569 | 0.055378 | 0.00075432 | 0.00048174 | 0.32142 | 0.32142 | 0.32142 | 0.99618 | -0.072321 | 1 | 0 | 44.1512
25 | 0.0055155 | 0.0013822 | -0.005515 | -0.0013822 | 4.8713e-07 | 6.8459e-08 | 0.0082875 | 0.0082876 | 0.0082876 | 0.99029 | -0.18555 | 0.99019 | -0.18741 | 2.2768
26 | 0.0069196 | 0.0017342 | -0.0069191 | -0.0017341 | 4.862e-07 | 1.5688e-07 | 0.010397 | 0.010397 | 0.010397 | 0.99029 | -0.18555 | 0.99021 | -0.18703 | 2.8565
27 | 0.053159 | 0.013402 | -0.053097 | -0.013363 | 6.1616e-05 | 3.9104e-05 | 0.079905 | 0.079905 | 0.079905 | 0.99029 | -0.18555 | 0.98904 | -0.20981 | 21.9519
28 | 0.011829 | 0.0029654 | -0.011827 | -0.0029641 | 2.4103e-06 | 1.278e-06 | 0.017727 | 0.017727 | 0.017727 | 0.993 | -0.13291 | 0.99278 | -0.13719 | 4.87
29 | 0.13672 | 0.034907 | -0.1363 | -0.034639 | 0.00042101 | 0.00026807 | 0.20511 | 0.20511 | 0.20511 | 0.993 | -0.13291 | 0.98966 | -0.19685 | 28.1739
30 | 0.20571 | 0.052732 | -0.20538 | -0.05252 | 0.00033205 | 0.00021202 | 0.30651 | 0.30651 | 0.30651 | 1 | 0 | 0.99824 | -0.033353 | 42.1036
31 | 0.001031 | 0.0002581 | -0.001031 | -0.00025839 | 2.1849e-08 | -2.981e-07 | 0.0015494 | 0.0015495 | 0.0015495 | 0.99009 | -0.18916 | 0.99007 | -0.18961 | 0.4257
32 | 0.0014537 | 0.00036367 | -0.0014536 | -0.00036401 | 5.1159e-08 | -3.3487e-07 | 0.0021845 | 0.0021847 | 0.0021847 | 0.99009 | -0.18916 | 0.99005 | -0.1899 | 0.60019
33 | -0.0024847 | -0.00062177 | 0.0024849 | 0.00062152 | 1.3354e-07 | -2.4304e-07 | 0.003734 | 0.0037339 | 0.003734 | 0.99009 | -0.18916 | 0.99015 | -0.18803 | 1.0258
34 | 0.0014536 | 0.00036401 | -0.0014536 | -0.00036431 | 4.5841e-08 | -3e-07 | 0.0021847 | 0.0021848 | 0.0021848 | 0.99005 | -0.1899 | 0.99002 | -0.19057 | 0.60022
35 | -0.0059522 | -0.0014905 | 0.0059527 | 0.0014906 | 4.8283e-07 | 1.0201e-07 | 0.0089447 | 0.0089447 | 0.0089447 | 0.99015 | -0.18803 | 0.99023 | -0.18633 | 2.4573
36 | -0.0042262 | -0.0010587 | 0.0042266 | 0.0010587 | 4.0037e-07 | -5.7746e-08 | 0.0064811 | 0.006481 | 0.0064811 | 0.97029 | -0.57408 | 0.97039 | -0.5721 | 1.7805
37 | 0.0042262 | 0.0010587 | -0.0042261 | -0.0010587 | 1.0292e-07 | -1.4832e-08 | 0.0064811 | 0.0064811 | 0.0064811 | 0.97029 | -0.57408 | 0.97027 | -0.5746 | 1.7805
38 | -0.0060097 | -0.0015055 | 0.0060103 | 0.0015057 | 5.6976e-07 | 1.4359e-07 | 0.0092152 | 0.0092151 | 0.0092152 | 0.97039 | -0.5721 | 0.97049 | -0.5701 | 2.5316
39 | 0.0042261 | 0.0010587 | -0.004226 | -0.0010588 | 1.778e-07 | -2.5612e-08 | 0.0064811 | 0.0064812 | 0.0064812 | 0.97027 | -0.5746 | 0.97022 | -0.57548 | 1.7805
40 | 0.0052339 | 0.0013117 | -0.0052338 | -0.0013117 | 1.8334e-07 | 1.7218e-08 | 0.0078953 | 0.0078953 | 0.0078953 | 0.98643 | -0.26034 | 0.9864 | -0.26107 | 2.169
41 | 0.010466 | 0.0026232 | -0.010465 | -0.0026227 | 8.769e-07 | 4.4146e-07 | 0.015787 | 0.015787 | 0.015787 | 0.98643 | -0.26034 | 0.98634 | -0.2621 | 4.3372
42 | 0.022859 | 0.0057444 | -0.02282 | -0.0057204 | 3.9327e-05 | 2.4046e-05 | 0.034488 | 0.034489 | 0.034489 | 0.98643 | -0.26034 | 0.98458 | -0.29644 | 9.4749
43 | -0.038559 | -0.0096793 | 0.038597 | 0.0097035 | 3.8394e-05 | 2.4185e-05 | 0.058171 | 0.058171 | 0.058171 | 0.98643 | -0.26034 | 0.98751 | -0.23949 | 15.981
44 | 0.0054432 | 0.0013642 | -0.0054429 | -0.0013641 | 3.4034e-07 | 4.7272e-08 | 0.0082264 | 0.0082265 | 0.0082265 | 0.98458 | -0.29644 | 0.98451 | -0.29776 | 2.26
45 | 0.017377 | 0.0043562 | -0.017373 | -0.0043541 | 3.577e-06 | 2.1134e-06 | 0.026262 | 0.026262 | 0.026262 | 0.98458 | -0.29644 | 0.98436 | -0.30076 | 7.2149
46 | 0.007279 | 0.0018244 | -0.0072779 | -0.001824 | 1.1839e-06 | 4.2204e-07 | 0.010968 | 0.010969 | 0.010969 | 0.98751 | -0.23949 | 0.98733 | -0.2429 | 3.0133
47 | -0.045876 | -0.011528 | 0.045941 | 0.011569 | 6.5096e-05 | 4.1196e-05 | 0.069139 | 0.069139 | 0.069139 | 0.98751 | -0.23949 | 0.98904 | -0.20981 | 18.9943
48 | 0.0071557 | 0.0017935 | -0.0071546 | -0.0017931 | 1.1225e-06 | 3.8703e-07 | 0.010766 | 0.010766 | 0.010766 | 0.98904 | -0.20981 | 0.98887 | -0.2131 | 2.9577
49 | 0.067192 | 0.016976 | -0.067173 | -0.016964 | 1.9055e-05 | 1.2134e-05 | 0.10226 | 0.10226 | 0.10226 | 0.97818 | -0.41863 | 0.97788 | -0.42455 | 28.0938
50 | -0.069362 | -0.01752 | 0.069581 | 0.017659 | 0.00021913 | 0.00013959 | 0.10556 | 0.10556 | 0.10556 | 0.97818 | -0.41863 | 0.98156 | -0.35293 | 29.0007
51 | 0.0021702 | 0.00054376 | -0.0021702 | -0.0005439 | 5.8268e-08 | -1.4167e-07 | 0.0033013 | 0.0033014 | 0.0033014 | 0.97818 | -0.41863 | 0.97815 | -0.41919 | 0.90697
52 | 0.067173 | 0.016964 | -0.067088 | -0.01691 | 8.4745e-05 | 5.3966e-05 | 0.10226 | 0.10226 | 0.10226 | 0.97788 | -0.42455 | 0.97653 | -0.45091 | 28.0938
53 | -0.069581 | -0.017659 | 0.069707 | 0.01774 | 0.00012603 | 8.0277e-05 | 0.10556 | 0.10556 | 0.10556 | 0.98156 | -0.35293 | 0.9835 | -0.31535 | 29.0007
54 | 0.064678 | 0.016306 | -0.064652 | -0.016289 | 2.6323e-05 | 1.6756e-05 | 0.09859 | 0.09859 | 0.09859 | 0.97653 | -0.45091 | 0.9761 | -0.45942 | 27.0851
55 | -0.073621 | -0.01872 | 0.073697 | 0.018769 | 7.6042e-05 | 4.8459e-05 | 0.11148 | 0.11148 | 0.11148 | 0.9835 | -0.31535 | 0.98461 | -0.29393 | 30.6273
56 | 0.014216 | 0.0035643 | -0.014213 | -0.0035625 | 3.0642e-06 | 1.7471e-06 | 0.021757 | 0.021757 | 0.021757 | 0.97233 | -0.53373 | 0.9721 | -0.53825 | 5.9771
57 | 0.017973 | 0.0045118 | -0.017961 | -0.0045047 | 1.1916e-05 | 7.106e-06 | 0.027508 | 0.027508 | 0.027508 | 0.97233 | -0.53373 | 0.97163 | -0.54764 | 7.5573
58 | 0.0027852 | 0.00069767 | -0.0027851 | -0.0006978 | 1.0967e-07 | -1.2775e-07 | 0.0042715 | 0.0042715 | 0.0042715 | 0.97022 | -0.57548 | 0.97018 | -0.57631 | 1.1735
59 | -0.015534 | -0.0038931 | 0.015539 | 0.0038958 | 4.7235e-06 | 2.7312e-06 | 0.023455 | 0.023455 | 0.023455 | 0.98552 | -0.27679 | 0.98584 | -0.2704 | 6.4437
60 | 0.010779 | 0.0027016 | -0.010778 | -0.002701 | 1.1113e-06 | 5.6868e-07 | 0.016275 | 0.016275 | 0.016275 | 0.98552 | -0.27679 | 0.98541 | -0.27895 | 4.4713
61 | 0.0047552 | 0.0011915 | -0.0047549 | -0.0011915 | 3.0719e-07 | -5.8675e-09 | 0.0071798 | 0.0071798 | 0.0071798 | 0.98552 | -0.27679 | 0.98545 | -0.27814 | 1.9725
62 | -0.022169 | -0.0055573 | 0.022176 | 0.005562 | 7.7672e-06 | 4.735e-06 | 0.033462 | 0.033461 | 0.033462 | 0.98584 | -0.2704 | 0.98622 | -0.26305 | 9.1927
63 | 0.0095199 | 0.0023857 | -0.0095181 | -0.0023848 | 1.8222e-06 | 8.6672e-07 | 0.014376 | 0.014376 | 0.014376 | 0.98541 | -0.27895 | 0.9852 | -0.28297 | 3.9493
64 | 0.0032536 | 0.00081522 | -0.0032534 | -0.00081539 | 2.1432e-07 | -1.6448e-07 | 0.0049129 | 0.004913 | 0.004913 | 0.98545 | -0.27814 | 0.98538 | -0.27952 | 1.3497
65 | 0.012219 | 0.0030627 | -0.012218 | -0.0030621 | 1.0354e-06 | 5.5509e-07 | 0.018267 | 0.018267 | 0.018267 | 0.99535 | -0.088219 | 0.99526 | -0.089997 | 5.0184
66 | 0.17569 | 0.04488 | -0.17526 | -0.044605 | 0.00043223 | 0.00027576 | 0.26295 | 0.26295 | 0.26295 | 0.99535 | -0.088219 | 0.99267 | -0.13924 | 36.1198
67 | -0.18791 | -0.047943 | 0.18802 | 0.048017 | 0.00011539 | 7.365e-05 | 0.28122 | 0.28122 | 0.28122 | 0.99535 | -0.088219 | 0.99602 | -0.075513 | 38.629
68 | 0.012498 | 0.0031323 | -0.012498 | -0.0031322 | 1.8453e-07 | 9.9972e-08 | 0.018734 | 0.018734 | 0.018734 | 0.99267 | -0.13924 | 0.99266 | -0.13955 | 5.1468
69 | 0.16276 | 0.041472 | -0.16266 | -0.041411 | 9.5648e-05 | 6.0994e-05 | 0.24422 | 0.24422 | 0.24422 | 0.99267 | -0.13924 | 0.99204 | -0.15143 | 33.5465
70 | -0.18802 | -0.048017 | 0.1881 | 0.048068 | 8.1125e-05 | 5.1777e-05 | 0.28122 | 0.28122 | 0.28122 | 0.99602 | -0.075513 | 0.99649 | -0.066592 | 38.629
71 | 0.02219 | 0.00557 | -0.022176 | -0.005562 | 1.3099e-05 | 7.9851e-06 | 0.033461 | 0.033461 | 0.033461 | 0.98686 | -0.25067 | 0.98622 | -0.26305 | 9.1927
72 | 0.081097 | 0.020687 | -0.081014 | -0.020635 | 8.2397e-05 | 5.1986e-05 | 0.12241 | 0.12241 | 0.12241 | 0.98686 | -0.25067 | 0.98576 | -0.27173 | 16.8146
73 | -0.10329 | -0.026257 | 0.10338 | 0.026317 | 9.494e-05 | 6.0229e-05 | 0.15587 | 0.15587 | 0.15587 | 0.98686 | -0.25067 | 0.98785 | -0.2316 | 21.4109
74 | 0.077208 | 0.019681 | -0.077126 | -0.019628 | 8.2649e-05 | 5.2689e-05 | 0.11667 | 0.11667 | 0.11667 | 0.98576 | -0.27173 | 0.98461 | -0.29393 | 32.0509
75 | -0.10338 | -0.026317 | 0.10345 | 0.026359 | 6.5475e-05 | 4.1535e-05 | 0.15587 | 0.15587 | 0.15587 | 0.98785 | -0.2316 | 0.98853 | -0.21848 | 21.4108
76 | 0.021806 | 0.0054683 | -0.021802 | -0.0054655 | 4.5689e-06 | 2.7785e-06 | 0.032788 | 0.032788 | 0.032788 | 0.98966 | -0.19685 | 0.98943 | -0.20124 | 9.0078
77 | 0.11449 | 0.029171 | -0.11449 | -0.029168 | 4.7776e-06 | 3.0356e-06 | 0.17232 | 0.17232 | 0.17232 | 0.98966 | -0.19685 | 0.98961 | -0.19771 | 23.67
78 | 0.010849 | 0.0027194 | -0.010847 | -0.0027185 | 1.6616e-06 | 8.4967e-07 | 0.016316 | 0.016316 | 0.016316 | 0.98943 | -0.20124 | 0.98927 | -0.20446 | 4.4825
79 | 0.010953 | 0.0027461 | -0.010949 | -0.0027443 | 3.6029e-06 | 1.8513e-06 | 0.016472 | 0.016472 | 0.016472 | 0.98943 | -0.20124 | 0.98908 | -0.20815 | 4.5254
80 | 0.10897 | 0.027784 | -0.10886 | -0.027715 | 0.00010913 | 6.9285e-05 | 0.16402 | 0.16402 | 0.16402 | 0.98961 | -0.19771 | 0.98853 | -0.21848 | 22.5296
81 | 0.0057265 | 0.0014351 | -0.0057259 | -0.001435 | 5.5919e-07 | 9.618e-08 | 0.0085831 | 0.0085831 | 0.0085831 | 0.99278 | -0.13719 | 0.99267 | -0.13924 | 2.358
82 | 0.10862 | 0.027807 | -0.10844 | -0.027691 | 0.00018246 | 0.00011583 | 0.16313 | 0.16313 | 0.16313 | 0.99204 | -0.15143 | 0.99022 | -0.18618 | 22.4081
83 | 0.054046 | 0.013604 | -0.053965 | -0.013553 | 8.0624e-05 | 5.1178e-05 | 0.081088 | 0.081088 | 0.081088 | 0.99204 | -0.15143 | 0.99042 | -0.18269 | 22.2769
84 | 0.098434 | 0.025185 | -0.09832 | -0.025112 | 0.00011366 | 7.2565e-05 | 0.1481 | 0.1481 | 0.1481 | 0.99022 | -0.18618 | 0.98897 | -0.21006 | 40.6875
85 | 0.043007 | 0.010807 | -0.042978 | -0.010789 | 2.9463e-05 | 1.8615e-05 | 0.064624 | 0.064624 | 0.064624 | 0.99042 | -0.18269 | 0.98968 | -0.19705 | 17.754
86 | 0.010958 | 0.0027457 | -0.010956 | -0.0027447 | 1.901e-06 | 9.76e-07 | 0.016464 | 0.016464 | 0.016464 | 0.99042 | -0.18269 | 0.99023 | -0.18633 | 4.523
87 | -0.022856 | -0.0057295 | 0.022862 | 0.0057335 | 6.6356e-06 | 4.0554e-06 | 0.034419 | 0.034418 | 0.034419 | 0.98813 | -0.22725 | 0.98844 | -0.22116 | 9.4556
88 | 0.0033933 | 0.00085021 | -0.0033932 | -0.00085033 | 1.8051e-07 | -1.2043e-07 | 0.0051108 | 0.0051109 | 0.0051109 | 0.98795 | -0.23061 | 0.9879 | -0.23173 | 1.4041
89 | -0.0017583 | -0.00044068 | 0.0017583 | 0.00044061 | 1.7126e-08 | -7.2399e-08 | 0.0026485 | 0.0026485 | 0.0026485 | 0.98789 | -0.23193 | 0.9879 | -0.23173 | 0.72761
90 | 0.0083436 | 0.0020906 | -0.0083427 | -0.0020903 | 8.1879e-07 | 3.591e-07 | 0.012791 | 0.012791 | 0.012791 | 0.97062 | -0.5676 | 0.97052 | -0.56966 | 3.514
91 | -0.01644 | -0.0041226 | 0.016443 | 0.004124 | 2.3936e-06 | 1.4073e-06 | 0.025182 | 0.025182 | 0.025182 | 0.97148 | -0.55069 | 0.97163 | -0.54764 | 6.9182
92 | 0.010227 | 0.0025632 | -0.010227 | -0.0025631 | 2.2243e-07 | 1.1206e-07 | 0.015617 | 0.015617 | 0.015617 | 0.97446 | -0.49193 | 0.97443 | -0.49238 | 4.2904
93 | -0.085098 | -0.021599 | 0.085189 | 0.021658 | 9.1145e-05 | 5.8147e-05 | 0.12889 | 0.12889 | 0.12889 | 0.98318 | -0.32147 | 0.98433 | -0.29923 | 35.4096
94 | 0.19794 | 0.050657 | -0.19766 | -0.05048 | 0.00027674 | 0.00017667 | 0.29543 | 0.29543 | 0.29543 | 0.99824 | -0.033353 | 0.99671 | -0.062273 | 40.5814
95 | 0.0051156 | 0.0012819 | -0.0051151 | -0.0012818 | 5.6093e-07 | 3.413e-08 | 0.0076914 | 0.0076916 | 0.0076916 | 0.98968 | -0.19705 | 0.98956 | -0.19935 | 2.1131
96 | 0.037862 | 0.0095069 | -0.03785 | -0.0094992 | 1.2293e-05 | 7.7378e-06 | 0.056933 | 0.056933 | 0.056933 | 0.98968 | -0.19705 | 0.98933 | -0.20386 | 15.641
97 | -0.0074594 | -0.0018689 | 0.0074596 | 0.0018689 | 1.5834e-07 | 6.1449e-08 | 0.011437 | 0.011437 | 0.011437 | 0.97049 | -0.5701 | 0.97052 | -0.56966 | 3.142
98 | -0.00088403 | -0.00022156 | 0.00088404 | 0.00022138 | 1.0218e-08 | -1.7648e-07 | 0.0013559 | 0.0013558 | 0.0013559 | 0.97017 | -0.57655 | 0.97018 | -0.57631 | 0.3725
99 | 0.001901 | 0.00047641 | -0.001901 | -0.00047644 | 8.6522e-09 | -2.7976e-08 | 0.0029157 | 0.0029157 | 0.0029157 | 0.97018 | -0.57631 | 0.97018 | -0.5764 | 0.80102
100 | 0.061781 | 0.01557 | -0.061732 | -0.015539 | 4.8527e-05 | 3.0875e-05 | 0.094213 | 0.094213 | 0.094213 | 0.9761 | -0.45942 | 0.97526 | -0.47585 | 25.8826
101 | -0.00098578 | -0.00024706 | 0.00098579 | 0.00024697 | 6.3208e-09 | -8.7861e-08 | 0.0015084 | 0.0015084 | 0.0015084 | 0.97244 | -0.53145 | 0.97245 | -0.53131 | 0.4144
102 | -0.0028858 | -0.00072316 | 0.0028858 | 0.00072316 | 7.7895e-10 | -8.2059e-10 | 0.0044157 | 0.0044157 | 0.0044157 | 0.97245 | -0.53131 | 0.97245 | -0.53131 | 1.2131
103 | 0.0094517 | 0.0023692 | -0.00945 | -0.0023683 | 1.7096e-06 | 8.242e-07 | 0.014468 | 0.014468 | 0.014468 | 0.9721 | -0.53825 | 0.97191 | -0.54205 | 3.9748
104 | 0.0037938 | 0.00095043 | -0.0037936 | -0.00095052 | 2.2823e-07 | -8.9963e-08 | 0.0057299 | 0.00573 | 0.00573 | 0.9852 | -0.28297 | 0.98514 | -0.28423 | 1.5742
105 | 0.0057243 | 0.0014344 | -0.0057242 | -0.0014343 | 1.3806e-07 | 2.5643e-08 | 0.0086457 | 0.0086457 | 0.0086457 | 0.9852 | -0.28297 | 0.98517 | -0.28347 | 2.3752
106 | -0.19762 | -0.050454 | 0.19766 | 0.05048 | 4.1258e-05 | 2.6339e-05 | 0.29543 | 0.29543 | 0.29543 | 0.99649 | -0.066592 | 0.99671 | -0.062273 | 40.5814
107 | 0.0053514 | 0.0013411 | -0.0053509 | -0.0013411 | 5.07e-07 | 5.6601e-08 | 0.0080494 | 0.0080495 | 0.0080495 | 0.98927 | -0.20446 | 0.98916 | -0.20645 | 2.2114
108 | 0.010949 | 0.0027443 | -0.010948 | -0.0027438 | 9.2771e-07 | 4.7673e-07 | 0.016472 | 0.016473 | 0.016473 | 0.98908 | -0.20815 | 0.98899 | -0.20993 | 4.5254
109 | 0.09832 | 0.025112 | -0.098061 | -0.024947 | 0.00025933 | 0.00016557 | 0.1481 | 0.1481 | 0.1481 | 0.98897 | -0.21006 | 0.98612 | -0.26478 | 40.6875
110 | -0.02785 | -0.0069836 | 0.027861 | 0.0069901 | 1.056e-05 | 6.5531e-06 | 0.041927 | 0.041927 | 0.041927 | 0.98844 | -0.22116 | 0.98885 | -0.2132 | 11.5185
111 | -0.032826 | -0.0082347 | 0.032841 | 0.0082438 | 1.4633e-05 | 9.1597e-06 | 0.0494 | 0.049399 | 0.0494 | 0.98885 | -0.2132 | 0.98933 | -0.20386 | 13.5713
112 | 0.0033667 | 0.00084363 | -0.0033666 | -0.00084367 | 6.2504e-08 | -4.3547e-08 | 0.0050624 | 0.0050625 | 0.0050625 | 0.98956 | -0.19935 | 0.98954 | -0.19974 | 1.3908
113 | 0.0017153 | 0.00042981 | -0.0017153 | -0.00042988 | 1.6067e-08 | -7.2447e-08 | 0.0025793 | 0.0025793 | 0.0025793 | 0.98954 | -0.19974 | 0.98953 | -0.19994 | 0.7086
114 | 0.0011718 | 0.00029357 | -0.0011718 | -0.00029368 | 1.0758e-08 | -1.097e-07 | 0.0017699 | 0.00177 | 0.00177 | 0.98513 | -0.28436 | 0.98512 | -0.28456 | 0.48626
115 | -0.0029303 | -0.0007343 | 0.0029304 | 0.0007342 | 9.5372e-08 | -1.0425e-07 | 0.0044262 | 0.0044261 | 0.0044262 | 0.98513 | -0.28436 | 0.98516 | -0.28368 | 1.216
116 | -0.0042776 | -0.0010718 | 0.0042777 | 0.0010718 | 4.2137e-08 | -7.307e-09 | 0.0064609 | 0.0064609 | 0.0064609 | 0.98516 | -0.28368 | 0.98517 | -0.28347 | 1.775
117 | 0.0021827 | 0.00054679 | -0.0021826 | -0.00054695 | 6.1321e-08 | -1.523e-07 | 0.0032968 | 0.0032969 | 0.0032969 | 0.98514 | -0.28423 | 0.98511 | -0.28482 | 0.90573
118 | 0.0011341 | 0.00028415 | -0.0011341 | -0.00028422 | 6.3643e-09 | -6.9558e-08 | 0.001713 | 0.001713 | 0.001713 | 0.98511 | -0.28482 | 0.9851 | -0.28494 | 0.47061
119 | 0.009088 | 0.0022779 | -0.0090872 | -0.0022775 | 7.773e-07 | 3.6397e-07 | 0.013892 | 0.013892 | 0.013892 | 0.97343 | -0.5119 | 0.97334 | -0.5137 | 3.8166
120 | -0.056864 | -0.014281 | 0.056877 | 0.014289 | 1.2734e-05 | 8.0937e-06 | 0.086935 | 0.086935 | 0.086935 | 0.97343 | -0.5119 | 0.97367 | -0.50721 | 23.8832
121 | 0.047776 | 0.012003 | -0.047767 | -0.011997 | 8.7231e-06 | 5.5286e-06 | 0.073042 | 0.073042 | 0.073042 | 0.97343 | -0.5119 | 0.97324 | -0.51573 | 20.0666
122 | 0.0072053 | 0.0018058 | -0.0072049 | -0.0018057 | 3.9501e-07 | 1.4491e-07 | 0.011015 | 0.011015 | 0.011015 | 0.97334 | -0.5137 | 0.97328 | -0.51485 | 3.0262
123 | -0.056877 | -0.014289 | 0.05694 | 0.014329 | 6.3393e-05 | 4.0293e-05 | 0.086935 | 0.086935 | 0.086935 | 0.97367 | -0.50721 | 0.97485 | -0.48389 | 23.8832
124 | 0.031017 | 0.007796 | -0.031005 | -0.0077887 | 1.1652e-05 | 7.2854e-06 | 0.047431 | 0.047431 | 0.047431 | 0.97324 | -0.51573 | 0.97284 | -0.5236 | 13.0305
125 | 0.01675 | 0.0042011 | -0.016748 | -0.0041999 | 2.0899e-06 | 1.232e-06 | 0.025611 | 0.025612 | 0.025612 | 0.97324 | -0.51573 | 0.9731 | -0.51835 | 7.0361
126 | 0.0053681 | 0.0013453 | -0.0053675 | -0.0013452 | 5.7763e-07 | 6.6728e-08 | 0.0080768 | 0.0080769 | 0.0080769 | 0.98899 | -0.20993 | 0.98887 | -0.21219 | 2.2189
127 | 0.0058752 | 0.0014725 | -0.0058748 | -0.0014724 | 4.2905e-07 | 9.8378e-08 | 0.0089824 | 0.0089825 | 0.0089825 | 0.97328 | -0.51485 | 0.9732 | -0.51638 | 2.4677
128 | -0.05933 | -0.014928 | 0.059353 | 0.014942 | 2.279e-05 | 1.4493e-05 | 0.090583 | 0.090583 | 0.090583 | 0.97485 | -0.48389 | 0.97526 | -0.47585 | 24.8854
129 | 0.029068 | 0.0073032 | -0.029058 | -0.0072973 | 9.3785e-06 | 5.8453e-06 | 0.044468 | 0.044468 | 0.044468 | 0.97284 | -0.5236 | 0.97249 | -0.53036 | 12.2164
130 | 0.016748 | 0.0041999 | -0.016742 | -0.0041963 | 6.0062e-06 | 3.5408e-06 | 0.025612 | 0.025612 | 0.025612 | 0.9731 | -0.51835 | 0.97272 | -0.52587 | 7.0362
131 | 0.013684 | 0.0034299 | -0.013684 | -0.0034299 | 1.0646e-07 | 6.0094e-08 | 0.020934 | 0.020934 | 0.020934 | 0.97272 | -0.52587 | 0.97271 | -0.52604 | 5.7511
132 | 0.029058 | 0.0072973 | -0.029049 | -0.0072911 | 9.9441e-06 | 6.1979e-06 | 0.044468 | 0.044468 | 0.044468 | 0.97249 | -0.53036 | 0.97213 | -0.53754 | 12.2164
133 | 0.026749 | 0.0067149 | -0.026747 | -0.0067132 | 2.7551e-06 | 1.709e-06 | 0.040948 | 0.040948 | 0.040948 | 0.97213 | -0.53754 | 0.97202 | -0.5397 | 11.2496
134 | 0.010432 | 0.0026147 | -0.01043 | -0.0026139 | 1.6091e-06 | 8.2068e-07 | 0.015958 | 0.015958 | 0.015958 | 0.97271 | -0.52604 | 0.97255 | -0.52928 | 4.3841
135 | 0.0084262 | 0.0021116 | -0.0084261 | -0.0021116 | 3.5587e-08 | 1.569e-08 | 0.012892 | 0.012892 | 0.012892 | 0.97255 | -0.52928 | 0.97255 | -0.52936 | 3.5418
136 | 0.0069203 | 0.0017342 | -0.00692 | -0.0017341 | 2.9638e-07 | 1.0221e-07 | 0.010588 | 0.010588 | 0.010588 | 0.97255 | -0.52936 | 0.9725 | -0.53026 | 2.9088
137 | 0.0059483 | 0.0014906 | -0.0059483 | -0.0014906 | 6.5206e-09 | 1.5683e-09 | 0.0091014 | 0.0091014 | 0.0091014 | 0.9725 | -0.53026 | 0.9725 | -0.53029 | 2.5004
138 | 0.024839 | 0.0062351 | -0.024836 | -0.0062334 | 2.7811e-06 | 1.7164e-06 | 0.038028 | 0.038028 | 0.038028 | 0.97202 | -0.5397 | 0.9719 | -0.54205 | 10.4473
139 | 0.0038671 | 0.00096899 | -0.0038669 | -0.00096905 | 1.8791e-07 | -5.7311e-08 | 0.005917 | 0.005917 | 0.005917 | 0.9725 | -0.53029 | 0.97245 | -0.53131 | 1.6256
140 | 0.023922 | 0.0060043 | -0.023902 | -0.0059918 | 2.0255e-05 | 1.2465e-05 | 0.036629 | 0.036629 | 0.036629 | 0.9719 | -0.54205 | 0.971 | -0.55981 | 10.0629
141 | 0.0080619 | 0.0020204 | -0.008061 | -0.0020201 | 8.9604e-07 | 3.7985e-07 | 0.012355 | 0.012355 | 0.012355 | 0.971 | -0.55981 | 0.97089 | -0.56215 | 3.3941
142 | 0.012163 | 0.0030498 | -0.012157 | -0.0030465 | 5.973e-06 | 3.2559e-06 | 0.018639 | 0.018639 | 0.018639 | 0.971 | -0.55981 | 0.97048 | -0.57012 | 5.1207
143 | 0.005715 | 0.0014321 | -0.0057147 | -0.001432 | 2.8505e-07 | 5.9911e-08 | 0.008759 | 0.008759 | 0.008759 | 0.97089 | -0.56215 | 0.97083 | -0.56319 | 2.4063
144 | 0.0066384 | 0.0016635 | -0.0066378 | -0.0016633 | 5.4093e-07 | 1.7417e-07 | 0.010178 | 0.010178 | 0.010178 | 0.97048 | -0.57012 | 0.9704 | -0.57183 | 2.7963
145 | 0.004657 | 0.0011669 | -0.0046569 | -0.0011669 | 1.407e-07 | -1.0089e-09 | 0.0071378 | 0.0071379 | 0.0071379 | 0.97083 | -0.56319 | 0.9708 | -0.56383 | 1.961
146 | -0.0016315 | -0.00040886 | 0.0016316 | 0.00040883 | 7.1515e-09 | -3.3056e-08 | 0.002502 | 0.002502 | 0.002502 | 0.97034 | -0.57298 | 0.97034 | -0.57288 | 0.68735
147 | 0.00070101 | 0.00017565 | -0.00070101 | -0.00017569 | 1.5322e-09 | -4.2694e-08 | 0.001075 | 0.001075 | 0.001075 | 0.97034 | -0.57298 | 0.97034 | -0.57302 | 0.29533
148 | -0.0024659 | -0.00061792 | 0.0024659 | 0.00061781 | 6.5983e-08 | -1.0979e-07 | 0.0037813 | 0.0037813 | 0.0037813 | 0.97034 | -0.57288 | 0.97037 | -0.57232 | 1.0388
149 | -0.0036386 | -0.00091172 | 0.0036387 | 0.00091168 | 8.436e-08 | -3.5281e-08 | 0.0055795 | 0.0055795 | 0.0055795 | 0.97037 | -0.57232 | 0.9704 | -0.57183 | 1.5328
150 | 0.0024048 | 0.00060252 | -0.0024047 | -0.00060268 | 8.9686e-08 | -1.6024e-07 | 0.003686 | 0.003686 | 0.003686 | 0.9708 | -0.56383 | 0.97076 | -0.56461 | 1.0126
151 | -0.097898 | -0.024843 | 0.098061 | 0.024947 | 0.00016254 | 0.00010378 | 0.1481 | 0.1481 | 0.1481 | 0.98433 | -0.29923 | 0.98612 | -0.26478 | 40.6876
152 | 0.0042241 | 0.0010586 | -0.004224 | -0.0010586 | 1.6676e-07 | -2.503e-08 | 0.0064672 | 0.0064673 | 0.0064673 | 0.97191 | -0.54205 | 0.97187 | -0.54288 | 1.7767

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.42878 | 0.10955

## res_load
| p_mw | q_mvar
0 | 0.0029463 | 0.00073842
1 | 0.0060856 | 0.0015252
2 | 0.0069207 | 0.0017345
3 | 0.0017517 | 0.00043903
4 | 0.0020497 | 0.00051369
5 | 0.00153 | 0.00038346
6 | 0.012991 | 0.0032558
7 | 0.0057352 | 0.0014374
8 | 0.001031 | 0.00025839
9 | 0.0034674 | 0.00086901
10 | 0.0014536 | 0.00036431
11 | 0.0017831 | 0.00044688
12 | 0.0052338 | 0.0013117
13 | 0.010465 | 0.0026227
14 | 0.0054429 | 0.0013641
15 | 0.017373 | 0.0043541
16 | 0.0072779 | 0.001824
17 | 0.0021702 | 0.0005439
18 | 0.0024097 | 0.00060392
19 | 0.0039136 | 0.00098083
20 | 0.007675 | 0.0019235
21 | 0.0014408 | 0.00036109
22 | 0.0066295 | 0.0016615
23 | 0.0012582 | 0.00031534
24 | 0.0015013 | 0.00037626
25 | 0.012218 | 0.0030621
26 | 0.003806 | 0.00095387
27 | 0.0055216 | 0.0013838
28 | 0.005515 | 0.0013822
29 | 0.0069191 | 0.0017341
30 | 0.0061005 | 0.0015289
31 | 0.012498 | 0.0031322
32 | 0.010001 | 0.0025065
33 | 0.0017497 | 0.00043852
34 | 0.0017583 | 0.00044068
35 | 0.0016348 | 0.00040972
36 | 0.0015673 | 0.00039281
37 | 0.0029399 | 0.00073681
38 | 0.010431 | 0.0026142
39 | 0.010899 | 0.0027316
40 | 0.0074342 | 0.0018632
41 | 0.0050037 | 0.0012541
42 | 0.0014491 | 0.00036319
43 | 0.00088403 | 0.00022156
44 | 0.0071546 | 0.0017931
45 | 0.0032534 | 0.00081539
46 | 0.0028712 | 0.00071958
47 | 0.0034289 | 0.00085936
48 | 0.00098578 | 0.00024706
49 | 0.0019 | 0.00047619
50 | 0.0047616 | 0.0011934
51 | 0.0015189 | 0.00038067
52 | 0.0095188 | 0.0023856
53 | 0.0054109 | 0.0013561
54 | 0.005496 | 0.0013774
55 | 0.0057259 | 0.001435
56 | 0.0049878 | 0.0012501
57 | 0.0049657 | 0.0012445
58 | 0.0017484 | 0.0004382
59 | 0.0050089 | 0.0012553
60 | 0.0016513 | 0.00041386
61 | 0.0017585 | 0.00044073
62 | 0.0011718 | 0.00029368
63 | 0.0013472 | 0.00033764
64 | 0.0014465 | 0.00036253
65 | 0.0016109 | 0.00040373
66 | 0.0010485 | 0.00026279
67 | 0.0011341 | 0.00028422
68 | 0.001882 | 0.00047166
69 | 0.0055801 | 0.0013985
70 | 0.0013297 | 0.00033324
71 | 0.0023901 | 0.00059902
72 | 0.0019374 | 0.00048556
73 | 0.0053675 | 0.0013452
74 | 0.0053509 | 0.0013411
75 | 0.0058748 | 0.0014724
76 | 0.0023791 | 0.00059627
77 | 0.0030579 | 0.00076638
78 | 0.0022992 | 0.00057624
79 | 0.0032526 | 0.00081518
80 | 0.002004 | 0.00050224
81 | 0.0015059 | 0.00037741
82 | 0.00097165 | 0.00024352
83 | 0.0019076 | 0.00047809
84 | 0.0020812 | 0.0005216
85 | 0.00091418 | 0.00022912
86 | 0.00098113 | 0.00024589
87 | 0.0036772 | 0.00092159
88 | 0.002346 | 0.00058797
89 | 0.0055182 | 0.001383
90 | 0.0010577 | 0.00026509
91 | 0.00093054 | 0.00023321
92 | 0.0008343 | 0.0002091
93 | 0.00070101 | 0.00017569
94 | 0.0011727 | 0.0002939
95 | 0.0029992 | 0.00075166
96 | 0.0022521 | 0.00056442
97 | 0.0024047 | 0.00060268
98 | 0.012709 | 0.0031852
99 | 0.0017153 | 0.00042988
100 | 0.010227 | 0.0025631
101 | 0.0052259 | 0.0013097
102 | 0.004224 | 0.0010586
103 | 0.00088315 | 0.00022134
104 | 0.001901 | 0.00047644

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1