## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-490_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-490_0_5_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_261-490_0_5_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_261-490_0_5_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_261-490_0_5_node_44 | 0.4 | n |  | TRUE
5 | bus_LV_261-490_0_5_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_261-490_0_5_node_43 | 0.4 | n |  | TRUE
7 | bus_LV_261-490_0_5_node_132 | 0.4 | n |  | TRUE
8 | bus_LV_261-490_0_5_node_127 | 0.4 | n |  | TRUE
9 | bus_LV_261-490_0_5_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_261-490_0_5_node_50 | 0.4 | n |  | TRUE
11 | bus_LV_261-490_0_5_node_136 | 0.4 | n |  | TRUE
12 | bus_LV_261-490_0_5_node_138 | 0.4 | n |  | TRUE
13 | bus_LV_261-490_0_5_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_261-490_0_5_node_28 | 0.4 | n |  | TRUE
15 | bus_LV_261-490_0_5_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_261-490_0_5_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_261-490_0_5_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_261-490_0_5_node_51 | 0.4 | n |  | TRUE
19 | bus_LV_261-490_0_5_node_128 | 0.4 | n |  | TRUE
20 | bus_LV_261-490_0_5_node_140 | 0.4 | n |  | TRUE
21 | bus_LV_261-490_0_5_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_261-490_0_5_node_145 | 0.4 | n |  | TRUE
23 | bus_LV_261-490_0_5_node_146 | 0.4 | n |  | TRUE
24 | bus_LV_261-490_0_5_node_144 | 0.4 | n |  | TRUE
25 | bus_LV_261-490_0_5_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_261-490_0_5_node_65 | 0.4 | n |  | TRUE
27 | bus_LV_261-490_0_5_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_261-490_0_5_node_63 | 0.4 | n |  | TRUE
29 | bus_LV_261-490_0_5_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_261-490_0_5_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_261-490_0_5_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_261-490_0_5_node_88 | 0.4 | n |  | TRUE
33 | bus_LV_261-490_0_5_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_261-490_0_5_node_162 | 0.4 | n |  | TRUE
35 | bus_LV_261-490_0_5_node_90 | 0.4 | n |  | TRUE
36 | bus_LV_261-490_0_5_node_18 | 0.4 | n |  | TRUE
37 | bus_LV_261-490_0_5_node_21 | 0.4 | n |  | TRUE
38 | bus_LV_261-490_0_5_node_148 | 0.4 | n |  | TRUE
39 | bus_LV_261-490_0_5_node_19 | 0.4 | n |  | TRUE
40 | bus_LV_261-490_0_5_node_71 | 0.4 | n |  | TRUE
41 | bus_LV_261-490_0_5_node_72 | 0.4 | n |  | TRUE
42 | bus_LV_261-490_0_5_node_67 | 0.4 | n |  | TRUE
43 | bus_LV_261-490_0_5_node_85 | 0.4 | n |  | TRUE
44 | bus_LV_261-490_0_5_node_82 | 0.4 | n |  | TRUE
45 | bus_LV_261-490_0_5_node_143 | 0.4 | n |  | TRUE
46 | bus_LV_261-490_0_5_node_25 | 0.4 | n |  | TRUE
47 | bus_LV_261-490_0_5_node_26 | 0.4 | n |  | TRUE
48 | bus_LV_261-490_0_5_node_119 | 0.4 | n |  | TRUE
49 | bus_LV_261-490_0_5_node_123 | 0.4 | n |  | TRUE
50 | bus_LV_261-490_0_5_node_27 | 0.4 | n |  | TRUE
51 | bus_LV_261-490_0_5_node_31 | 0.4 | n |  | TRUE
52 | bus_LV_261-490_0_5_node_112 | 0.4 | n |  | TRUE
53 | bus_LV_261-490_0_5_node_157 | 0.4 | n |  | TRUE
54 | bus_LV_261-490_0_5_node_29 | 0.4 | n |  | TRUE
55 | bus_LV_261-490_0_5_node_47 | 0.4 | n |  | TRUE
56 | bus_LV_261-490_0_5_node_30 | 0.4 | n |  | TRUE
57 | bus_LV_261-490_0_5_node_120 | 0.4 | n |  | TRUE
58 | bus_LV_261-490_0_5_node_116 | 0.4 | n |  | TRUE
59 | bus_LV_261-490_0_5_node_32 | 0.4 | n |  | TRUE
60 | bus_LV_261-490_0_5_node_38 | 0.4 | n |  | TRUE
61 | bus_LV_261-490_0_5_node_158 | 0.4 | n |  | TRUE
62 | bus_LV_261-490_0_5_node_33 | 0.4 | n |  | TRUE
63 | bus_LV_261-490_0_5_node_110 | 0.4 | n |  | TRUE
64 | bus_LV_261-490_0_5_node_60 | 0.4 | n |  | TRUE
65 | bus_LV_261-490_0_5_node_35 | 0.4 | n |  | TRUE
66 | bus_LV_261-490_0_5_node_105 | 0.4 | n |  | TRUE
67 | bus_LV_261-490_0_5_node_102 | 0.4 | n |  | TRUE
68 | bus_LV_261-490_0_5_node_36 | 0.4 | n |  | TRUE
69 | bus_LV_261-490_0_5_node_100 | 0.4 | n |  | TRUE
70 | bus_LV_261-490_0_5_node_113 | 0.4 | n |  | TRUE
71 | bus_LV_261-490_0_5_node_37 | 0.4 | n |  | TRUE
72 | bus_LV_261-490_0_5_node_106 | 0.4 | n |  | TRUE
73 | bus_LV_261-490_0_5_node_101 | 0.4 | n |  | TRUE
74 | bus_LV_261-490_0_5_node_91 | 0.4 | n |  | TRUE
75 | bus_LV_261-490_0_5_node_40 | 0.4 | n |  | TRUE
76 | bus_LV_261-490_0_5_node_64 | 0.4 | n |  | TRUE
77 | bus_LV_261-490_0_5_node_68 | 0.4 | n |  | TRUE
78 | bus_LV_261-490_0_5_node_45 | 0.4 | n |  | TRUE
79 | bus_LV_261-490_0_5_node_130 | 0.4 | n |  | TRUE
80 | bus_LV_261-490_0_5_node_125 | 0.4 | n |  | TRUE
81 | bus_LV_261-490_0_5_node_49 | 0.4 | n |  | TRUE
82 | bus_LV_261-490_0_5_node_135 | 0.4 | n |  | TRUE
83 | bus_LV_261-490_0_5_node_126 | 0.4 | n |  | TRUE
84 | bus_LV_261-490_0_5_node_139 | 0.4 | n |  | TRUE
85 | bus_LV_261-490_0_5_node_151 | 0.4 | n |  | TRUE
86 | bus_LV_261-490_0_5_node_155 | 0.4 | n |  | TRUE
87 | bus_LV_261-490_0_5_node_86 | 0.4 | n |  | TRUE
88 | bus_LV_261-490_0_5_node_89 | 0.4 | n |  | TRUE
89 | bus_LV_261-490_0_5_node_150 | 0.4 | n |  | TRUE
90 | bus_LV_261-490_0_5_node_149 | 0.4 | n |  | TRUE
91 | bus_LV_261-490_0_5_node_84 | 0.4 | n |  | TRUE
92 | bus_LV_261-490_0_5_node_80 | 0.4 | n |  | TRUE
93 | bus_LV_261-490_0_5_node_66 | 0.4 | n |  | TRUE
94 | bus_LV_261-490_0_5_node_83 | 0.4 | n |  | TRUE
95 | bus_LV_261-490_0_5_node_122 | 0.4 | n |  | TRUE
96 | bus_LV_261-490_0_5_node_121 | 0.4 | n |  | TRUE
97 | bus_LV_261-490_0_5_node_117 | 0.4 | n |  | TRUE
98 | bus_LV_261-490_0_5_node_111 | 0.4 | n |  | TRUE
99 | bus_LV_261-490_0_5_node_46 | 0.4 | n |  | TRUE
100 | bus_LV_261-490_0_5_node_97 | 0.4 | n |  | TRUE
101 | bus_LV_261-490_0_5_node_104 | 0.4 | n |  | TRUE
102 | bus_LV_261-490_0_5_node_62 | 0.4 | n |  | TRUE
103 | bus_LV_261-490_0_5_node_56 | 0.4 | n |  | TRUE
104 | bus_LV_261-490_0_5_node_58 | 0.4 | n |  | TRUE
105 | bus_LV_261-490_0_5_node_103 | 0.4 | n |  | TRUE
106 | bus_LV_261-490_0_5_node_115 | 0.4 | n |  | TRUE
107 | bus_LV_261-490_0_5_node_93 | 0.4 | n |  | TRUE
108 | bus_LV_261-490_0_5_node_98 | 0.4 | n |  | TRUE
109 | bus_LV_261-490_0_5_node_114 | 0.4 | n |  | TRUE
110 | bus_LV_261-490_0_5_node_99 | 0.4 | n |  | TRUE
111 | bus_LV_261-490_0_5_node_161 | 0.4 | n |  | TRUE
112 | bus_LV_261-490_0_5_node_87 | 0.4 | n |  | TRUE
113 | bus_LV_261-490_0_5_node_69 | 0.4 | n |  | TRUE
114 | bus_LV_261-490_0_5_node_92 | 0.4 | n |  | TRUE
115 | bus_LV_261-490_0_5_node_160 | 0.4 | n |  | TRUE
116 | bus_LV_261-490_0_5_node_48 | 0.4 | n |  | TRUE
117 | bus_LV_261-490_0_5_node_52 | 0.4 | n |  | TRUE
118 | bus_LV_261-490_0_5_node_53 | 0.4 | n |  | TRUE
119 | bus_LV_261-490_0_5_node_54 | 0.4 | n |  | TRUE
120 | bus_LV_261-490_0_5_node_55 | 0.4 | n |  | TRUE
121 | bus_LV_261-490_0_5_node_57 | 0.4 | n |  | TRUE
122 | bus_LV_261-490_0_5_node_118 | 0.4 | n |  | TRUE
123 | bus_LV_261-490_0_5_node_59 | 0.4 | n |  | TRUE
124 | bus_LV_261-490_0_5_node_61 | 0.4 | n |  | TRUE
125 | bus_LV_261-490_0_5_node_81 | 0.4 | n |  | TRUE
126 | bus_LV_261-490_0_5_node_96 | 0.4 | n |  | TRUE
127 | bus_LV_261-490_0_5_node_94 | 0.4 | n |  | TRUE
128 | bus_LV_261-490_0_5_node_70 | 0.4 | n |  | TRUE
129 | bus_LV_261-490_0_5_node_77 | 0.4 | n |  | TRUE
130 | bus_LV_261-490_0_5_node_73 | 0.4 | n |  | TRUE
131 | bus_LV_261-490_0_5_node_74 | 0.4 | n |  | TRUE
132 | bus_LV_261-490_0_5_node_75 | 0.4 | n |  | TRUE
133 | bus_LV_261-490_0_5_node_76 | 0.4 | n |  | TRUE
134 | bus_LV_261-490_0_5_node_78 | 0.4 | n |  | TRUE
135 | bus_LV_261-490_0_5_node_79 | 0.4 | n |  | TRUE
136 | bus_LV_261-490_0_5_node_109 | 0.4 | n |  | TRUE
137 | bus_LV_261-490_0_5_node_108 | 0.4 | n |  | TRUE
138 | bus_LV_261-490_0_5_node_159 | 0.4 | n |  | TRUE
139 | bus_LV_261-490_0_5_node_95 | 0.4 | n |  | TRUE
140 | bus_LV_261-490_0_5_node_107 | 0.4 | n |  | TRUE
141 | bus_LV_261-490_0_5_node_124 | 0.4 | n |  | TRUE
142 | bus_LV_261-490_0_5_node_129 | 0.4 | n |  | TRUE
143 | bus_LV_261-490_0_5_node_131 | 0.4 | n |  | TRUE
144 | bus_LV_261-490_0_5_node_133 | 0.4 | n |  | TRUE
145 | bus_LV_261-490_0_5_node_134 | 0.4 | n |  | TRUE
146 | bus_LV_261-490_0_5_node_152 | 0.4 | n |  | TRUE
147 | bus_LV_261-490_0_5_node_153 | 0.4 | n |  | TRUE
148 | bus_LV_261-490_0_5_node_137 | 0.4 | n |  | TRUE
149 | bus_LV_261-490_0_5_node_141 | 0.4 | n |  | TRUE
150 | bus_LV_261-490_0_5_node_142 | 0.4 | n |  | TRUE
151 | bus_LV_261-490_0_5_node_147 | 0.4 | n |  | TRUE
152 | bus_LV_261-490_0_5_node_154 | 0.4 | n |  | TRUE
153 | bus_LV_261-490_0_5_node_156 | 0.4 | n |  | TRUE
154 | bus_MV_389_0_node_36 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-490_0_5_load_0 | 0 | 0.0082496 | 0.0020675 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-490_0_5_load_44 | 4 | 0.0078692 | 0.0019722 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-490_0_5_load_43 | 6 | 0.0034811 | 0.00087244 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-490_0_5_load_132 | 7 | 0.0026429 | 0.00066237 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-490_0_5_load_127 | 8 | 0.001821 | 0.00045639 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-490_0_5_load_50 | 10 | 0.0019209 | 0.00048143 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-490_0_5_load_136 | 11 | 0.0018289 | 0.00045837 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-490_0_5_load_138 | 12 | 0.0058309 | 0.0014614 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-490_0_5_load_51 | 18 | 0.022812 | 0.0057172 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-490_0_5_load_128 | 19 | 0.0037556 | 0.00094125 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-490_0_5_load_140 | 20 | 0.0023548 | 0.00059017 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-490_0_5_load_145 | 22 | 0.0035849 | 0.00089845 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-490_0_5_load_146 | 23 | 0.0019857 | 0.00049766 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-490_0_5_load_144 | 24 | 0.0037815 | 0.00094773 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-490_0_5_load_65 | 26 | 0.0058443 | 0.0014647 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-490_0_5_load_63 | 28 | 0.0056456 | 0.0014149 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-490_0_5_load_88 | 32 | 0.00371 | 0.00092981 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-490_0_5_load_162 | 34 | 0.0020808 | 0.0005215 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-490_0_5_load_90 | 35 | 0.0039726 | 0.00099562 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-490_0_5_load_148 | 38 | 0.0026275 | 0.00065852 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-490_0_5_load_72 | 41 | 0.0026785 | 0.00067131 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-490_0_5_load_67 | 42 | 0.0016582 | 0.00041558 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-490_0_5_load_85 | 43 | 0.0041159 | 0.0010315 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-490_0_5_load_82 | 44 | 0.0043128 | 0.0010809 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-490_0_5_load_143 | 45 | 0.0043458 | 0.0010892 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-490_0_5_load_119 | 48 | 0.0058095 | 0.001456 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-490_0_5_load_123 | 49 | 0.0056713 | 0.0014214 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-490_0_5_load_112 | 52 | 0.0050998 | 0.0012781 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-490_0_5_load_157 | 53 | 0.0043175 | 0.0010821 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-490_0_5_load_120 | 57 | 0.0059036 | 0.0014796 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-490_0_5_load_116 | 58 | 0.0032881 | 0.00082406 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-490_0_5_load_158 | 61 | 0.0043217 | 0.0010831 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-490_0_5_load_110 | 63 | 0.0052222 | 0.0013088 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-490_0_5_load_105 | 66 | 0.0043503 | 0.0010903 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-490_0_5_load_102 | 67 | 0.005421 | 0.0013586 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-490_0_5_load_100 | 69 | 0.0027844 | 0.00069783 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-490_0_5_load_106 | 72 | 0.0030119 | 0.00075486 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-490_0_5_load_101 | 73 | 0.003638 | 0.00091177 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-490_0_5_load_91 | 74 | 0.0046924 | 0.001176 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-490_0_5_load_64 | 76 | 0.0018651 | 0.00046744 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-490_0_5_load_68 | 77 | 0.0015635 | 0.00039185 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-490_0_5_load_45 | 78 | 0.0019554 | 0.00049007 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-490_0_5_load_130 | 79 | 0.001909 | 0.00047844 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-490_0_5_load_125 | 80 | 0.0019326 | 0.00048435 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-490_0_5_load_49 | 81 | 0.026114 | 0.0065448 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-490_0_5_load_135 | 82 | 0.0041125 | 0.0010307 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-490_0_5_load_126 | 83 | 0.0038997 | 0.00097736 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-490_0_5_load_139 | 84 | 0.0060674 | 0.0015206 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-490_0_5_load_151 | 85 | 0.0029344 | 0.00073544 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-490_0_5_load_155 | 86 | 0.019541 | 0.0048975 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-490_0_5_load_86 | 87 | 0.0038751 | 0.00097119 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-490_0_5_load_89 | 88 | 0.0042211 | 0.0010579 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-490_0_5_load_150 | 89 | 0.0026092 | 0.00065392 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-490_0_5_load_149 | 90 | 0.0026539 | 0.00066512 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-490_0_5_load_84 | 91 | 0.0061678 | 0.0015458 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-490_0_5_load_66 | 93 | 0.0058435 | 0.0014645 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-490_0_5_load_83 | 94 | 0.0014143 | 0.00035446 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-490_0_5_load_122 | 95 | 0.0094585 | 0.0023705 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-490_0_5_load_121 | 96 | 0.0058184 | 0.0014582 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-490_0_5_load_117 | 97 | 0.0056799 | 0.0014235 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-490_0_5_load_111 | 98 | 0.0055566 | 0.0013926 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-490_0_5_load_46 | 99 | 0.0094318 | 0.0023638 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-490_0_5_load_97 | 100 | 0.0022883 | 0.00057349 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-490_0_5_load_62 | 102 | 0.0074243 | 0.0018607 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-490_0_5_load_56 | 103 | 0.015986 | 0.0040065 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-490_0_5_load_58 | 104 | 0.0030277 | 0.0007588 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-490_0_5_load_103 | 105 | 0.0047647 | 0.0011941 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-490_0_5_load_98 | 108 | 0.0028385 | 0.00071138 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-490_0_5_load_114 | 109 | 0.0021986 | 0.00055103 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-490_0_5_load_99 | 110 | 0.0024984 | 0.00062615 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-490_0_5_load_161 | 111 | 0.0045577 | 0.0011423 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-490_0_5_load_87 | 112 | 0.0041354 | 0.0010364 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-490_0_5_load_69 | 113 | 0.0022336 | 0.00055979 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-490_0_5_load_92 | 114 | 0.0046699 | 0.0011704 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-490_0_5_load_160 | 115 | 0.0043362 | 0.0010867 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-490_0_5_load_48 | 116 | 0.0068208 | 0.0017094 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-490_0_5_load_52 | 117 | 0.0051325 | 0.0012863 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-490_0_5_load_53 | 118 | 0.0053656 | 0.0013447 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-490_0_5_load_55 | 120 | 0.0048352 | 0.0012118 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-490_0_5_load_118 | 122 | 0.0043659 | 0.0010942 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-490_0_5_load_59 | 123 | 0.0064552 | 0.0016178 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-490_0_5_load_61 | 124 | 0.0022563 | 0.00056549 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_261-490_0_5_load_81 | 125 | 0.0062936 | 0.0015773 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_261-490_0_5_load_96 | 126 | 0.0033777 | 0.00084653 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_261-490_0_5_load_94 | 127 | 0.011656 | 0.0029211 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_261-490_0_5_load_70 | 128 | 0.00068165 | 0.00017084 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_261-490_0_5_load_77 | 129 | 0.0032372 | 0.00081133 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_261-490_0_5_load_73 | 130 | 0.00075365 | 0.00018888 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_261-490_0_5_load_74 | 131 | 0.0022559 | 0.00056539 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_261-490_0_5_load_75 | 132 | 0.007655 | 0.0019185 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_261-490_0_5_load_76 | 133 | 0.00089496 | 0.0002243 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_261-490_0_5_load_78 | 134 | 0.0016265 | 0.00040764 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_261-490_0_5_load_79 | 135 | 0.0022575 | 0.00056578 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_261-490_0_5_load_109 | 136 | 0.0051261 | 0.0012847 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_261-490_0_5_load_108 | 137 | 0.0022563 | 0.00056549 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_261-490_0_5_load_159 | 138 | 0.0030175 | 0.00075625 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_261-490_0_5_load_95 | 139 | 0.0039514 | 0.00099031 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_261-490_0_5_load_107 | 140 | 0.0022575 | 0.00056579 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_261-490_0_5_load_124 | 141 | 0.0027083 | 0.00067876 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_261-490_0_5_load_129 | 142 | 0.0034345 | 0.00086077 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_261-490_0_5_load_133 | 144 | 0.0014258 | 0.00035735 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_261-490_0_5_load_134 | 145 | 0.0018764 | 0.00047027 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_261-490_0_5_load_152 | 146 | 0.002011 | 0.00050401 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_261-490_0_5_load_153 | 147 | 0.0032798 | 0.000822 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_261-490_0_5_load_137 | 148 | 0.0052299 | 0.0013107 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_261-490_0_5_load_141 | 149 | 0.0046442 | 0.0011639 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_261-490_0_5_load_142 | 150 | 0.0069601 | 0.0017444 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_261-490_0_5_load_147 | 151 | 0.014449 | 0.0036213 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_261-490_0_5_load_156 | 153 | 0.0049183 | 0.0012326 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 118 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-490_0_5_line_0 |  | 0 | 1 | 0.0069897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-490_0_5_line_1 |  | 1 | 2 | 0.009833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-490_0_5_line_2 |  | 1 | 3 | 0.0080799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-490_0_5_line_3 |  | 2 | 4 | 0.015738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-490_0_5_line_4 |  | 3 | 5 | 0.007503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-490_0_5_line_5 |  | 3 | 6 | 0.010533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-490_0_5_line_6 |  | 4 | 78 | 0.027865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-490_0_5_line_7 |  | 5 | 7 | 0.028193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-490_0_5_line_8 |  | 5 | 8 | 0.018991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-490_0_5_line_9 |  | 7 | 79 | 0.0097562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-490_0_5_line_10 |  | 8 | 80 | 0.021324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-490_0_5_line_11 |  | 9 | 10 | 0.010432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-490_0_5_line_12 |  | 9 | 11 | 0.030667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-490_0_5_line_13 |  | 9 | 12 | 0.017405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-490_0_5_line_14 |  | 10 | 81 | 0.036619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-490_0_5_line_15 |  | 11 | 82 | 0.0048712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-490_0_5_line_16 |  | 12 | 37 | 0.02124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-490_0_5_line_17 |  | 13 | 14 | 0.006464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_261-490_0_5_line_18 |  | 13 | 15 | 0.009938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_261-490_0_5_line_19 |  | 14 | 53 | 0.0064111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-490_0_5_line_20 |  | 14 | 47 | 0.0092585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_261-490_0_5_line_21 |  | 15 | 17 | 0.002927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-490_0_5_line_22 |  | 15 | 19 | 0.012361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_261-490_0_5_line_23 |  | 16 | 17 | 0.0093792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-490_0_5_line_24 |  | 16 | 18 | 0.0090183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-490_0_5_line_25 |  | 17 | 20 | 0.028117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-490_0_5_line_26 |  | 19 | 83 | 0.015926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-490_0_5_line_27 |  | 20 | 84 | 0.0020074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-490_0_5_line_28 |  | 21 | 22 | 0.034269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-490_0_5_line_29 |  | 21 | 23 | 0.022897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-490_0_5_line_30 |  | 21 | 24 | 0.018492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-490_0_5_line_31 |  | 22 | 85 | 0.0018419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-490_0_5_line_32 |  | 23 | 86 | 0.0088699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-490_0_5_line_33 |  | 25 | 26 | 0.011685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-490_0_5_line_34 |  | 25 | 27 | 0.0085325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-490_0_5_line_35 |  | 25 | 28 | 0.038504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-490_0_5_line_36 |  | 27 | 43 | 0.029416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-490_0_5_line_37 |  | 27 | 44 | 0.010579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-490_0_5_line_38 |  | 28 | 76 | 0.01941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-490_0_5_line_39 |  | 29 | 30 | 0.005412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-490_0_5_line_40 |  | 29 | 31 | 0.0098846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-490_0_5_line_41 |  | 29 | 32 | 0.022106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-490_0_5_line_42 |  | 30 | 33 | 0.042284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-490_0_5_line_43 |  | 30 | 34 | 0.01541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-490_0_5_line_44 |  | 31 | 35 | 0.01075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-490_0_5_line_45 |  | 32 | 87 | 0.016207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-490_0_5_line_46 |  | 33 | 45 | 0.01168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-490_0_5_line_47 |  | 35 | 37 | 0.0013771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-490_0_5_line_48 |  | 36 | 37 | 0.010463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-490_0_5_line_49 |  | 36 | 38 | 0.014209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-490_0_5_line_50 |  | 38 | 90 | 0.011157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-490_0_5_line_51 |  | 39 | 40 | 0.00352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-490_0_5_line_52 |  | 39 | 41 | 0.023587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-490_0_5_line_53 |  | 39 | 42 | 0.016184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-490_0_5_line_54 |  | 40 | 91 | 0.0047444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-490_0_5_line_55 |  | 41 | 92 | 0.00064047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-490_0_5_line_56 |  | 42 | 93 | 0.0058293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-490_0_5_line_57 |  | 43 | 88 | 0.019141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-490_0_5_line_58 |  | 44 | 94 | 0.019225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-490_0_5_line_59 |  | 46 | 47 | 0.004662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_261-490_0_5_line_60 |  | 46 | 48 | 0.017989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_261-490_0_5_line_61 |  | 47 | 49 | 0.042707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-490_0_5_line_62 |  | 48 | 97 | 0.015845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_261-490_0_5_line_63 |  | 49 | 56 | 0.01749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-490_0_5_line_64 |  | 50 | 51 | 0.004616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-490_0_5_line_65 |  | 50 | 52 | 0.021756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-490_0_5_line_66 |  | 51 | 58 | 0.012788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-490_0_5_line_67 |  | 52 | 98 | 0.016645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-490_0_5_line_68 |  | 53 | 54 | 0.011263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-490_0_5_line_69 |  | 54 | 55 | 0.004437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-490_0_5_line_70 |  | 55 | 99 | 0.016885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-490_0_5_line_71 |  | 56 | 57 | 0.03288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-490_0_5_line_72 |  | 57 | 96 | 0.00066796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-490_0_5_line_73 |  | 58 | 100 | 0.022182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-490_0_5_line_74 |  | 59 | 60 | 0.042474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-490_0_5_line_75 |  | 59 | 61 | 0.016692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-490_0_5_line_76 |  | 60 | 74 | 0.028865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-490_0_5_line_77 |  | 60 | 71 | 0.03173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-490_0_5_line_78 |  | 62 | 63 | 0.012686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-490_0_5_line_79 |  | 62 | 64 | 0.009862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_261-490_0_5_line_80 |  | 63 | 101 | 0.018373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_261-490_0_5_line_81 |  | 64 | 102 | 0.03475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-490_0_5_line_82 |  | 64 | 103 | 0.023608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
83 | LV_261-490_0_5_line_83 |  | 64 | 104 | 0.014411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_261-490_0_5_line_84 |  | 65 | 66 | 0.036649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_261-490_0_5_line_85 |  | 65 | 67 | 0.020947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_261-490_0_5_line_86 |  | 67 | 105 | 0.02381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_261-490_0_5_line_87 |  | 68 | 69 | 0.0062815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_261-490_0_5_line_88 |  | 68 | 70 | 0.0083771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_261-490_0_5_line_89 |  | 69 | 108 | 0.0091362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_261-490_0_5_line_90 |  | 70 | 109 | 0.0086442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_261-490_0_5_line_91 |  | 70 | 98 | 0.021573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_261-490_0_5_line_92 |  | 70 | 106 | 0.024001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_261-490_0_5_line_93 |  | 71 | 72 | 0.058896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_261-490_0_5_line_94 |  | 71 | 73 | 0.0096952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_261-490_0_5_line_95 |  | 73 | 110 | 0.023272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_261-490_0_5_line_96 |  | 75 | 76 | 0.026255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_261-490_0_5_line_97 |  | 75 | 77 | 0.04094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_261-490_0_5_line_98 |  | 77 | 113 | 0.015552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_261-490_0_5_line_99 |  | 79 | 142 | 0.016953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_261-490_0_5_line_100 |  | 80 | 141 | 0.012318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_261-490_0_5_line_101 |  | 82 | 148 | 0.00697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_261-490_0_5_line_102 |  | 83 | 141 | 0.012066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_261-490_0_5_line_103 |  | 84 | 149 | 0.028645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_261-490_0_5_line_104 |  | 85 | 89 | 0.018469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_261-490_0_5_line_105 |  | 86 | 152 | 0.0052541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_261-490_0_5_line_106 |  | 87 | 112 | 0.016847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_261-490_0_5_line_107 |  | 90 | 151 | 0.024221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_261-490_0_5_line_108 |  | 91 | 94 | 0.014455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_261-490_0_5_line_109 |  | 92 | 129 | 0.013469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-490_0_5_line_110 |  | 92 | 125 | 0.022827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_261-490_0_5_line_111 |  | 95 | 96 | 0.014941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_261-490_0_5_line_112 |  | 97 | 122 | 0.01439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
113 | LV_261-490_0_5_line_113 |  | 99 | 116 | 0.016828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_261-490_0_5_line_114 |  | 100 | 139 | 0.012823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_261-490_0_5_line_115 |  | 101 | 105 | 0.011796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_261-490_0_5_line_116 |  | 102 | 126 | 0.018451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_261-490_0_5_line_117 |  | 103 | 119 | 0.020506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
118 | LV_261-490_0_5_line_118 |  | 104 | 123 | 0.023709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_261-490_0_5_line_119 |  | 106 | 107 | 0.008697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_261-490_0_5_line_120 |  | 107 | 111 | 0.0090045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_261-490_0_5_line_121 |  | 108 | 110 | 0.021836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_261-490_0_5_line_122 |  | 109 | 138 | 0.0023538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_261-490_0_5_line_123 |  | 113 | 128 | 0.0093312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_261-490_0_5_line_124 |  | 114 | 115 | 0.012049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_261-490_0_5_line_125 |  | 115 | 138 | 0.01079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_261-490_0_5_line_126 |  | 117 | 118 | 0.031235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
127 | LV_261-490_0_5_line_127 |  | 117 | 119 | 0.022418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
128 | LV_261-490_0_5_line_128 |  | 118 | 120 | 0.004279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_261-490_0_5_line_129 |  | 119 | 121 | 0.002594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
130 | LV_261-490_0_5_line_130 |  | 121 | 122 | 0.0055648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
131 | LV_261-490_0_5_line_131 |  | 123 | 124 | 0.012361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_261-490_0_5_line_132 |  | 124 | 125 | 0.011811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_261-490_0_5_line_133 |  | 126 | 127 | 0.007159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_261-490_0_5_line_134 |  | 127 | 139 | 0.019931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_261-490_0_5_line_135 |  | 129 | 132 | 0.0059777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_261-490_0_5_line_136 |  | 130 | 131 | 0.014669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_261-490_0_5_line_137 |  | 130 | 132 | 0.013671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_261-490_0_5_line_138 |  | 131 | 133 | 0.0040115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_261-490_0_5_line_139 |  | 133 | 134 | 0.017679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_261-490_0_5_line_140 |  | 134 | 135 | 0.020248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_261-490_0_5_line_141 |  | 135 | 136 | 0.0024958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_261-490_0_5_line_142 |  | 136 | 137 | 0.016536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_261-490_0_5_line_143 |  | 137 | 140 | 0.0037654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_261-490_0_5_line_144 |  | 142 | 143 | 0.0035335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_261-490_0_5_line_145 |  | 143 | 144 | 0.011897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_261-490_0_5_line_146 |  | 143 | 145 | 0.01309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_261-490_0_5_line_147 |  | 144 | 146 | 0.0075323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_261-490_0_5_line_148 |  | 146 | 147 | 0.0040874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_261-490_0_5_line_149 |  | 147 | 152 | 0.023432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_261-490_0_5_line_150 |  | 149 | 150 | 0.0042002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_261-490_0_5_line_151 |  | 150 | 151 | 0.02416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_261-490_0_5_line_152 |  | 152 | 153 | 0.017442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-490_0_5_trafo_53 | 0.63 MVA 20/0.4 kV | 154 | 118 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2678591.9293 | 1249056.4557 | 2678596.2404 | 1249061.9576
1 | 2678591.9293 | 1249056.4557 | 2678585.8627 | 1249048.7029
2 | 2678585.4096 | 1249061.2283 | 2678588.5209 | 1249058.9456 | 2678591.9293 | 1249056.4557
3 | 2678585.8627 | 1249048.7029 | 2678576.1555 | 1249036.3149
4 | 2678580.7607 | 1249055.329 | 2678585.4096 | 1249061.2283
5 | 2678585.4096 | 1249061.2283 | 2678591.9058 | 1249069.5193
6 | 2678576.1555 | 1249036.3149 | 2678558.9688 | 1249014.3816
7 | 2678580.7607 | 1249055.329 | 2678553.8113 | 1249063.6087
8 | 2678580.7607 | 1249055.329 | 2678573.78 | 1249046.4634 | 2678569.0578 | 1249040.3732
9 | 2678544.4853 | 1249066.474 | 2678553.8113 | 1249063.6087
10 | 2678555.9913 | 1249023.5215 | 2678569.0578 | 1249040.3732
11 | 2678424.538 | 1249005.7134 | 2678434.3492 | 1249002.1694
12 | 2678424.538 | 1249005.7134 | 2678411.9804 | 1248977.7356
13 | 2678424.538 | 1249005.7134 | 2678408.1371 | 1249011.5408
14 | 2678468.7906 | 1248989.7288 | 2678434.3492 | 1249002.1694
15 | 2678409.9858 | 1248973.2915 | 2678411.9804 | 1248977.7356
16 | 2678388.7245 | 1249019.7611 | 2678394.1869 | 1249017.8431 | 2678397.5355 | 1249015.3077 | 2678408.1371 | 1249011.5408
17 | 2678538.9683 | 1248975.8173 | 2678532.9482 | 1248978.2171
18 | 2678523.7168 | 1248981.8975 | 2678529.1676 | 1248979.7236 | 2678532.9482 | 1248978.2171
19 | 2678538.9683 | 1248975.8173 | 2678544.8583 | 1248973.2857
20 | 2678535.6393 | 1248967.178 | 2678537.1146 | 1248970.9558 | 2678538.9683 | 1248975.8173
21 | 2678520.9914 | 1248982.9844 | 2678523.7168 | 1248981.8975
22 | 2678523.7168 | 1248981.8975 | 2678531.2909 | 1248991.6657
23 | 2678517.3757 | 1248974.3302 | 2678518.9641 | 1248978.1207 | 2678520.9914 | 1248982.9844
24 | 2678517.3757 | 1248974.3302 | 2678514.4228 | 1248975.492 | 2678511.3645 | 1248974.3506 | 2678508.9373 | 1248975.2274
25 | 2678520.9914 | 1248982.9844 | 2678494.5603 | 1248992.5731
26 | 2678531.2909 | 1248991.6657 | 2678541.05 | 1249004.2519
27 | 2678492.6733 | 1248993.2577 | 2678494.5603 | 1248992.5731
28 | 2678445.6592 | 1249099.8281 | 2678442.8554 | 1249096.0104 | 2678440.7245 | 1249095.5486 | 2678439.0104 | 1249094.4029 | 2678436.8672 | 1249092.0172 | 2678424.6608 | 1249073.6145
29 | 2678445.6592 | 1249099.8281 | 2678451.6558 | 1249096.3382 | 2678466.8314 | 1249091.4015
30 | 2678445.6592 | 1249099.8281 | 2678448.8859 | 1249104.2184 | 2678448.3895 | 1249106.3468 | 2678448.4677 | 1249108.4271 | 2678449.4806 | 1249110.631 | 2678452.663 | 1249114.9429 | 2678453.3006 | 1249115.702
31 | 2678423.6427 | 1249072.0796 | 2678424.6608 | 1249073.6145
32 | 2678466.8314 | 1249091.4015 | 2678475.2663 | 1249088.6576
33 | 2678341.1788 | 1248943.9663 | 2678342.4032 | 1248943.8825 | 2678343.5931 | 1248943.5535 | 2678351.8327 | 1248939.4081
34 | 2678341.1788 | 1248943.9663 | 2678343.0992 | 1248947.7834 | 2678345.0123 | 1248951.5892
35 | 2678341.1788 | 1248943.9663 | 2678339.889 | 1248943.8492 | 2678338.7451 | 1248943.5561 | 2678337.3944 | 1248942.9045 | 2678336.1528 | 1248941.9985 | 2678334.844 | 1248940.469 | 2678321.4283 | 1248912.5468
36 | 2678345.0123 | 1248951.5892 | 2678344.3541 | 1248952.8259 | 2678343.7548 | 1248954.1745 | 2678343.4637 | 1248955.6273 | 2678343.5479 | 1248957.2518 | 2678343.7651 | 1248958.5334 | 2678344.9528 | 1248961.2288 | 2678353.3018 | 1248978.5027
37 | 2678345.0123 | 1248951.5892 | 2678346.0085 | 1248950.4905 | 2678347.4486 | 1248949.5199 | 2678354.1116 | 1248946.3943
38 | 2678313.0222 | 1248895.051 | 2678321.4283 | 1248912.5468
39 | 2678362.6499 | 1249028.3005 | 2678367.8144 | 1249026.6342
40 | 2678367.8144 | 1249026.6342 | 2678373.6993 | 1249024.7439 | 2678377.2257 | 1249023.6119
41 | 2678367.8144 | 1249026.6342 | 2678364.3023 | 1249018.6931 | 2678358.4546 | 1249006.611
42 | 2678362.6499 | 1249028.3005 | 2678364.4545 | 1249033.4503 | 2678366.2664 | 1249038.6225 | 2678357.1763 | 1249041.3488 | 2678363.9112 | 1249057.9721 | 2678366.3245 | 1249061.0618
43 | 2678362.6499 | 1249028.3005 | 2678350.8445 | 1249031.3467 | 2678347.6269 | 1249031.4042
44 | 2678377.2257 | 1249023.6119 | 2678383.2395 | 1249021.6789 | 2678387.4246 | 1249020.2156
45 | 2678351.3938 | 1248992.0225 | 2678358.4546 | 1249006.611
46 | 2678366.3245 | 1249061.0618 | 2678373.5162 | 1249070.2655
47 | 2678388.7245 | 1249019.7611 | 2678387.4246 | 1249020.2156
48 | 2678388.7245 | 1249019.7611 | 2678390.819 | 1249025.2595 | 2678392.4464 | 1249029.5397
49 | 2678392.4464 | 1249029.5397 | 2678405.8072 | 1249024.7051
50 | 2678405.8072 | 1249024.7051 | 2678416.298 | 1249020.909
51 | 2678387.2944 | 1248926.9412 | 2678388.8992 | 1248930.0758
52 | 2678387.2944 | 1248926.9412 | 2678408.6303 | 1248916.8854
53 | 2678387.2944 | 1248926.9412 | 2678385.4616 | 1248923.3477 | 2678377.4334 | 1248926.8441 | 2678374.3831 | 1248928.3316
54 | 2678388.8992 | 1248930.0758 | 2678384.6039 | 1248932.0907
55 | 2678408.6303 | 1248916.8854 | 2678409.2097 | 1248916.6123
56 | 2678369.1436 | 1248930.8867 | 2678374.3831 | 1248928.3316
57 | 2678361.6314 | 1248995.7362 | 2678353.3018 | 1248978.5027
58 | 2678371.5169 | 1248938.2297 | 2678354.1116 | 1248946.3943
59 | 2678535.6393 | 1248967.178 | 2678531.2897 | 1248968.8883
60 | 2678531.2897 | 1248968.8883 | 2678524.6837 | 1248952.1557
61 | 2678535.6393 | 1248967.178 | 2678537.4923 | 1248964.1114 | 2678540.6729 | 1248962.8637 | 2678573.4186 | 1248948.6246
62 | 2678524.6837 | 1248952.1557 | 2678523.7789 | 1248949.8638 | 2678521.9117 | 1248944.8799 | 2678518.7314 | 1248937.4755
63 | 2678589.4574 | 1248941.6502 | 2678573.4186 | 1248948.6246
64 | 2678598.5442 | 1248820.7936 | 2678601.1024 | 1248816.9469
65 | 2678601.1024 | 1248816.9469 | 2678581.2023 | 1248808.155
66 | 2678598.5442 | 1248820.7936 | 2678593.5815 | 1248827.7217 | 2678589.7396 | 1248829.5764
67 | 2678566.1775 | 1248800.998 | 2678577.4907 | 1248806.5152 | 2678581.2023 | 1248808.155
68 | 2678555.2058 | 1248968.8384 | 2678544.8583 | 1248973.2857
69 | 2678559.2918 | 1248967.0801 | 2678555.2058 | 1248968.8384
70 | 2678559.2918 | 1248967.0801 | 2678559.5528 | 1248969.0406 | 2678559.8059 | 1248970.4561 | 2678560.1295 | 1248971.1053 | 2678561.7005 | 1248973.3611 | 2678567.6352 | 1248981.4032
71 | 2678589.4574 | 1248941.6502 | 2678585.473 | 1248930.0556 | 2678587.6447 | 1248929.1504 | 2678580.2973 | 1248912.4261
72 | 2678580.2973 | 1248912.4261 | 2678580.0286 | 1248911.8146 | 2678580.0286 | 1248911.8146
73 | 2678589.7396 | 1248829.5764 | 2678569.7632 | 1248839.2199
74 | 2678450.6558 | 1248744.6907 | 2678462.1429 | 1248744.0534 | 2678468.1925 | 1248745.7124 | 2678470.7814 | 1248748.0928 | 2678475.2229 | 1248744.0264 | 2678480.1306 | 1248739.5325 | 2678484.0516 | 1248741.1189 | 2678488.0101 | 1248742.7281
75 | 2678450.6558 | 1248744.6907 | 2678443.307 | 1248746.4726 | 2678434.4482 | 1248748.6806
76 | 2678488.0101 | 1248742.7281 | 2678490.4236 | 1248738.9684 | 2678493.6136 | 1248737.5874 | 2678514.3967 | 1248735.1883
77 | 2678485.79 | 1248763.814 | 2678481.4459 | 1248759.3867 | 2678485.4363 | 1248755.1697 | 2678482.6522 | 1248752.1307 | 2678482.581 | 1248744.3907 | 2678484.0516 | 1248741.1189 | 2678488.0101 | 1248742.7281
78 | 2678482.0493 | 1248870.6202 | 2678477.8626 | 1248871.9991 | 2678475.4409 | 1248864.0834
79 | 2678485.9087 | 1248879.7001 | 2678482.0493 | 1248870.6202
80 | 2678470.5141 | 1248846.3943 | 2678471.9706 | 1248852.7404 | 2678475.4409 | 1248864.0834
81 | 2678485.9087 | 1248879.7001 | 2678517.2027 | 1248864.5931
82 | 2678485.9087 | 1248879.7001 | 2678490.1674 | 1248886.0055 | 2678492.1733 | 1248889.6347 | 2678498.9831 | 1248899.3363
83 | 2678485.9087 | 1248879.7001 | 2678472.9229 | 1248885.9497
84 | 2678462.6315 | 1248790.4158 | 2678456.0041 | 1248791.8959 | 2678449.136 | 1248796.1637 | 2678441.7303 | 1248799.9685 | 2678430.3502 | 1248807.1299
85 | 2678462.6315 | 1248790.4158 | 2678465.0053 | 1248809.6057 | 2678465.1964 | 1248811.2049
86 | 2678465.1964 | 1248811.2049 | 2678467.3031 | 1248828.839 | 2678468.3917 | 1248834.7907
87 | 2678541.7508 | 1248794.3884 | 2678539.7298 | 1248798.7315 | 2678538.3513 | 1248799.3004
88 | 2678546.7877 | 1248791.542 | 2678543.7588 | 1248789.8895 | 2678541.7508 | 1248794.3884
89 | 2678530.2111 | 1248795.7557 | 2678531.4447 | 1248796.5202 | 2678537.6416 | 1248799.5934 | 2678538.3513 | 1248799.3004
90 | 2678546.7877 | 1248791.542 | 2678548.9635 | 1248787.4901 | 2678550.9839 | 1248783.9857
91 | 2678546.7877 | 1248791.542 | 2678566.1775 | 1248800.998
92 | 2678546.7877 | 1248791.542 | 2678543.7588 | 1248789.8895 | 2678525.7199 | 1248780.0434
93 | 2678485.79 | 1248763.814 | 2678483.5694 | 1248763.8402 | 2678480.8142 | 1248765.4605 | 2678472.9092 | 1248775.0295 | 2678471.7281 | 1248779.2503 | 2678471.3188 | 1248783.359 | 2678471.9251 | 1248791.1727 | 2678474.7148 | 1248815.7331
94 | 2678485.79 | 1248763.814 | 2678493.2298 | 1248770.0306
95 | 2678511.843 | 1248783.958 | 2678500.9073 | 1248776.4456 | 2678493.2298 | 1248770.0306
96 | 2678302.1471 | 1248871.2422 | 2678306.4392 | 1248880.1721 | 2678306.6225 | 1248881.7312 | 2678313.0222 | 1248895.051
97 | 2678302.1471 | 1248871.2422 | 2678317.376 | 1248864.0158 | 2678330.8663 | 1248858.0675 | 2678339.3527 | 1248854.1661
98 | 2678339.3527 | 1248854.1661 | 2678352.52 | 1248848.113 | 2678353.495 | 1248847.6975
99 | 2678528.2801 | 1249071.4527 | 2678544.4853 | 1249066.474
100 | 2678548.4435 | 1249013.7873 | 2678555.9913 | 1249023.5215
101 | 2678407.1317 | 1248966.9326 | 2678409.9858 | 1248973.2915
102 | 2678548.4435 | 1249013.7873 | 2678541.05 | 1249004.2519
103 | 2678492.6733 | 1248993.2577 | 2678476.4883 | 1248999.1292 | 2678465.7419 | 1249003.0178
104 | 2678423.6427 | 1249072.0796 | 2678416.0483 | 1249060.63 | 2678413.3044 | 1249056.7775
105 | 2678480.2626 | 1249087.0322 | 2678475.2663 | 1249088.6576
106 | 2678351.3938 | 1248992.0225 | 2678344.0542 | 1248976.8579
107 | 2678439.0738 | 1249012.6676 | 2678416.298 | 1249020.909
108 | 2678371.5169 | 1248938.2297 | 2678384.6039 | 1248932.0907
109 | 2678409.2097 | 1248916.6123 | 2678403.6544 | 1248904.3422
110 | 2678409.2097 | 1248916.6123 | 2678429.7784 | 1248906.7134
111 | 2678580.0286 | 1248911.8146 | 2678582.1293 | 1248910.5749 | 2678592.9023 | 1248904.2323
112 | 2678512.8787 | 1248924.3373 | 2678516.2462 | 1248931.3506 | 2678517.8241 | 1248935.3633 | 2678518.7314 | 1248937.4755
113 | 2678577.6273 | 1248994.9434 | 2678567.6352 | 1248981.4032
114 | 2678558.2153 | 1248844.7945 | 2678569.7632 | 1248839.2199
115 | 2678470.5141 | 1248846.3943 | 2678468.3917 | 1248834.7907
116 | 2678517.2027 | 1248864.5931 | 2678533.8192 | 1248856.5716
117 | 2678509.3229 | 1248916.9929 | 2678505.1531 | 1248908.5426 | 2678500.0593 | 1248900.8696 | 2678498.9831 | 1248899.3363
118 | 2678451.559 | 1248896.2313 | 2678472.9229 | 1248885.9497
119 | 2678518.5818 | 1248775.0453 | 2678525.7199 | 1248780.0434
120 | 2678518.5818 | 1248775.0453 | 2678522.4759 | 1248767.2578 | 2678522.7008 | 1248767.4529
121 | 2678530.2111 | 1248795.7557 | 2678518.0223 | 1248788.203 | 2678511.843 | 1248783.958
122 | 2678552.1595 | 1248781.9465 | 2678550.9839 | 1248783.9857
123 | 2678362.0794 | 1248844.0395 | 2678353.495 | 1248847.6975
124 | 2678564.84 | 1248763.4508 | 2678561.8863 | 1248766.8462 | 2678557.4405 | 1248772.9473
125 | 2678552.1595 | 1248781.9465 | 2678553.2069 | 1248780.1298 | 2678557.2488 | 1248775.4466 | 2678557.4405 | 1248772.9473 | 2678557.4405 | 1248772.9473
126 | 2678461.6356 | 1248941.5808 | 2678489.3978 | 1248927.2664
127 | 2678509.3229 | 1248916.9929 | 2678489.3978 | 1248927.2664
128 | 2678457.8323 | 1248943.5418 | 2678461.6356 | 1248941.5808
129 | 2678509.3229 | 1248916.9929 | 2678510.4701 | 1248919.3209
130 | 2678510.4701 | 1248919.3209 | 2678512.8787 | 1248924.3373
131 | 2678440.4208 | 1248901.5916 | 2678451.559 | 1248896.2313
132 | 2678440.4208 | 1248901.5916 | 2678429.7784 | 1248906.7134
133 | 2678540.2663 | 1248853.4593 | 2678533.8192 | 1248856.5716
134 | 2678540.2663 | 1248853.4593 | 2678558.2153 | 1248844.7945
135 | 2678403.6544 | 1248904.3422 | 2678401.189 | 1248898.8966
136 | 2678395.5504 | 1248886.4424 | 2678389.5002 | 1248873.0792
137 | 2678395.5504 | 1248886.4424 | 2678401.189 | 1248898.8966
138 | 2678387.8457 | 1248869.4248 | 2678389.5002 | 1248873.0792
139 | 2678387.8457 | 1248869.4248 | 2678387.3157 | 1248868.2542 | 2678386.8701 | 1248863.6894 | 2678389.5863 | 1248859.8781 | 2678396.033 | 1248856.8377
140 | 2678396.033 | 1248856.8377 | 2678414.3469 | 1248848.2006
141 | 2678416.6043 | 1248847.136 | 2678414.3469 | 1248848.2006
142 | 2678416.6043 | 1248847.136 | 2678431.5603 | 1248840.0825
143 | 2678434.966 | 1248838.4764 | 2678431.5603 | 1248840.0825
144 | 2678524.9024 | 1249072.4904 | 2678528.2801 | 1249071.4527
145 | 2678524.9024 | 1249072.4904 | 2678518.5386 | 1249074.6188 | 2678513.6049 | 1249076.2189
146 | 2678524.9024 | 1249072.4904 | 2678529.4179 | 1249084.4701 | 2678529.5082 | 1249084.7427
147 | 2678506.44 | 1249078.5426 | 2678513.6049 | 1249076.2189
148 | 2678506.44 | 1249078.5426 | 2678502.5519 | 1249079.8035
149 | 2678480.2626 | 1249087.0322 | 2678502.5519 | 1249079.8035
150 | 2678465.7419 | 1249003.0178 | 2678461.7923 | 1249004.447
151 | 2678439.0738 | 1249012.6676 | 2678461.7923 | 1249004.447
152 | 2678480.2626 | 1249087.0322 | 2678483.2376 | 1249093.3207 | 2678486.0719 | 1249098.2618 | 2678489.2529 | 1249101.8421

## bus_geodata
| x | y | coords
0 | 2678596.2404 | 1249061.9576
1 | 2678591.9293 | 1249056.4557
2 | 2678585.8627 | 1249048.7029
3 | 2678585.4096 | 1249061.2283
4 | 2678576.1555 | 1249036.3149
5 | 2678580.7607 | 1249055.329
6 | 2678591.9058 | 1249069.5193
7 | 2678553.8113 | 1249063.6087
8 | 2678569.0578 | 1249040.3732
9 | 2678424.538 | 1249005.7134
10 | 2678434.3492 | 1249002.1694
11 | 2678411.9804 | 1248977.7356
12 | 2678408.1371 | 1249011.5408
13 | 2678532.9482 | 1248978.2171
14 | 2678538.9683 | 1248975.8173
15 | 2678523.7168 | 1248981.8975
16 | 2678517.3757 | 1248974.3302
17 | 2678520.9914 | 1248982.9844
18 | 2678508.9373 | 1248975.2274
19 | 2678531.2909 | 1248991.6657
20 | 2678494.5603 | 1248992.5731
21 | 2678445.6592 | 1249099.8281
22 | 2678424.6608 | 1249073.6145
23 | 2678466.8314 | 1249091.4015
24 | 2678453.3006 | 1249115.702
25 | 2678341.1788 | 1248943.9663
26 | 2678351.8327 | 1248939.4081
27 | 2678345.0123 | 1248951.5892
28 | 2678321.4283 | 1248912.5468
29 | 2678367.8144 | 1249026.6342
30 | 2678362.6499 | 1249028.3005
31 | 2678377.2257 | 1249023.6119
32 | 2678358.4546 | 1249006.611
33 | 2678366.3245 | 1249061.0618
34 | 2678347.6269 | 1249031.4042
35 | 2678387.4246 | 1249020.2156
36 | 2678392.4464 | 1249029.5397
37 | 2678388.7245 | 1249019.7611
38 | 2678405.8072 | 1249024.7051
39 | 2678387.2944 | 1248926.9412
40 | 2678388.8992 | 1248930.0758
41 | 2678408.6303 | 1248916.8854
42 | 2678374.3831 | 1248928.3316
43 | 2678353.3018 | 1248978.5027
44 | 2678354.1116 | 1248946.3943
45 | 2678373.5162 | 1249070.2655
46 | 2678531.2897 | 1248968.8883
47 | 2678535.6393 | 1248967.178
48 | 2678524.6837 | 1248952.1557
49 | 2678573.4186 | 1248948.6246
50 | 2678601.1024 | 1248816.9469
51 | 2678598.5442 | 1248820.7936
52 | 2678581.2023 | 1248808.155
53 | 2678544.8583 | 1248973.2857
54 | 2678555.2058 | 1248968.8384
55 | 2678559.2918 | 1248967.0801
56 | 2678589.4574 | 1248941.6502
57 | 2678580.2973 | 1248912.4261
58 | 2678589.7396 | 1248829.5764
59 | 2678450.6558 | 1248744.6907
60 | 2678488.0101 | 1248742.7281
61 | 2678434.4482 | 1248748.6806
62 | 2678482.0493 | 1248870.6202
63 | 2678475.4409 | 1248864.0834
64 | 2678485.9087 | 1248879.7001
65 | 2678462.6315 | 1248790.4158
66 | 2678430.3502 | 1248807.1299
67 | 2678465.1964 | 1248811.2049
68 | 2678541.7508 | 1248794.3884
69 | 2678538.3513 | 1248799.3004
70 | 2678546.7877 | 1248791.542
71 | 2678485.79 | 1248763.814
72 | 2678474.7148 | 1248815.7331
73 | 2678493.2298 | 1248770.0306
74 | 2678514.3967 | 1248735.1883
75 | 2678302.1471 | 1248871.2422
76 | 2678313.0222 | 1248895.051
77 | 2678339.3527 | 1248854.1661
78 | 2678558.9688 | 1249014.3816
79 | 2678544.4853 | 1249066.474
80 | 2678555.9913 | 1249023.5215
81 | 2678468.7906 | 1248989.7288
82 | 2678409.9858 | 1248973.2915
83 | 2678541.05 | 1249004.2519
84 | 2678492.6733 | 1248993.2577
85 | 2678423.6427 | 1249072.0796
86 | 2678475.2663 | 1249088.6576
87 | 2678351.3938 | 1248992.0225
88 | 2678361.6314 | 1248995.7362
89 | 2678413.3044 | 1249056.7775
90 | 2678416.298 | 1249020.909
91 | 2678384.6039 | 1248932.0907
92 | 2678409.2097 | 1248916.6123
93 | 2678369.1436 | 1248930.8867
94 | 2678371.5169 | 1248938.2297
95 | 2678592.9023 | 1248904.2323
96 | 2678580.0286 | 1248911.8146
97 | 2678518.7314 | 1248937.4755
98 | 2678566.1775 | 1248800.998
99 | 2678567.6352 | 1248981.4032
100 | 2678569.7632 | 1248839.2199
101 | 2678470.5141 | 1248846.3943
102 | 2678517.2027 | 1248864.5931
103 | 2678498.9831 | 1248899.3363
104 | 2678472.9229 | 1248885.9497
105 | 2678468.3917 | 1248834.7907
106 | 2678525.7199 | 1248780.0434
107 | 2678518.5818 | 1248775.0453
108 | 2678530.2111 | 1248795.7557
109 | 2678550.9839 | 1248783.9857
110 | 2678511.843 | 1248783.958
111 | 2678522.7008 | 1248767.4529
112 | 2678344.0542 | 1248976.8579
113 | 2678353.495 | 1248847.6975
114 | 2678564.84 | 1248763.4508
115 | 2678557.4405 | 1248772.9473
116 | 2678577.6273 | 1248994.9434
117 | 2678489.3978 | 1248927.2664
118 | 2678461.6356 | 1248941.5808
119 | 2678509.3229 | 1248916.9929
120 | 2678457.8323 | 1248943.5418
121 | 2678510.4701 | 1248919.3209
122 | 2678512.8787 | 1248924.3373
123 | 2678451.559 | 1248896.2313
124 | 2678440.4208 | 1248901.5916
125 | 2678429.7784 | 1248906.7134
126 | 2678533.8192 | 1248856.5716
127 | 2678540.2663 | 1248853.4593
128 | 2678362.0794 | 1248844.0395
129 | 2678403.6544 | 1248904.3422
130 | 2678395.5504 | 1248886.4424
131 | 2678389.5002 | 1248873.0792
132 | 2678401.189 | 1248898.8966
133 | 2678387.8457 | 1248869.4248
134 | 2678396.033 | 1248856.8378
135 | 2678414.3469 | 1248848.2006
136 | 2678416.6043 | 1248847.136
137 | 2678431.5604 | 1248840.0825
138 | 2678552.1595 | 1248781.9465
139 | 2678558.2153 | 1248844.7945
140 | 2678434.966 | 1248838.4764
141 | 2678548.4435 | 1249013.7873
142 | 2678528.2801 | 1249071.4527
143 | 2678524.9024 | 1249072.4904
144 | 2678513.6049 | 1249076.2189
145 | 2678529.5082 | 1249084.7427
146 | 2678506.44 | 1249078.5426
147 | 2678502.5519 | 1249079.8035
148 | 2678407.1317 | 1248966.9326
149 | 2678465.7419 | 1249003.0178
150 | 2678461.7923 | 1249004.447
151 | 2678439.0738 | 1249012.6676
152 | 2678480.2626 | 1249087.0322
153 | 2678489.2529 | 1249101.8421
154 | 2678457.8323 | 1248943.5418

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98052 | -0.37402 | 0.0082496 | 0.0020675
1 | 0.98057 | -0.37297 | 0 | 0
2 | 0.98048 | -0.37472 | 0 | 0
3 | 0.9807 | -0.37032 | 0 | 0
4 | 0.98034 | -0.37753 | 0.0078692 | 0.0019722
5 | 0.98085 | -0.36739 | 0 | 0
6 | 0.98067 | -0.37099 | 0.0034811 | 0.00087244
7 | 0.97939 | -0.39601 | 0.0026429 | 0.00066237
8 | 0.98222 | -0.34077 | 0.001821 | 0.00045639
9 | 0.9743 | -0.49565 | 0 | 0
10 | 0.97402 | -0.50102 | 0.0019209 | 0.00048143
11 | 0.97398 | -0.50194 | 0.0018289 | 0.00045837
12 | 0.97493 | -0.48313 | 0.0058309 | 0.0014614
13 | 0.98902 | -0.20912 | 0 | 0
14 | 0.98936 | -0.20275 | 0 | 0
15 | 0.988 | -0.22874 | 0 | 0
16 | 0.98746 | -0.23935 | 0 | 0
17 | 0.98765 | -0.23552 | 0 | 0
18 | 0.98727 | -0.24303 | 0.022812 | 0.0057172
19 | 0.98695 | -0.24898 | 0.0037556 | 0.00094125
20 | 0.98486 | -0.2894 | 0.0023548 | 0.00059017
21 | 0.97553 | -0.47172 | 0 | 0
22 | 0.97524 | -0.47745 | 0.0035849 | 0.00089845
23 | 0.97581 | -0.46631 | 0.0019857 | 0.00049766
24 | 0.97547 | -0.473 | 0.0037815 | 0.00094773
25 | 0.98114 | -0.3628 | 0 | 0
26 | 0.98108 | -0.36404 | 0.0058443 | 0.0014647
27 | 0.98128 | -0.36005 | 0 | 0
28 | 0.98071 | -0.37117 | 0.0056456 | 0.0014149
29 | 0.97545 | -0.47302 | 0 | 0
30 | 0.97541 | -0.47365 | 0 | 0
31 | 0.97561 | -0.46973 | 0 | 0
32 | 0.97521 | -0.47776 | 0.00371 | 0.00092981
33 | 0.97524 | -0.47702 | 0 | 0
34 | 0.97538 | -0.47424 | 0.0020808 | 0.0005215
35 | 0.97579 | -0.46616 | 0.0039726 | 0.00099562
36 | 0.97648 | -0.45275 | 0 | 0
37 | 0.97582 | -0.4656 | 0 | 0
38 | 0.97737 | -0.43532 | 0.0026275 | 0.00065852
39 | 0.9828 | -0.33042 | 0 | 0
40 | 0.98267 | -0.33284 | 0 | 0
41 | 0.98379 | -0.31105 | 0.0026785 | 0.00067131
42 | 0.98268 | -0.33262 | 0.0016582 | 0.00041558
43 | 0.98105 | -0.36449 | 0.0041159 | 0.0010315
44 | 0.98154 | -0.35503 | 0.0043128 | 0.0010809
45 | 0.9752 | -0.47795 | 0.0043458 | 0.0010892
46 | 0.99017 | -0.18721 | 0 | 0
47 | 0.98988 | -0.19278 | 0 | 0
48 | 0.99128 | -0.16575 | 0.0058095 | 0.001456
49 | 0.98882 | -0.21321 | 0.0056713 | 0.0014214
50 | 0.98214 | -0.34298 | 0 | 0
51 | 0.98236 | -0.33854 | 0 | 0
52 | 0.98106 | -0.36393 | 0.0050998 | 0.0012781
53 | 0.98924 | -0.2051 | 0.0043175 | 0.0010821
54 | 0.98907 | -0.20836 | 0 | 0
55 | 0.989 | -0.20965 | 0 | 0
56 | 0.98848 | -0.21981 | 0 | 0
57 | 0.98784 | -0.23224 | 0.0059036 | 0.0014796
58 | 0.98299 | -0.32625 | 0.0032881 | 0.00082406
59 | 0.97772 | -0.42949 | 0 | 0
60 | 0.97789 | -0.42614 | 0 | 0
61 | 0.97765 | -0.4308 | 0.0043217 | 0.0010831
62 | 0.99039 | -0.18314 | 0 | 0
63 | 0.99016 | -0.18759 | 0.0052222 | 0.0013088
64 | 0.99057 | -0.17968 | 0 | 0
65 | 0.98946 | -0.20116 | 0 | 0
66 | 0.98931 | -0.204 | 0.0043503 | 0.0010903
67 | 0.98954 | -0.19954 | 0.005421 | 0.0013586
68 | 0.97929 | -0.39874 | 0 | 0
69 | 0.97915 | -0.40146 | 0.0027844 | 0.00069783
70 | 0.97947 | -0.39512 | 0 | 0
71 | 0.97816 | -0.42093 | 0 | 0
72 | 0.97799 | -0.42416 | 0.0030119 | 0.00075486
73 | 0.97826 | -0.4188 | 0.003638 | 0.00091177
74 | 0.97777 | -0.42861 | 0.0046924 | 0.001176
75 | 0.98049 | -0.37553 | 0 | 0
76 | 0.9806 | -0.3734 | 0.0018651 | 0.00046744
77 | 0.98032 | -0.37886 | 0.0015635 | 0.00039185
78 | 0.98029 | -0.37851 | 0.0019554 | 0.00049007
79 | 0.97891 | -0.40546 | 0.001909 | 0.00047844
80 | 0.98379 | -0.31026 | 0.0019326 | 0.00048435
81 | 0.97313 | -0.5186 | 0.026114 | 0.0065448
82 | 0.97394 | -0.50278 | 0.0041125 | 0.0010307
83 | 0.98566 | -0.27406 | 0.0038997 | 0.00097736
84 | 0.98466 | -0.29317 | 0.0060674 | 0.0015206
85 | 0.97523 | -0.47764 | 0.0029344 | 0.00073544
86 | 0.97593 | -0.46389 | 0.019541 | 0.0048975
87 | 0.97508 | -0.48014 | 0.0038751 | 0.00097119
88 | 0.98098 | -0.36595 | 0.0042211 | 0.0010579
89 | 0.97519 | -0.47852 | 0.0026092 | 0.00065392
90 | 0.97809 | -0.42112 | 0.0026539 | 0.00066512
91 | 0.9825 | -0.3361 | 0.0061678 | 0.0015458
92 | 0.98382 | -0.31049 | 0 | 0
93 | 0.98265 | -0.33323 | 0.0058435 | 0.0014645
94 | 0.98208 | -0.34444 | 0.0014143 | 0.00035446
95 | 0.9877 | -0.23495 | 0.0094585 | 0.0023705
96 | 0.98783 | -0.23243 | 0.0058184 | 0.0014582
97 | 0.99229 | -0.14647 | 0.0056799 | 0.0014235
98 | 0.98032 | -0.37844 | 0.0055566 | 0.0013926
99 | 0.98875 | -0.21454 | 0.0094318 | 0.0023638
100 | 0.98416 | -0.30366 | 0.0022883 | 0.00057349
101 | 0.98991 | -0.19234 | 0 | 0
102 | 0.98783 | -0.23243 | 0.0074243 | 0.0018607
103 | 0.99274 | -0.13791 | 0.015986 | 0.0040065
104 | 0.98931 | -0.20393 | 0.0030277 | 0.0007588
105 | 0.98976 | -0.19539 | 0.0047647 | 0.0011941
106 | 0.97937 | -0.39711 | 0 | 0
107 | 0.97933 | -0.39783 | 0 | 0
108 | 0.97897 | -0.40495 | 0.0028385 | 0.00071138
109 | 0.97936 | -0.39735 | 0.0021986 | 0.00055103
110 | 0.9786 | -0.41216 | 0.0024984 | 0.00062615
111 | 0.9793 | -0.39857 | 0.0045577 | 0.0011423
112 | 0.97502 | -0.48142 | 0.0041354 | 0.0010364
113 | 0.98028 | -0.37968 | 0.0022336 | 0.00055979
114 | 0.97919 | -0.40065 | 0.0046699 | 0.0011704
115 | 0.97924 | -0.39963 | 0.0043362 | 0.0010867
116 | 0.98864 | -0.21658 | 0.0068208 | 0.0017094
117 | 0.99635 | -0.069036 | 0.0051325 | 0.0012863
118 | 1 | 0 | -0.5201 | -0.13314
119 | 0.99376 | -0.11839 | 0 | 0
120 | 0.99998 | -0.00036063 | 0.0048352 | 0.0012118
121 | 0.99359 | -0.12165 | 0 | 0
122 | 0.99322 | -0.12864 | 0.0043659 | 0.0010942
123 | 0.98731 | -0.24268 | 0.0064552 | 0.0016178
124 | 0.98633 | -0.26151 | 0.0022563 | 0.00056549
125 | 0.98543 | -0.27906 | 0.0062936 | 0.0015773
126 | 0.9865 | -0.2581 | 0.0033777 | 0.00084653
127 | 0.98601 | -0.26765 | 0.011656 | 0.0029211
128 | 0.98027 | -0.3798 | 0.00068165 | 0.00017084
129 | 0.98346 | -0.31736 | 0.0032372 | 0.00081133
130 | 0.98311 | -0.32436 | 0.00075365 | 0.00018888
131 | 0.98288 | -0.32877 | 0.0022559 | 0.00056539
132 | 0.98333 | -0.32006 | 0.007655 | 0.0019185
133 | 0.98283 | -0.32982 | 0.00089496 | 0.0002243
134 | 0.98261 | -0.33413 | 0.0016265 | 0.00040764
135 | 0.98238 | -0.33848 | 0.0022575 | 0.00056578
136 | 0.98236 | -0.33892 | 0.0051261 | 0.0012847
137 | 0.98229 | -0.34027 | 0.0022563 | 0.00056549
138 | 0.97933 | -0.39787 | 0.0030175 | 0.00075625
139 | 0.98485 | -0.2901 | 0.0039514 | 0.00099031
140 | 0.98229 | -0.34042 | 0.0022575 | 0.00056579
141 | 0.98472 | -0.29225 | 0.0027083 | 0.00067876
142 | 0.9781 | -0.42132 | 0.0034345 | 0.00086077
143 | 0.97794 | -0.42441 | 0 | 0
144 | 0.97743 | -0.4344 | 0.0014258 | 0.00035735
145 | 0.97792 | -0.42486 | 0.0018764 | 0.00047027
146 | 0.97712 | -0.44054 | 0.002011 | 0.00050401
147 | 0.97696 | -0.44372 | 0.0032798 | 0.000822
148 | 0.9739 | -0.50345 | 0.0052299 | 0.0013107
149 | 0.98204 | -0.34403 | 0.0046442 | 0.0011639
150 | 0.98168 | -0.35116 | 0.0069601 | 0.0017444
151 | 0.97972 | -0.3892 | 0.014449 | 0.0036213
152 | 0.9761 | -0.46058 | 0 | 0
153 | 0.97602 | -0.46215 | 0.0049183 | 0.0012326
154 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0082496 | -0.0020675 | 0.00825 | 0.0020677 | 4.1083e-07 | 1.7476e-07 | 0.012519 | 0.012519 | 0.012519 | 0.98052 | -0.37402 | 0.98057 | -0.37297 | 3.4394
1 | 0.0098268 | 0.002463 | -0.009826 | -0.0024626 | 8.1999e-07 | 4.0076e-07 | 0.014912 | 0.014912 | 0.014912 | 0.98057 | -0.37297 | 0.98048 | -0.37472 | 4.0968
2 | -0.018077 | -0.0045307 | 0.018079 | 0.0045321 | 2.28e-06 | 1.3573e-06 | 0.027432 | 0.027432 | 0.027432 | 0.98057 | -0.37297 | 0.9807 | -0.37032 | 7.5362
3 | 0.009826 | 0.0024626 | -0.0098247 | -0.002462 | 1.3124e-06 | 6.415e-07 | 0.014912 | 0.014912 | 0.014912 | 0.98048 | -0.37472 | 0.98034 | -0.37753 | 4.0968
4 | -0.02156 | -0.0054045 | 0.021563 | 0.0054063 | 3.0111e-06 | 1.8324e-06 | 0.032714 | 0.032714 | 0.032714 | 0.9807 | -0.37032 | 0.98085 | -0.36739 | 8.9872
5 | 0.0034812 | 0.00087237 | -0.0034811 | -0.00087244 | 1.102e-07 | -6.2372e-08 | 0.0052819 | 0.005282 | 0.005282 | 0.9807 | -0.37032 | 0.98067 | -0.37099 | 1.4511
6 | 0.0019555 | 0.00048978 | -0.0019554 | -0.00049007 | 9.2056e-08 | -2.924e-07 | 0.0029681 | 0.0029682 | 0.0029682 | 0.98034 | -0.37753 | 0.98029 | -0.37851 | 0.81544
7 | 0.056169 | 0.014165 | -0.056092 | -0.014116 | 7.6822e-05 | 4.8811e-05 | 0.085243 | 0.085243 | 0.085243 | 0.98085 | -0.36739 | 0.97939 | -0.39601 | 23.4184
8 | -0.077732 | -0.019572 | 0.077831 | 0.019635 | 9.9086e-05 | 6.3175e-05 | 0.11796 | 0.11796 | 0.11796 | 0.98085 | -0.36739 | 0.98222 | -0.34077 | 32.4056
9 | 0.053449 | 0.013454 | -0.053425 | -0.013439 | 2.4139e-05 | 1.5326e-05 | 0.081228 | 0.081228 | 0.081228 | 0.97939 | -0.39601 | 0.97891 | -0.40546 | 22.3153
10 | -0.079652 | -0.020091 | 0.079769 | 0.020165 | 0.00011653 | 7.4306e-05 | 0.12072 | 0.12071 | 0.12072 | 0.98222 | -0.34077 | 0.98379 | -0.31026 | 33.1635
11 | 0.028064 | 0.0070442 | -0.028057 | -0.0070398 | 7.1877e-06 | 4.4703e-06 | 0.042865 | 0.042865 | 0.042865 | 0.9743 | -0.49565 | 0.97402 | -0.50102 | 11.7762
12 | 0.011175 | 0.0028017 | -0.011172 | -0.0028 | 3.3501e-06 | 1.7623e-06 | 0.017068 | 0.017068 | 0.017068 | 0.9743 | -0.49565 | 0.97398 | -0.50194 | 4.689
13 | -0.039239 | -0.009846 | 0.039263 | 0.0098608 | 2.3445e-05 | 1.4788e-05 | 0.059933 | 0.059933 | 0.059933 | 0.9743 | -0.49565 | 0.97493 | -0.48313 | 16.4651
14 | 0.026136 | 0.0065583 | -0.026114 | -0.0065448 | 2.1896e-05 | 1.3558e-05 | 0.039931 | 0.039931 | 0.039931 | 0.97402 | -0.50102 | 0.97313 | -0.5186 | 10.97
15 | 0.0093429 | 0.0023416 | -0.0093425 | -0.0023414 | 3.7217e-07 | 1.7757e-07 | 0.014274 | 0.014274 | 0.014274 | 0.97398 | -0.50194 | 0.97394 | -0.50278 | 3.9214
16 | -0.045093 | -0.011322 | 0.045131 | 0.011346 | 3.7738e-05 | 2.3887e-05 | 0.068833 | 0.068832 | 0.068833 | 0.97493 | -0.48313 | 0.97582 | -0.4656 | 18.91
17 | -0.22349 | -0.056839 | 0.22356 | 0.056883 | 6.8635e-05 | 4.3594e-05 | 0.33654 | 0.33654 | 0.33654 | 0.98902 | -0.20912 | 0.98936 | -0.20275 | 23.1139
18 | 0.22349 | 0.056839 | -0.22328 | -0.056704 | 0.00021104 | 0.00013481 | 0.33654 | 0.33654 | 0.33654 | 0.98902 | -0.20912 | 0.988 | -0.22874 | 46.2279
19 | 0.02058 | 0.0051612 | -0.020578 | -0.0051598 | 2.3036e-06 | 1.392e-06 | 0.030954 | 0.030955 | 0.030955 | 0.98936 | -0.20275 | 0.98924 | -0.2051 | 8.504
20 | -0.24414 | -0.062044 | 0.24425 | 0.062118 | 0.00011722 | 7.4547e-05 | 0.36749 | 0.36749 | 0.36749 | 0.98936 | -0.20275 | 0.98988 | -0.19278 | 25.2399
21 | 0.13087 | 0.033239 | -0.13083 | -0.033212 | 4.271e-05 | 2.7297e-05 | 0.19726 | 0.19726 | 0.19726 | 0.988 | -0.22874 | 0.98765 | -0.23552 | 54.192
22 | 0.092406 | 0.023465 | -0.092316 | -0.023407 | 8.9919e-05 | 5.739e-05 | 0.13928 | 0.13928 | 0.13928 | 0.988 | -0.22874 | 0.98695 | -0.24898 | 38.2637
23 | -0.022816 | -0.0057196 | 0.02282 | 0.0057222 | 4.1578e-06 | 2.541e-06 | 0.034382 | 0.034382 | 0.034382 | 0.98746 | -0.23935 | 0.98765 | -0.23552 | 9.4456
24 | 0.022816 | 0.0057196 | -0.022812 | -0.0057172 | 3.9978e-06 | 2.4432e-06 | 0.034382 | 0.034382 | 0.034382 | 0.98746 | -0.23935 | 0.98727 | -0.24303 | 9.4457
25 | 0.10801 | 0.02749 | -0.10773 | -0.027311 | 0.00027971 | 0.00017866 | 0.16288 | 0.16288 | 0.16288 | 0.98765 | -0.23552 | 0.98486 | -0.2894 | 44.7465
26 | 0.08856 | 0.022466 | -0.088454 | -0.022398 | 0.00010663 | 6.8039e-05 | 0.13362 | 0.13362 | 0.13362 | 0.98695 | -0.24898 | 0.98566 | -0.27406 | 36.7081
27 | 0.10537 | 0.026721 | -0.10535 | -0.026709 | 1.9107e-05 | 1.2203e-05 | 0.15932 | 0.15932 | 0.15932 | 0.98486 | -0.2894 | 0.98466 | -0.29317 | 43.7691
28 | 0.0091311 | 0.0022888 | -0.0091286 | -0.0022877 | 2.493e-06 | 1.1678e-06 | 0.013928 | 0.013928 | 0.013928 | 0.97553 | -0.47172 | 0.97524 | -0.47745 | 3.8265
29 | -0.012913 | -0.0032365 | 0.012916 | 0.0032383 | 3.331e-06 | 1.8459e-06 | 0.019697 | 0.019696 | 0.019697 | 0.97553 | -0.47172 | 0.97581 | -0.46631 | 5.4111
30 | 0.0037817 | 0.00094765 | -0.0037815 | -0.00094773 | 2.3074e-07 | -8.3185e-08 | 0.0057684 | 0.0057684 | 0.0057684 | 0.97553 | -0.47172 | 0.97547 | -0.473 | 1.5847
31 | 0.0055438 | 0.0013892 | -0.0055437 | -0.0013892 | 4.9419e-08 | 8.6455e-09 | 0.0084586 | 0.0084586 | 0.0084586 | 0.97524 | -0.47745 | 0.97523 | -0.47764 | 2.3238
32 | -0.014902 | -0.003736 | 0.014904 | 0.003737 | 1.7177e-06 | 9.8848e-07 | 0.022724 | 0.022724 | 0.022724 | 0.97581 | -0.46631 | 0.97593 | -0.46389 | 6.243
33 | 0.0058446 | 0.0014648 | -0.0058443 | -0.0014647 | 3.4431e-07 | 7.2791e-08 | 0.0088641 | 0.0088642 | 0.0088642 | 0.98114 | -0.3628 | 0.98108 | -0.36404 | 2.4352
34 | -0.017841 | -0.004472 | 0.017843 | 0.0044734 | 2.3426e-06 | 1.3915e-06 | 0.027058 | 0.027058 | 0.027058 | 0.98114 | -0.3628 | 0.98128 | -0.36005 | 7.4335
35 | 0.011996 | 0.0030072 | -0.011991 | -0.0030047 | 4.7795e-06 | 2.5728e-06 | 0.018194 | 0.018194 | 0.018194 | 0.98114 | -0.3628 | 0.98071 | -0.37117 | 4.9984
36 | 0.008339 | 0.0020901 | -0.0083373 | -0.0020894 | 1.764e-06 | 7.5741e-07 | 0.012645 | 0.012646 | 0.012646 | 0.98128 | -0.36005 | 0.98105 | -0.36449 | 3.474
37 | -0.026182 | -0.0065636 | 0.026188 | 0.0065674 | 6.2538e-06 | 3.8688e-06 | 0.039703 | 0.039703 | 0.039703 | 0.98128 | -0.36005 | 0.98154 | -0.35503 | 10.9075
38 | 0.0063458 | 0.0015898 | -0.0063451 | -0.0015896 | 6.7476e-07 | 1.8695e-07 | 0.0096281 | 0.0096282 | 0.0096282 | 0.98071 | -0.37117 | 0.9806 | -0.3734 | 2.6451
39 | 0.0064278 | 0.0016105 | -0.0064276 | -0.0016104 | 1.9512e-07 | 5.7322e-08 | 0.0098052 | 0.0098052 | 0.0098052 | 0.97545 | -0.47302 | 0.97541 | -0.47365 | 2.6937
40 | -0.018152 | -0.0045496 | 0.018155 | 0.0045513 | 2.8422e-06 | 1.6956e-06 | 0.027691 | 0.02769 | 0.027691 | 0.97545 | -0.47302 | 0.97561 | -0.46973 | 7.6073
41 | 0.011724 | 0.0029392 | -0.011722 | -0.0029378 | 2.6518e-06 | 1.4212e-06 | 0.017885 | 0.017885 | 0.017885 | 0.97545 | -0.47302 | 0.97521 | -0.47776 | 4.9136
42 | 0.0043467 | 0.0010891 | -0.004346 | -0.0010891 | 6.9721e-07 | -8.1486e-08 | 0.0066309 | 0.0066311 | 0.0066311 | 0.97541 | -0.47365 | 0.97524 | -0.47702 | 1.8217
43 | 0.0020809 | 0.00052134 | -0.0020808 | -0.0005215 | 5.8231e-08 | -1.5508e-07 | 0.0031743 | 0.0031744 | 0.0031744 | 0.97541 | -0.47365 | 0.97538 | -0.47424 | 0.87209
44 | -0.018155 | -0.0045513 | 0.018158 | 0.0045532 | 3.0911e-06 | 1.844e-06 | 0.02769 | 0.02769 | 0.02769 | 0.97561 | -0.46973 | 0.97579 | -0.46616 | 7.6073
45 | 0.0080116 | 0.0020079 | -0.0080107 | -0.0020076 | 9.0827e-07 | 3.791e-07 | 0.012225 | 0.012225 | 0.012225 | 0.97521 | -0.47776 | 0.97508 | -0.48014 | 3.3584
46 | 0.004346 | 0.0010891 | -0.0043458 | -0.0010892 | 1.926e-07 | -2.2472e-08 | 0.0066311 | 0.0066311 | 0.0066311 | 0.97524 | -0.47702 | 0.9752 | -0.47795 | 1.8217
47 | -0.022131 | -0.0055488 | 0.022131 | 0.0055492 | 5.8817e-07 | 3.5923e-07 | 0.033748 | 0.033748 | 0.033748 | 0.97579 | -0.46616 | 0.97582 | -0.4656 | 9.2715
48 | 0.067304 | 0.016921 | -0.067262 | -0.016895 | 4.1287e-05 | 2.6293e-05 | 0.10258 | 0.10258 | 0.10258 | 0.97648 | -0.45275 | 0.97582 | -0.4656 | 28.1815
49 | -0.067304 | -0.016921 | 0.06736 | 0.016957 | 5.6068e-05 | 3.5706e-05 | 0.10258 | 0.10258 | 0.10258 | 0.97648 | -0.45275 | 0.97737 | -0.43532 | 28.1815
50 | -0.069987 | -0.017616 | 0.070035 | 0.017646 | 4.7525e-05 | 3.0276e-05 | 0.10658 | 0.10658 | 0.10658 | 0.97737 | -0.43532 | 0.97809 | -0.42112 | 29.2805
51 | 0.038122 | 0.0095727 | -0.038117 | -0.0095699 | 4.3986e-06 | 2.7705e-06 | 0.057726 | 0.057726 | 0.057726 | 0.9828 | -0.33042 | 0.98267 | -0.33284 | 15.8587
52 | -0.045624 | -0.011453 | 0.045667 | 0.01148 | 4.2215e-05 | 2.6719e-05 | 0.069085 | 0.069085 | 0.069085 | 0.9828 | -0.33042 | 0.98379 | -0.31105 | 18.9794
53 | 0.0075026 | 0.0018804 | -0.0075018 | -0.0018801 | 7.8314e-07 | 2.9615e-07 | 0.011359 | 0.01136 | 0.01136 | 0.9828 | -0.33042 | 0.98268 | -0.33262 | 3.1208
54 | 0.038117 | 0.0095699 | -0.038111 | -0.0095662 | 5.9285e-06 | 3.7342e-06 | 0.057726 | 0.057726 | 0.057726 | 0.98267 | -0.33284 | 0.9825 | -0.3361 | 15.8587
55 | -0.048345 | -0.012151 | 0.048346 | 0.012152 | 1.2847e-06 | 8.1407e-07 | 0.073136 | 0.073136 | 0.073136 | 0.98379 | -0.31105 | 0.98382 | -0.31049 | 20.0924
56 | 0.0058436 | 0.0014645 | -0.0058435 | -0.0014645 | 1.7116e-07 | 3.5694e-08 | 0.0088486 | 0.0088487 | 0.0088487 | 0.98268 | -0.33262 | 0.98265 | -0.33323 | 2.431
57 | 0.0042214 | 0.0010579 | -0.0042211 | -0.0010579 | 2.9427e-07 | -5.3342e-08 | 0.0064028 | 0.0064029 | 0.0064029 | 0.98105 | -0.36449 | 0.98098 | -0.36595 | 1.759
58 | -0.030501 | -0.0076483 | 0.030517 | 0.007658 | 1.5416e-05 | 9.6229e-06 | 0.046241 | 0.046241 | 0.046241 | 0.98154 | -0.35503 | 0.98208 | -0.34444 | 12.7037
59 | 0.27122 | 0.068923 | -0.27115 | -0.068876 | 7.2731e-05 | 4.6308e-05 | 0.40793 | 0.40793 | 0.40793 | 0.99017 | -0.18721 | 0.98988 | -0.19278 | 28.0174
60 | -0.27122 | -0.068923 | 0.27151 | 0.069101 | 0.00028065 | 0.00017869 | 0.40793 | 0.40793 | 0.40793 | 0.99017 | -0.18721 | 0.99128 | -0.16575 | 28.0174
61 | 0.026899 | 0.0067582 | -0.026872 | -0.006742 | 2.6192e-05 | 1.6215e-05 | 0.040441 | 0.040441 | 0.040441 | 0.98988 | -0.19278 | 0.98882 | -0.21321 | 11.1102
62 | -0.27731 | -0.070557 | 0.27757 | 0.070722 | 0.00025787 | 0.00016422 | 0.41665 | 0.41665 | 0.41665 | 0.99128 | -0.16575 | 0.99229 | -0.14647 | 28.6163
63 | 0.021201 | 0.0053206 | -0.021194 | -0.0053166 | 6.6769e-06 | 4.0489e-06 | 0.031907 | 0.031907 | 0.031907 | 0.98882 | -0.21321 | 0.98848 | -0.21981 | 8.7656
64 | -0.053373 | -0.013431 | 0.053384 | 0.013438 | 1.1325e-05 | 7.1893e-06 | 0.080884 | 0.080884 | 0.080884 | 0.98214 | -0.34298 | 0.98236 | -0.33854 | 22.2209
65 | 0.053373 | 0.013431 | -0.05332 | -0.013397 | 5.3374e-05 | 3.3884e-05 | 0.080884 | 0.080884 | 0.080884 | 0.98214 | -0.34298 | 0.98106 | -0.36393 | 22.2209
66 | -0.053384 | -0.013438 | 0.053416 | 0.013458 | 3.1374e-05 | 1.9917e-05 | 0.080884 | 0.080884 | 0.080884 | 0.98236 | -0.33854 | 0.98299 | -0.32625 | 22.2209
67 | 0.04822 | 0.012119 | -0.048187 | -0.012097 | 3.3398e-05 | 2.1165e-05 | 0.073149 | 0.073149 | 0.073149 | 0.98106 | -0.36393 | 0.98032 | -0.37844 | 20.0959
68 | 0.016261 | 0.0040777 | -0.016258 | -0.0040763 | 2.5269e-06 | 1.4727e-06 | 0.02446 | 0.02446 | 0.02446 | 0.98924 | -0.2051 | 0.98907 | -0.20836 | 6.7198
69 | 0.016258 | 0.0040763 | -0.016257 | -0.0040757 | 9.9549e-07 | 5.8018e-07 | 0.02446 | 0.02446 | 0.02446 | 0.98907 | -0.20836 | 0.989 | -0.20965 | 6.7198
70 | 0.016257 | 0.0040757 | -0.016253 | -0.0040735 | 3.7883e-06 | 2.2079e-06 | 0.02446 | 0.02446 | 0.02446 | 0.989 | -0.20965 | 0.98875 | -0.21454 | 6.7198
71 | 0.021194 | 0.0053166 | -0.021182 | -0.005309 | 1.2553e-05 | 7.6124e-06 | 0.031907 | 0.031907 | 0.031907 | 0.98848 | -0.21981 | 0.98784 | -0.23224 | 8.7656
72 | 0.015278 | 0.0038294 | -0.015278 | -0.0038293 | 1.3267e-07 | 7.6357e-08 | 0.023014 | 0.023014 | 0.023014 | 0.98784 | -0.23224 | 0.98783 | -0.23243 | 6.3226
73 | -0.056704 | -0.014282 | 0.056765 | 0.014321 | 6.1324e-05 | 3.8966e-05 | 0.085861 | 0.085861 | 0.085861 | 0.98299 | -0.32625 | 0.98416 | -0.30366 | 23.5882
74 | -0.004322 | -0.0010831 | 0.0043226 | 0.001083 | 6.891e-07 | -9.1744e-08 | 0.0065777 | 0.0065775 | 0.0065777 | 0.97772 | -0.42949 | 0.97789 | -0.42614 | 1.807
75 | 0.004322 | 0.0010831 | -0.0043217 | -0.0010831 | 2.7082e-07 | -3.5996e-08 | 0.0065777 | 0.0065777 | 0.0065777 | 0.97772 | -0.42949 | 0.97765 | -0.4308 | 1.8071
76 | 0.0046929 | 0.001176 | -0.0046924 | -0.001176 | 5.5198e-07 | -8.8136e-09 | 0.007141 | 0.0071411 | 0.0071411 | 0.97789 | -0.42614 | 0.97777 | -0.42861 | 1.9618
77 | -0.0090156 | -0.002259 | 0.0090178 | 0.00226 | 2.2393e-06 | 1.035e-06 | 0.013718 | 0.013718 | 0.013718 | 0.97789 | -0.42614 | 0.97816 | -0.42093 | 3.7688
78 | 0.019771 | 0.0049582 | -0.019766 | -0.0049557 | 4.1979e-06 | 2.5234e-06 | 0.029706 | 0.029706 | 0.029706 | 0.99039 | -0.18314 | 0.99016 | -0.18759 | 8.1609
79 | -0.019771 | -0.0049582 | 0.019774 | 0.0049602 | 3.2634e-06 | 1.9617e-06 | 0.029706 | 0.029706 | 0.029706 | 0.99039 | -0.18314 | 0.99057 | -0.17968 | 8.1609
80 | 0.014544 | 0.0036469 | -0.014541 | -0.003645 | 3.2917e-06 | 1.8704e-06 | 0.021858 | 0.021858 | 0.021858 | 0.99016 | -0.18759 | 0.98991 | -0.19234 | 6.0049
81 | 0.085917 | 0.021802 | -0.085699 | -0.021664 | 0.00021738 | 0.00013868 | 0.12916 | 0.12916 | 0.12916 | 0.99057 | -0.17968 | 0.98783 | -0.23243 | 35.4832
82 | -0.20096 | -0.050894 | 0.20136 | 0.051152 | 0.0004039 | 0.00025789 | 0.30207 | 0.30207 | 0.30207 | 0.99057 | -0.17968 | 0.99274 | -0.13791 | 41.4928
83 | 0.09527 | 0.024131 | -0.095159 | -0.024061 | 0.00011083 | 7.0744e-05 | 0.1432 | 0.1432 | 0.1432 | 0.99057 | -0.17968 | 0.98931 | -0.20393 | 39.3417
84 | 0.0043509 | 0.0010902 | -0.0043503 | -0.0010903 | 5.8838e-07 | -9.409e-08 | 0.006543 | 0.0065432 | 0.0065432 | 0.98946 | -0.20116 | 0.98931 | -0.204 | 1.7976
85 | -0.0043509 | -0.0010902 | 0.0043512 | 0.0010901 | 3.3628e-07 | -5.3849e-08 | 0.006543 | 0.0065429 | 0.006543 | 0.98946 | -0.20116 | 0.98954 | -0.19954 | 1.7975
86 | -0.0097722 | -0.0024488 | 0.0097741 | 0.0024497 | 1.928e-06 | 9.2798e-07 | 0.014695 | 0.014695 | 0.014695 | 0.98954 | -0.19954 | 0.98976 | -0.19539 | 4.037
87 | 0.023808 | 0.0059729 | -0.023805 | -0.005971 | 3.0832e-06 | 1.8942e-06 | 0.036179 | 0.036179 | 0.036179 | 0.97929 | -0.39874 | 0.97915 | -0.40146 | 9.9392
88 | -0.023808 | -0.0059729 | 0.023813 | 0.0059754 | 4.1118e-06 | 2.5261e-06 | 0.036179 | 0.036179 | 0.036179 | 0.97929 | -0.39874 | 0.97947 | -0.39512 | 9.9392
89 | 0.021021 | 0.0052732 | -0.021017 | -0.005271 | 3.4968e-06 | 2.123e-06 | 0.031947 | 0.031947 | 0.031947 | 0.97915 | -0.40146 | 0.97897 | -0.40495 | 8.7768
90 | 0.014225 | 0.0035658 | -0.014223 | -0.0035649 | 1.5139e-06 | 8.6012e-07 | 0.021611 | 0.021611 | 0.021611 | 0.97947 | -0.39512 | 0.97936 | -0.39735 | 5.9371
91 | -0.042596 | -0.010683 | 0.04263 | 0.010705 | 3.388e-05 | 2.1411e-05 | 0.064715 | 0.064715 | 0.064715 | 0.97947 | -0.39512 | 0.98032 | -0.37844 | 17.7788
92 | 0.0045585 | 0.0011422 | -0.0045581 | -0.0011423 | 4.3166e-07 | -2.5795e-08 | 0.0069252 | 0.0069253 | 0.0069253 | 0.97947 | -0.39512 | 0.97937 | -0.39711 | 1.9026
93 | 0.0030124 | 0.00075442 | -0.0030119 | -0.00075486 | 4.638e-07 | -4.4234e-07 | 0.0045824 | 0.0045827 | 0.0045827 | 0.97816 | -0.42093 | 0.97799 | -0.42416 | 1.259
94 | -0.01203 | -0.0030145 | 0.012031 | 0.0030151 | 1.2176e-06 | 6.5758e-07 | 0.018301 | 0.018301 | 0.018301 | 0.97816 | -0.42093 | 0.97826 | -0.4188 | 5.0277
95 | -0.015669 | -0.0039269 | 0.015674 | 0.0039298 | 4.9576e-06 | 2.8806e-06 | 0.023834 | 0.023834 | 0.023834 | 0.97826 | -0.4188 | 0.9786 | -0.41216 | 6.5479
96 | -0.0044795 | -0.0011222 | 0.00448 | 0.0011221 | 4.55e-07 | -3.9979e-08 | 0.0067981 | 0.0067979 | 0.0067981 | 0.98049 | -0.37553 | 0.9806 | -0.3734 | 1.8676
97 | 0.0044795 | 0.0011222 | -0.0044788 | -0.0011222 | 7.0952e-07 | -6.2173e-08 | 0.0067981 | 0.0067982 | 0.0067982 | 0.98049 | -0.37553 | 0.98032 | -0.37886 | 1.8676
98 | 0.0029153 | 0.00073038 | -0.0029152 | -0.00073051 | 1.142e-07 | -1.2298e-07 | 0.0044251 | 0.0044251 | 0.0044251 | 0.98032 | -0.37886 | 0.98028 | -0.37968 | 1.2157
99 | 0.051516 | 0.01296 | -0.051477 | -0.012936 | 3.9002e-05 | 2.4748e-05 | 0.078326 | 0.078326 | 0.078326 | 0.97891 | -0.40546 | 0.9781 | -0.42132 | 21.5181
100 | -0.081701 | -0.02065 | 0.081772 | 0.020695 | 7.0609e-05 | 4.5033e-05 | 0.12364 | 0.12364 | 0.12364 | 0.98379 | -0.31026 | 0.98472 | -0.29225 | 33.9665
101 | 0.0052301 | 0.0013108 | -0.0052299 | -0.0013107 | 1.6689e-07 | 2.0077e-08 | 0.0079907 | 0.0079907 | 0.0079907 | 0.97394 | -0.50278 | 0.9739 | -0.50345 | 2.1952
102 | 0.084554 | 0.021421 | -0.08448 | -0.021374 | 7.3822e-05 | 4.7092e-05 | 0.12773 | 0.12773 | 0.12773 | 0.98566 | -0.27406 | 0.98472 | -0.29225 | 35.0908
103 | 0.099287 | 0.025188 | -0.099045 | -0.025034 | 0.00024218 | 0.00015463 | 0.15015 | 0.15015 | 0.15015 | 0.98466 | -0.29317 | 0.98204 | -0.34403 | 41.2501
104 | 0.0026093 | 0.00065376 | -0.0026092 | -0.00065392 | 1.0978e-07 | -1.6018e-07 | 0.0039812 | 0.0039813 | 0.0039813 | 0.97523 | -0.47764 | 0.97519 | -0.47852 | 1.0938
105 | -0.034445 | -0.0086345 | 0.03445 | 0.0086379 | 5.4345e-06 | 3.4124e-06 | 0.052519 | 0.052519 | 0.052519 | 0.97593 | -0.46389 | 0.9761 | -0.46058 | 14.4283
106 | 0.0041356 | 0.0010364 | -0.0041354 | -0.0010364 | 2.5164e-07 | -4.9088e-08 | 0.0063111 | 0.0063111 | 0.0063111 | 0.97508 | -0.48014 | 0.97502 | -0.48142 | 1.7338
107 | -0.072689 | -0.018311 | 0.0728 | 0.018382 | 0.00011114 | 7.0826e-05 | 0.11062 | 0.11062 | 0.11062 | 0.97809 | -0.42112 | 0.97972 | -0.3892 | 30.3897
108 | 0.031944 | 0.0080204 | -0.031931 | -0.0080124 | 1.269e-05 | 7.9388e-06 | 0.048384 | 0.048384 | 0.048384 | 0.9825 | -0.3361 | 0.98208 | -0.34444 | 13.2924
109 | 0.028347 | 0.0071131 | -0.028338 | -0.0071073 | 9.286e-06 | 5.7721e-06 | 0.042878 | 0.042878 | 0.042878 | 0.98382 | -0.31049 | 0.98346 | -0.31736 | 11.7796
110 | -0.076693 | -0.019265 | 0.076808 | 0.019338 | 0.00011521 | 7.3445e-05 | 0.11601 | 0.11601 | 0.11601 | 0.98382 | -0.31049 | 0.98543 | -0.27906 | 31.8719
111 | -0.0094585 | -0.0023705 | 0.0094597 | 0.0023711 | 1.1376e-06 | 5.3685e-07 | 0.01425 | 0.01425 | 0.01425 | 0.9877 | -0.23495 | 0.98783 | -0.23243 | 3.9147
112 | -0.28325 | -0.072145 | 0.2835 | 0.072301 | 0.00024388 | 0.00015534 | 0.42517 | 0.42517 | 0.42517 | 0.99229 | -0.14647 | 0.99322 | -0.12864 | 29.2013
113 | 0.0068214 | 0.0017097 | -0.0068208 | -0.0017094 | 6.6506e-07 | 2.0983e-07 | 0.010266 | 0.010266 | 0.010266 | 0.98875 | -0.21454 | 0.98864 | -0.21658 | 2.8203
114 | -0.059053 | -0.014894 | 0.059092 | 0.014919 | 3.8364e-05 | 2.439e-05 | 0.089321 | 0.089321 | 0.089321 | 0.98416 | -0.30366 | 0.98485 | -0.2901 | 24.5387
115 | 0.014541 | 0.003645 | -0.014539 | -0.0036438 | 2.1134e-06 | 1.201e-06 | 0.021858 | 0.021858 | 0.021858 | 0.98991 | -0.19234 | 0.98976 | -0.19539 | 6.0049
116 | 0.078275 | 0.019803 | -0.078179 | -0.019742 | 9.6304e-05 | 6.1398e-05 | 0.11798 | 0.11798 | 0.11798 | 0.98783 | -0.23243 | 0.9865 | -0.2581 | 32.4108
117 | -0.21735 | -0.055158 | 0.21755 | 0.055288 | 0.00020435 | 0.00012972 | 0.32603 | 0.32603 | 0.32603 | 0.99274 | -0.13791 | 0.99376 | -0.11839 | 22.3921
118 | 0.092131 | 0.023302 | -0.091961 | -0.023193 | 0.00017092 | 0.00010908 | 0.13865 | 0.13865 | 0.13865 | 0.98931 | -0.20393 | 0.98731 | -0.24268 | 38.0907
119 | 0.0045581 | 0.0011423 | -0.0045579 | -0.0011423 | 1.5642e-07 | -9.3292e-09 | 0.0069253 | 0.0069253 | 0.0069253 | 0.97937 | -0.39711 | 0.97933 | -0.39783 | 1.9026
120 | 0.0045579 | 0.0011423 | -0.0045577 | -0.0011423 | 1.6195e-07 | -9.6493e-09 | 0.0069253 | 0.0069254 | 0.0069254 | 0.97933 | -0.39783 | 0.9793 | -0.39857 | 1.9026
121 | 0.018179 | 0.0045596 | -0.018173 | -0.0045559 | 6.2526e-06 | 3.7272e-06 | 0.027633 | 0.027633 | 0.027633 | 0.97897 | -0.40495 | 0.9786 | -0.41216 | 7.5915
122 | 0.012025 | 0.0030139 | -0.012025 | -0.0030137 | 2.9465e-07 | 1.5896e-07 | 0.01827 | 0.01827 | 0.01827 | 0.97936 | -0.39735 | 0.97933 | -0.39787 | 5.0193
123 | 0.00068165 | 0.00017072 | -0.00068165 | -0.00017084 | 3.7463e-09 | -1.1524e-07 | 0.0010347 | 0.0010347 | 0.0010347 | 0.98028 | -0.37968 | 0.98027 | -0.3798 | 0.28426
124 | -0.0046699 | -0.0011704 | 0.0046702 | 0.0011704 | 2.2756e-07 | -5.9382e-09 | 0.0070966 | 0.0070966 | 0.0070966 | 0.97919 | -0.40065 | 0.97924 | -0.39963 | 1.9496
125 | -0.0090063 | -0.0022571 | 0.0090071 | 0.0022575 | 7.5784e-07 | 3.4926e-07 | 0.013686 | 0.013686 | 0.013686 | 0.97924 | -0.39963 | 0.97933 | -0.39787 | 3.7598
126 | -0.5119 | -0.13083 | 0.51361 | 0.13193 | 0.0017155 | 0.0010963 | 0.7654 | 0.7654 | 0.7654 | 0.99635 | -0.069036 | 1 | 0 | 52.569
127 | 0.50677 | 0.12954 | -0.50556 | -0.12877 | 0.0012067 | 0.00077113 | 0.75774 | 0.75774 | 0.75774 | 0.99635 | -0.069036 | 0.99376 | -0.11839 | 52.0426
128 | 0.0048353 | 0.0012118 | -0.0048352 | -0.0012118 | 8.307e-08 | -2.9721e-09 | 0.007195 | 0.007195 | 0.007195 | 1 | 0 | 0.99998 | -0.00036063 | 1.9767
129 | 0.28801 | 0.073486 | -0.28796 | -0.073457 | 4.5324e-05 | 2.8873e-05 | 0.43171 | 0.43171 | 0.43171 | 0.99376 | -0.11839 | 0.99359 | -0.12165 | 29.6505
130 | 0.28796 | 0.073457 | -0.28786 | -0.073395 | 9.7231e-05 | 6.194e-05 | 0.43171 | 0.43171 | 0.43171 | 0.99359 | -0.12165 | 0.99322 | -0.12864 | 29.6505
131 | 0.085505 | 0.021575 | -0.085428 | -0.021526 | 7.7042e-05 | 4.9149e-05 | 0.12892 | 0.12892 | 0.12892 | 0.98731 | -0.24268 | 0.98633 | -0.26151 | 35.4179
132 | 0.083172 | 0.02096 | -0.083102 | -0.020916 | 6.9777e-05 | 4.4507e-05 | 0.12552 | 0.12552 | 0.12552 | 0.98633 | -0.26151 | 0.98543 | -0.27906 | 34.4827
133 | 0.074801 | 0.018895 | -0.074767 | -0.018873 | 3.4207e-05 | 2.1801e-05 | 0.11288 | 0.11288 | 0.11288 | 0.9865 | -0.2581 | 0.98601 | -0.26765 | 31.0111
134 | 0.063111 | 0.015952 | -0.063043 | -0.015909 | 6.7868e-05 | 4.3181e-05 | 0.095291 | 0.095291 | 0.095291 | 0.98601 | -0.26765 | 0.98485 | -0.2901 | 26.1788
135 | 0.0251 | 0.006296 | -0.025097 | -0.006294 | 3.2334e-06 | 1.9936e-06 | 0.03798 | 0.03798 | 0.03798 | 0.98346 | -0.31736 | 0.98333 | -0.32006 | 10.4339
136 | 0.016685 | 0.0041845 | -0.016681 | -0.0041824 | 3.5086e-06 | 2.0595e-06 | 0.025255 | 0.025255 | 0.025255 | 0.98311 | -0.32436 | 0.98288 | -0.32877 | 6.9382
137 | -0.017439 | -0.0043734 | 0.017442 | 0.0043755 | 3.5719e-06 | 2.1126e-06 | 0.026396 | 0.026396 | 0.026396 | 0.98311 | -0.32436 | 0.98333 | -0.32006 | 7.2516
138 | 0.014425 | 0.0036171 | -0.014425 | -0.0036166 | 7.1752e-07 | 4.0837e-07 | 0.02184 | 0.02184 | 0.02184 | 0.98288 | -0.32877 | 0.98283 | -0.32982 | 5.9999
139 | 0.01353 | 0.0033923 | -0.013527 | -0.0033908 | 2.782e-06 | 1.5565e-06 | 0.020485 | 0.020485 | 0.020485 | 0.98283 | -0.32982 | 0.98261 | -0.33413 | 5.6277
140 | 0.0119 | 0.0029831 | -0.011898 | -0.0029818 | 2.4661e-06 | 1.3219e-06 | 0.018022 | 0.018022 | 0.018022 | 0.98261 | -0.33413 | 0.98238 | -0.33848 | 4.9511
141 | 0.0096405 | 0.002416 | -0.0096403 | -0.0024159 | 1.9957e-07 | 9.6125e-08 | 0.014602 | 0.014602 | 0.014602 | 0.98238 | -0.33848 | 0.98236 | -0.33892 | 4.0117
142 | 0.0045142 | 0.0011312 | -0.0045139 | -0.0011312 | 2.8992e-07 | -2.3787e-08 | 0.0068377 | 0.0068378 | 0.0068378 | 0.98236 | -0.33892 | 0.98229 | -0.34027 | 1.8785
143 | 0.0022575 | 0.00056575 | -0.0022575 | -0.00056579 | 1.6513e-08 | -3.7096e-08 | 0.0034198 | 0.0034198 | 0.0034198 | 0.98229 | -0.34027 | 0.98229 | -0.34042 | 0.93951
144 | 0.048042 | 0.012075 | -0.048035 | -0.01207 | 7.0807e-06 | 4.4873e-06 | 0.073101 | 0.073101 | 0.073101 | 0.9781 | -0.42132 | 0.97794 | -0.42441 | 20.0826
145 | 0.046159 | 0.0116 | -0.046137 | -0.011586 | 2.2014e-05 | 1.394e-05 | 0.070246 | 0.070246 | 0.070246 | 0.97794 | -0.42441 | 0.97743 | -0.4344 | 19.2983
146 | 0.0018764 | 0.00047013 | -0.0018764 | -0.00047027 | 4.0013e-08 | -1.3862e-07 | 0.0028551 | 0.0028551 | 0.0028551 | 0.97794 | -0.42441 | 0.97792 | -0.42486 | 0.78438
147 | 0.044711 | 0.011229 | -0.044698 | -0.011221 | 1.309e-05 | 8.2831e-06 | 0.068075 | 0.068075 | 0.068075 | 0.97743 | -0.4344 | 0.97712 | -0.44054 | 18.702
148 | 0.042687 | 0.010717 | -0.04268 | -0.010712 | 6.4786e-06 | 4.0951e-06 | 0.065013 | 0.065013 | 0.065013 | 0.97712 | -0.44054 | 0.97696 | -0.44372 | 17.8606
149 | 0.039401 | 0.0098905 | -0.039369 | -0.0098705 | 3.1652e-05 | 1.9964e-05 | 0.060017 | 0.060017 | 0.060017 | 0.97696 | -0.44372 | 0.9761 | -0.46058 | 16.4883
150 | 0.0944 | 0.02387 | -0.094368 | -0.023849 | 3.226e-05 | 2.0593e-05 | 0.14311 | 0.14311 | 0.14311 | 0.98204 | -0.34403 | 0.98168 | -0.35116 | 39.3169
151 | 0.087408 | 0.022105 | -0.087249 | -0.022003 | 0.00015921 | 0.00010159 | 0.13256 | 0.13256 | 0.13256 | 0.98168 | -0.35116 | 0.97972 | -0.3892 | 36.4186
152 | 0.0049187 | 0.0012327 | -0.0049183 | -0.0012326 | 3.6775e-07 | 1.7358e-08 | 0.0074982 | 0.0074983 | 0.0074983 | 0.9761 | -0.46058 | 0.97602 | -0.46215 | 2.06

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.52547 | 0.13448

## res_load
| p_mw | q_mvar
0 | 0.0082496 | 0.0020675
1 | 0.0078692 | 0.0019722
2 | 0.0034811 | 0.00087244
3 | 0.0026429 | 0.00066237
4 | 0.001821 | 0.00045639
5 | 0.0019209 | 0.00048143
6 | 0.0018289 | 0.00045837
7 | 0.0058309 | 0.0014614
8 | 0.022812 | 0.0057172
9 | 0.0037556 | 0.00094125
10 | 0.0023548 | 0.00059017
11 | 0.0035849 | 0.00089845
12 | 0.0019857 | 0.00049766
13 | 0.0037815 | 0.00094773
14 | 0.0058443 | 0.0014647
15 | 0.0056456 | 0.0014149
16 | 0.00371 | 0.00092981
17 | 0.0020808 | 0.0005215
18 | 0.0039726 | 0.00099562
19 | 0.0026275 | 0.00065852
20 | 0.0026785 | 0.00067131
21 | 0.0016582 | 0.00041558
22 | 0.0041159 | 0.0010315
23 | 0.0043128 | 0.0010809
24 | 0.0043458 | 0.0010892
25 | 0.0058095 | 0.001456
26 | 0.0056713 | 0.0014214
27 | 0.0050998 | 0.0012781
28 | 0.0043175 | 0.0010821
29 | 0.0059036 | 0.0014796
30 | 0.0032881 | 0.00082406
31 | 0.0043217 | 0.0010831
32 | 0.0052222 | 0.0013088
33 | 0.0043503 | 0.0010903
34 | 0.005421 | 0.0013586
35 | 0.0027844 | 0.00069783
36 | 0.0030119 | 0.00075486
37 | 0.003638 | 0.00091177
38 | 0.0046924 | 0.001176
39 | 0.0018651 | 0.00046744
40 | 0.0015635 | 0.00039185
41 | 0.0019554 | 0.00049007
42 | 0.001909 | 0.00047844
43 | 0.0019326 | 0.00048435
44 | 0.026114 | 0.0065448
45 | 0.0041125 | 0.0010307
46 | 0.0038997 | 0.00097736
47 | 0.0060674 | 0.0015206
48 | 0.0029344 | 0.00073544
49 | 0.019541 | 0.0048975
50 | 0.0038751 | 0.00097119
51 | 0.0042211 | 0.0010579
52 | 0.0026092 | 0.00065392
53 | 0.0026539 | 0.00066512
54 | 0.0061678 | 0.0015458
55 | 0.0058435 | 0.0014645
56 | 0.0014143 | 0.00035446
57 | 0.0094585 | 0.0023705
58 | 0.0058184 | 0.0014582
59 | 0.0056799 | 0.0014235
60 | 0.0055566 | 0.0013926
61 | 0.0094318 | 0.0023638
62 | 0.0022883 | 0.00057349
63 | 0.0074243 | 0.0018607
64 | 0.015986 | 0.0040065
65 | 0.0030277 | 0.0007588
66 | 0.0047647 | 0.0011941
67 | 0.0028385 | 0.00071138
68 | 0.0021986 | 0.00055103
69 | 0.0024984 | 0.00062615
70 | 0.0045577 | 0.0011423
71 | 0.0041354 | 0.0010364
72 | 0.0022336 | 0.00055979
73 | 0.0046699 | 0.0011704
74 | 0.0043362 | 0.0010867
75 | 0.0068208 | 0.0017094
76 | 0.0051325 | 0.0012863
77 | 0.0053656 | 0.0013447
78 | 0.0048352 | 0.0012118
79 | 0.0043659 | 0.0010942
80 | 0.0064552 | 0.0016178
81 | 0.0022563 | 0.00056549
82 | 0.0062936 | 0.0015773
83 | 0.0033777 | 0.00084653
84 | 0.011656 | 0.0029211
85 | 0.00068165 | 0.00017084
86 | 0.0032372 | 0.00081133
87 | 0.00075365 | 0.00018888
88 | 0.0022559 | 0.00056539
89 | 0.007655 | 0.0019185
90 | 0.00089496 | 0.0002243
91 | 0.0016265 | 0.00040764
92 | 0.0022575 | 0.00056578
93 | 0.0051261 | 0.0012847
94 | 0.0022563 | 0.00056549
95 | 0.0030175 | 0.00075625
96 | 0.0039514 | 0.00099031
97 | 0.0022575 | 0.00056579
98 | 0.0027083 | 0.00067876
99 | 0.0034345 | 0.00086077
100 | 0.0014258 | 0.00035735
101 | 0.0018764 | 0.00047027
102 | 0.002011 | 0.00050401
103 | 0.0032798 | 0.000822
104 | 0.0052299 | 0.0013107
105 | 0.0046442 | 0.0011639
106 | 0.0069601 | 0.0017444
107 | 0.014449 | 0.0036213
108 | 0.0049183 | 0.0012326

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1