## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-500_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-500_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-500_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-500_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-500_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-500_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-500_0_4_node_12 | 0.4 | n |  | TRUE
7 | bus_LV_261-500_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_261-500_0_4_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_261-500_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_261-500_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_261-500_0_4_node_58 | 0.4 | n |  | TRUE
12 | bus_LV_261-500_0_4_node_59 | 0.4 | n |  | TRUE
13 | bus_LV_261-500_0_4_node_60 | 0.4 | n |  | TRUE
14 | bus_LV_261-500_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_261-500_0_4_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_261-500_0_4_node_117 | 0.4 | n |  | TRUE
17 | bus_LV_261-500_0_4_node_118 | 0.4 | n |  | TRUE
18 | bus_LV_261-500_0_4_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_261-500_0_4_node_19 | 0.4 | n |  | TRUE
20 | bus_LV_261-500_0_4_node_136 | 0.4 | n |  | TRUE
21 | bus_LV_261-500_0_4_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_261-500_0_4_node_87 | 0.4 | n |  | TRUE
23 | bus_LV_261-500_0_4_node_99 | 0.4 | n |  | TRUE
24 | bus_LV_261-500_0_4_node_32 | 0.4 | n |  | TRUE
25 | bus_LV_261-500_0_4_node_61 | 0.4 | n |  | TRUE
26 | bus_LV_261-500_0_4_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_261-500_0_4_node_125 | 0.4 | n |  | TRUE
28 | bus_LV_261-500_0_4_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_261-500_0_4_node_46 | 0.4 | n |  | TRUE
30 | bus_LV_261-500_0_4_node_47 | 0.4 | n |  | TRUE
31 | bus_LV_261-500_0_4_node_44 | 0.4 | n |  | TRUE
32 | bus_LV_261-500_0_4_node_25 | 0.4 | n |  | TRUE
33 | bus_LV_261-500_0_4_node_85 | 0.4 | n |  | TRUE
34 | bus_LV_261-500_0_4_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_261-500_0_4_node_83 | 0.4 | n |  | TRUE
36 | bus_LV_261-500_0_4_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_261-500_0_4_node_34 | 0.4 | n |  | TRUE
38 | bus_LV_261-500_0_4_node_121 | 0.4 | n |  | TRUE
39 | bus_LV_261-500_0_4_node_120 | 0.4 | n |  | TRUE
40 | bus_LV_261-500_0_4_node_29 | 0.4 | n |  | TRUE
41 | bus_LV_261-500_0_4_node_64 | 0.4 | n |  | TRUE
42 | bus_LV_261-500_0_4_node_66 | 0.4 | n |  | TRUE
43 | bus_LV_261-500_0_4_node_30 | 0.4 | n |  | TRUE
44 | bus_LV_261-500_0_4_node_50 | 0.4 | n |  | TRUE
45 | bus_LV_261-500_0_4_node_62 | 0.4 | n |  | TRUE
46 | bus_LV_261-500_0_4_node_126 | 0.4 | n |  | TRUE
47 | bus_LV_261-500_0_4_node_105 | 0.4 | n |  | TRUE
48 | bus_LV_261-500_0_4_node_119 | 0.4 | n |  | TRUE
49 | bus_LV_261-500_0_4_node_135 | 0.4 | n |  | TRUE
50 | bus_LV_261-500_0_4_node_43 | 0.4 | n |  | TRUE
51 | bus_LV_261-500_0_4_node_40 | 0.4 | n |  | TRUE
52 | bus_LV_261-500_0_4_node_86 | 0.4 | n |  | TRUE
53 | bus_LV_261-500_0_4_node_133 | 0.4 | n |  | TRUE
54 | bus_LV_261-500_0_4_node_55 | 0.4 | n |  | TRUE
55 | bus_LV_261-500_0_4_node_88 | 0.4 | n |  | TRUE
56 | bus_LV_261-500_0_4_node_97 | 0.4 | n |  | TRUE
57 | bus_LV_261-500_0_4_node_134 | 0.4 | n |  | TRUE
58 | bus_LV_261-500_0_4_node_53 | 0.4 | n |  | TRUE
59 | bus_LV_261-500_0_4_node_45 | 0.4 | n |  | TRUE
60 | bus_LV_261-500_0_4_node_132 | 0.4 | n |  | TRUE
61 | bus_LV_261-500_0_4_node_130 | 0.4 | n |  | TRUE
62 | bus_LV_261-500_0_4_node_84 | 0.4 | n |  | TRUE
63 | bus_LV_261-500_0_4_node_33 | 0.4 | n |  | TRUE
64 | bus_LV_261-500_0_4_node_122 | 0.4 | n |  | TRUE
65 | bus_LV_261-500_0_4_node_36 | 0.4 | n |  | TRUE
66 | bus_LV_261-500_0_4_node_63 | 0.4 | n |  | TRUE
67 | bus_LV_261-500_0_4_node_67 | 0.4 | n |  | TRUE
68 | bus_LV_261-500_0_4_node_65 | 0.4 | n |  | TRUE
69 | bus_LV_261-500_0_4_node_109 | 0.4 | n |  | TRUE
70 | bus_LV_261-500_0_4_node_52 | 0.4 | n |  | TRUE
71 | bus_LV_261-500_0_4_node_48 | 0.4 | n |  | TRUE
72 | bus_LV_261-500_0_4_node_116 | 0.4 | n |  | TRUE
73 | bus_LV_261-500_0_4_node_68 | 0.4 | n |  | TRUE
74 | bus_LV_261-500_0_4_node_35 | 0.4 | n |  | TRUE
75 | bus_LV_261-500_0_4_node_37 | 0.4 | n |  | TRUE
76 | bus_LV_261-500_0_4_node_49 | 0.4 | n |  | TRUE
77 | bus_LV_261-500_0_4_node_51 | 0.4 | n |  | TRUE
78 | bus_LV_261-500_0_4_node_38 | 0.4 | n |  | TRUE
79 | bus_LV_261-500_0_4_node_39 | 0.4 | n |  | TRUE
80 | bus_LV_261-500_0_4_node_41 | 0.4 | n |  | TRUE
81 | bus_LV_261-500_0_4_node_42 | 0.4 | n |  | TRUE
82 | bus_LV_261-500_0_4_node_128 | 0.4 | n |  | TRUE
83 | bus_LV_261-500_0_4_node_73 | 0.4 | n |  | TRUE
84 | bus_LV_261-500_0_4_node_78 | 0.4 | n |  | TRUE
85 | bus_LV_261-500_0_4_node_71 | 0.4 | n |  | TRUE
86 | bus_LV_261-500_0_4_node_129 | 0.4 | n |  | TRUE
87 | bus_LV_261-500_0_4_node_54 | 0.4 | n |  | TRUE
88 | bus_LV_261-500_0_4_node_108 | 0.4 | n |  | TRUE
89 | bus_LV_261-500_0_4_node_110 | 0.4 | n |  | TRUE
90 | bus_LV_261-500_0_4_node_106 | 0.4 | n |  | TRUE
91 | bus_LV_261-500_0_4_node_72 | 0.4 | n |  | TRUE
92 | bus_LV_261-500_0_4_node_76 | 0.4 | n |  | TRUE
93 | bus_LV_261-500_0_4_node_56 | 0.4 | n |  | TRUE
94 | bus_LV_261-500_0_4_node_57 | 0.4 | n |  | TRUE
95 | bus_LV_261-500_0_4_node_75 | 0.4 | n |  | TRUE
96 | bus_LV_261-500_0_4_node_70 | 0.4 | n |  | TRUE
97 | bus_LV_261-500_0_4_node_127 | 0.4 | n |  | TRUE
98 | bus_LV_261-500_0_4_node_74 | 0.4 | n |  | TRUE
99 | bus_LV_261-500_0_4_node_69 | 0.4 | n |  | TRUE
100 | bus_LV_261-500_0_4_node_114 | 0.4 | n |  | TRUE
101 | bus_LV_261-500_0_4_node_115 | 0.4 | n |  | TRUE
102 | bus_LV_261-500_0_4_node_113 | 0.4 | n |  | TRUE
103 | bus_LV_261-500_0_4_node_107 | 0.4 | n |  | TRUE
104 | bus_LV_261-500_0_4_node_79 | 0.4 | n |  | TRUE
105 | bus_LV_261-500_0_4_node_77 | 0.4 | n |  | TRUE
106 | bus_LV_261-500_0_4_node_81 | 0.4 | n |  | TRUE
107 | bus_LV_261-500_0_4_node_80 | 0.4 | n |  | TRUE
108 | bus_LV_261-500_0_4_node_82 | 0.4 | n |  | TRUE
109 | bus_LV_261-500_0_4_node_131 | 0.4 | n |  | TRUE
110 | bus_LV_261-500_0_4_node_111 | 0.4 | n |  | TRUE
111 | bus_LV_261-500_0_4_node_112 | 0.4 | n |  | TRUE
112 | bus_LV_261-500_0_4_node_90 | 0.4 | n |  | TRUE
113 | bus_LV_261-500_0_4_node_91 | 0.4 | n |  | TRUE
114 | bus_LV_261-500_0_4_node_92 | 0.4 | n |  | TRUE
115 | bus_LV_261-500_0_4_node_93 | 0.4 | n |  | TRUE
116 | bus_LV_261-500_0_4_node_94 | 0.4 | n |  | TRUE
117 | bus_LV_261-500_0_4_node_95 | 0.4 | n |  | TRUE
118 | bus_LV_261-500_0_4_node_102 | 0.4 | n |  | TRUE
119 | bus_LV_261-500_0_4_node_103 | 0.4 | n |  | TRUE
120 | bus_LV_261-500_0_4_node_96 | 0.4 | n |  | TRUE
121 | bus_LV_261-500_0_4_node_98 | 0.4 | n |  | TRUE
122 | bus_LV_261-500_0_4_node_100 | 0.4 | n |  | TRUE
123 | bus_LV_261-500_0_4_node_101 | 0.4 | n |  | TRUE
124 | bus_LV_261-500_0_4_node_104 | 0.4 | n |  | TRUE
125 | bus_LV_261-500_0_4_node_123 | 0.4 | n |  | TRUE
126 | bus_LV_261-500_0_4_node_124 | 0.4 | n |  | TRUE
127 | bus_MV_542_0_node_42 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-500_0_4_load_0 | 0 | 0.0053317 | 0.0013362 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-500_0_4_load_1 | 1 | 0.0065584 | 0.0016437 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-500_0_4_load_3 | 3 | 0.0045336 | 0.0011362 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-500_0_4_load_4 | 4 | 0.0021742 | 0.00054492 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-500_0_4_load_5 | 5 | 0.003691 | 0.00092505 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-500_0_4_load_10 | 8 | 0.00644 | 0.001614 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-500_0_4_load_7 | 9 | 0.0010532 | 0.00026396 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-500_0_4_load_8 | 10 | 0.0047116 | 0.0011809 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-500_0_4_load_60 | 13 | 0.011677 | 0.0029266 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-500_0_4_load_9 | 14 | 0.0084132 | 0.0021086 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-500_0_4_load_118 | 17 | 0.0046937 | 0.0011763 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-500_0_4_load_136 | 20 | 0.0041423 | 0.0010381 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-500_0_4_load_99 | 23 | 0.0010449 | 0.00026187 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-500_0_4_load_61 | 25 | 0.007508 | 0.0018817 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-500_0_4_load_125 | 27 | 0.0062572 | 0.0015682 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-500_0_4_load_46 | 29 | 0.0022204 | 0.00055649 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-500_0_4_load_47 | 30 | 0.009559 | 0.0023957 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-500_0_4_load_44 | 31 | 0.003591 | 0.00089999 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-500_0_4_load_85 | 33 | 0.0010163 | 0.00025471 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-500_0_4_load_83 | 35 | 0.0068332 | 0.0017126 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-500_0_4_load_34 | 37 | 0.019929 | 0.0049946 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-500_0_4_load_121 | 38 | 0.0043815 | 0.0010981 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-500_0_4_load_120 | 39 | 0.004815 | 0.0012068 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-500_0_4_load_64 | 41 | 0.0010212 | 0.00025595 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-500_0_4_load_66 | 42 | 0.0036487 | 0.00091444 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-500_0_4_load_62 | 45 | 0.011502 | 0.0028827 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-500_0_4_load_126 | 46 | 0.0040949 | 0.0010263 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-500_0_4_load_105 | 47 | 0.0025978 | 0.00065107 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-500_0_4_load_119 | 48 | 0.0010811 | 0.00027096 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-500_0_4_load_135 | 49 | 0.0041295 | 0.001035 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-500_0_4_load_43 | 50 | 0.0057938 | 0.0014521 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-500_0_4_load_86 | 52 | 0.002744 | 0.00068771 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-500_0_4_load_133 | 53 | 0.0044601 | 0.0011178 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-500_0_4_load_88 | 55 | 0.00094692 | 0.00023732 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-500_0_4_load_97 | 56 | 0.0010764 | 0.00026978 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-500_0_4_load_134 | 57 | 0.0041934 | 0.001051 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-500_0_4_load_45 | 59 | 0.0029854 | 0.00074822 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-500_0_4_load_132 | 60 | 0.00063022 | 0.00015795 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-500_0_4_load_84 | 62 | 0.0024541 | 0.00061506 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-500_0_4_load_33 | 63 | 0.0010205 | 0.00025576 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-500_0_4_load_122 | 64 | 0.0043352 | 0.0010865 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-500_0_4_load_36 | 65 | 0.0014768 | 0.00037013 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-500_0_4_load_67 | 67 | 0.032017 | 0.0080243 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-500_0_4_load_65 | 68 | 0.0010119 | 0.0002536 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-500_0_4_load_48 | 71 | 0.014501 | 0.0036342 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-500_0_4_load_116 | 72 | 0.0078859 | 0.0019764 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-500_0_4_load_68 | 73 | 0.0068525 | 0.0017174 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-500_0_4_load_49 | 76 | 0.0075344 | 0.0018883 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-500_0_4_load_51 | 77 | 0.0014014 | 0.00035122 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-500_0_4_load_38 | 78 | 0.016843 | 0.0042212 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-500_0_4_load_39 | 79 | 0.013908 | 0.0034857 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-500_0_4_load_41 | 80 | 0.017573 | 0.0044043 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-500_0_4_load_128 | 82 | 0.0050186 | 0.0012578 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-500_0_4_load_78 | 84 | 0.0053196 | 0.0013332 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-500_0_4_load_129 | 86 | 0.0049754 | 0.001247 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-500_0_4_load_54 | 87 | 0.0026023 | 0.0006522 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-500_0_4_load_108 | 88 | 0.00099063 | 0.00024828 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-500_0_4_load_110 | 89 | 0.0012479 | 0.00031274 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-500_0_4_load_106 | 90 | 0.0029064 | 0.00072841 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-500_0_4_load_75 | 95 | 0.0031371 | 0.00078624 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-500_0_4_load_127 | 97 | 0.002635 | 0.0006604 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-500_0_4_load_74 | 98 | 0.0033193 | 0.00083191 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-500_0_4_load_69 | 99 | 0.012507 | 0.0031346 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-500_0_4_load_114 | 100 | 0.0022409 | 0.00056162 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-500_0_4_load_115 | 101 | 0.0028214 | 0.00070711 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-500_0_4_load_113 | 102 | 0.0029272 | 0.00073363 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-500_0_4_load_107 | 103 | 0.0010318 | 0.0002586 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-500_0_4_load_79 | 104 | 0.0052849 | 0.0013245 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-500_0_4_load_77 | 105 | 0.010437 | 0.0026158 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-500_0_4_load_81 | 106 | 0.010274 | 0.0025749 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-500_0_4_load_82 | 108 | 0.0098277 | 0.0024631 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-500_0_4_load_131 | 109 | 0.0097506 | 0.0024437 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-500_0_4_load_111 | 110 | 0.0053455 | 0.0013397 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-500_0_4_load_90 | 112 | 0.002781 | 0.00069698 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-500_0_4_load_91 | 113 | 0.00097707 | 0.00024488 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-500_0_4_load_92 | 114 | 0.00093192 | 0.00023356 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-500_0_4_load_93 | 115 | 0.00097471 | 0.00024428 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-500_0_4_load_94 | 116 | 0.0010761 | 0.00026971 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-500_0_4_load_95 | 117 | 0.0026605 | 0.00066679 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-500_0_4_load_102 | 118 | 0.0031046 | 0.00077809 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-500_0_4_load_103 | 119 | 0.0023107 | 0.00057912 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-500_0_4_load_96 | 120 | 0.0028142 | 0.0007053 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_261-500_0_4_load_98 | 121 | 0.00090374 | 0.0002265 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_261-500_0_4_load_100 | 122 | 0.0025521 | 0.00063961 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_261-500_0_4_load_101 | 123 | 0.0016077 | 0.00040294 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_261-500_0_4_load_123 | 125 | 0.0041116 | 0.0010305 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_261-500_0_4_load_124 | 126 | 0.0029277 | 0.00073376 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 45 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-500_0_4_line_0 |  | 0 | 1 | 0.020734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-500_0_4_line_1 |  | 0 | 2 | 0.017244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-500_0_4_line_2 |  | 2 | 3 | 0.024391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-500_0_4_line_3 |  | 2 | 4 | 0.018344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-500_0_4_line_4 |  | 3 | 5 | 0.020264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-500_0_4_line_5 |  | 4 | 6 | 0.0051947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-500_0_4_line_6 |  | 5 | 7 | 0.0089529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-500_0_4_line_7 |  | 6 | 8 | 0.0072873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-500_0_4_line_8 |  | 7 | 9 | 0.013786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-500_0_4_line_9 |  | 7 | 10 | 0.025353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-500_0_4_line_10 |  | 8 | 14 | 0.040694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-500_0_4_line_11 |  | 10 | 11 | 0.025563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-500_0_4_line_12 |  | 11 | 12 | 0.006322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-500_0_4_line_13 |  | 11 | 13 | 0.028724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-500_0_4_line_14 |  | 12 | 100 | 0.009076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-500_0_4_line_15 |  | 15 | 16 | 0.007917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-500_0_4_line_16 |  | 15 | 17 | 0.0058865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-500_0_4_line_17 |  | 16 | 47 | 0.0075769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-500_0_4_line_18 |  | 17 | 48 | 0.0047511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_261-500_0_4_line_19 |  | 18 | 19 | 0.015453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-500_0_4_line_20 |  | 18 | 20 | 0.029758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-500_0_4_line_21 |  | 19 | 24 | 0.017231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_261-500_0_4_line_22 |  | 19 | 25 | 0.0070488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_261-500_0_4_line_23 |  | 20 | 49 | 0.013196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_261-500_0_4_line_24 |  | 21 | 22 | 0.004224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-500_0_4_line_25 |  | 21 | 23 | 0.0081346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_261-500_0_4_line_26 |  | 22 | 55 | 7.6064e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-500_0_4_line_27 |  | 22 | 52 | 0.0066001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-500_0_4_line_28 |  | 23 | 56 | 0.0049015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-500_0_4_line_29 |  | 24 | 46 | 0.030519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_261-500_0_4_line_30 |  | 24 | 26 | 0.008998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_261-500_0_4_line_31 |  | 25 | 30 | 0.065285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_261-500_0_4_line_32 |  | 26 | 27 | 0.02097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-500_0_4_line_33 |  | 28 | 29 | 0.026621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_261-500_0_4_line_34 |  | 28 | 30 | 0.0034937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_261-500_0_4_line_35 |  | 28 | 31 | 0.035153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-500_0_4_line_36 |  | 29 | 58 | 0.024678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_261-500_0_4_line_37 |  | 31 | 59 | 0.0083869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-500_0_4_line_38 |  | 32 | 33 | 0.034039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-500_0_4_line_39 |  | 32 | 34 | 0.004405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-500_0_4_line_40 |  | 32 | 35 | 0.014929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-500_0_4_line_41 |  | 33 | 62 | 0.036608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-500_0_4_line_42 |  | 34 | 36 | 0.035555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-500_0_4_line_43 |  | 34 | 37 | 0.024174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-500_0_4_line_44 |  | 36 | 38 | 0.03212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-500_0_4_line_45 |  | 36 | 39 | 0.015195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-500_0_4_line_46 |  | 37 | 63 | 0.019839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_261-500_0_4_line_47 |  | 38 | 64 | 0.016951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-500_0_4_line_48 |  | 39 | 65 | 0.026825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-500_0_4_line_49 |  | 40 | 41 | 0.027775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_261-500_0_4_line_50 |  | 40 | 42 | 0.03115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_261-500_0_4_line_51 |  | 41 | 66 | 0.0082141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_261-500_0_4_line_52 |  | 42 | 67 | 0.034248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_261-500_0_4_line_53 |  | 43 | 44 | 0.021064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_261-500_0_4_line_54 |  | 43 | 45 | 0.034173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_261-500_0_4_line_55 |  | 44 | 70 | 0.010101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-500_0_4_line_56 |  | 44 | 71 | 0.033105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_261-500_0_4_line_57 |  | 46 | 73 | 0.014482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_261-500_0_4_line_58 |  | 47 | 119 | 0.014938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-500_0_4_line_59 |  | 48 | 123 | 0.0035688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-500_0_4_line_60 |  | 49 | 57 | 0.022565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-500_0_4_line_61 |  | 50 | 51 | 0.013378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-500_0_4_line_62 |  | 51 | 81 | 0.029215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-500_0_4_line_63 |  | 53 | 54 | 0.016953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-500_0_4_line_64 |  | 54 | 92 | 0.019808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-500_0_4_line_65 |  | 56 | 120 | 0.0073428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-500_0_4_line_66 |  | 58 | 87 | 0.029434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_261-500_0_4_line_67 |  | 59 | 80 | 0.025402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-500_0_4_line_68 |  | 60 | 61 | 0.021781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-500_0_4_line_69 |  | 61 | 86 | 0.020164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-500_0_4_line_70 |  | 61 | 109 | 0.01009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-500_0_4_line_71 |  | 64 | 125 | 0.015567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-500_0_4_line_72 |  | 65 | 74 | 0.0019111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-500_0_4_line_73 |  | 66 | 77 | 0.013253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_261-500_0_4_line_74 |  | 67 | 73 | 0.0099679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
75 | LV_261-500_0_4_line_75 |  | 68 | 69 | 0.00055701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-500_0_4_line_76 |  | 69 | 103 | 0.017213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-500_0_4_line_77 |  | 69 | 72 | 0.0070835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-500_0_4_line_78 |  | 70 | 88 | 0.014173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-500_0_4_line_79 |  | 71 | 76 | 0.035311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_261-500_0_4_line_80 |  | 74 | 75 | 0.01301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_261-500_0_4_line_81 |  | 75 | 76 | 0.020755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-500_0_4_line_82 |  | 76 | 77 | 0.010843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_261-500_0_4_line_83 |  | 78 | 79 | 0.031281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_261-500_0_4_line_84 |  | 79 | 80 | 0.0036206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_261-500_0_4_line_85 |  | 81 | 82 | 0.013357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_261-500_0_4_line_86 |  | 82 | 86 | 0.015035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_261-500_0_4_line_87 |  | 83 | 84 | 0.0065837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_261-500_0_4_line_88 |  | 83 | 85 | 0.006714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_261-500_0_4_line_89 |  | 84 | 104 | 0.017325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_261-500_0_4_line_90 |  | 85 | 99 | 0.032852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_261-500_0_4_line_91 |  | 87 | 91 | 0.010853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_261-500_0_4_line_92 |  | 88 | 89 | 0.018257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_261-500_0_4_line_93 |  | 88 | 90 | 0.0068703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_261-500_0_4_line_94 |  | 89 | 102 | 0.0060039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_261-500_0_4_line_95 |  | 90 | 103 | 0.0061823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_261-500_0_4_line_96 |  | 91 | 97 | 0.0081315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_261-500_0_4_line_97 |  | 92 | 98 | 0.013446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_261-500_0_4_line_98 |  | 93 | 94 | 0.015427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_261-500_0_4_line_99 |  | 93 | 95 | 0.0096517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_261-500_0_4_line_100 |  | 94 | 96 | 0.013495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_261-500_0_4_line_101 |  | 94 | 97 | 0.0080853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_261-500_0_4_line_102 |  | 95 | 98 | 0.018633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_261-500_0_4_line_103 |  | 96 | 99 | 0.011206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
104 | LV_261-500_0_4_line_104 |  | 100 | 101 | 0.014532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_261-500_0_4_line_105 |  | 100 | 102 | 0.0066034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_261-500_0_4_line_106 |  | 101 | 124 | 0.0078584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_261-500_0_4_line_107 |  | 104 | 107 | 0.029527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
108 | LV_261-500_0_4_line_108 |  | 105 | 106 | 0.011502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_261-500_0_4_line_109 |  | 106 | 107 | 0.006113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-500_0_4_line_110 |  | 107 | 108 | 0.017365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_261-500_0_4_line_111 |  | 108 | 109 | 0.022743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_261-500_0_4_line_112 |  | 110 | 111 | 0.0066369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_261-500_0_4_line_113 |  | 111 | 115 | 5.2666e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_261-500_0_4_line_114 |  | 112 | 113 | 0.005594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_261-500_0_4_line_115 |  | 112 | 114 | 0.0068851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_261-500_0_4_line_116 |  | 113 | 115 | 0.017868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_261-500_0_4_line_117 |  | 114 | 116 | 0.01895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_261-500_0_4_line_118 |  | 114 | 117 | 0.007239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_261-500_0_4_line_119 |  | 116 | 118 | 0.0056854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_261-500_0_4_line_120 |  | 118 | 119 | 0.0065501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_261-500_0_4_line_121 |  | 119 | 124 | 0.00751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_261-500_0_4_line_122 |  | 120 | 121 | 0.006985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_261-500_0_4_line_123 |  | 121 | 122 | 0.006933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_261-500_0_4_line_124 |  | 121 | 123 | 0.015593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_261-500_0_4_line_125 |  | 125 | 126 | 0.0095706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-500_0_4_trafo_62 | 0.63 MVA 20/0.4 kV | 127 | 45 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2683675.8865 | 1250599.7145 | 2683683.8526 | 1250580.5723
1 | 2683669.2611 | 1250615.6353 | 2683675.8865 | 1250599.7145
2 | 2683669.2611 | 1250615.6353 | 2683665.3522 | 1250626.7329 | 2683655.4149 | 1250634.5208
3 | 2683669.2611 | 1250615.6353 | 2683659.0425 | 1250611.6437 | 2683652.0045 | 1250609.4436
4 | 2683639.4657 | 1250647.0204 | 2683655.4149 | 1250634.5208
5 | 2683647.0464 | 1250607.8938 | 2683652.0045 | 1250609.4436
6 | 2683632.4191 | 1250652.5429 | 2683639.4657 | 1250647.0204
7 | 2683647.0464 | 1250607.8938 | 2683643.4902 | 1250603.1067 | 2683643.9453 | 1250601.8636
8 | 2683632.4191 | 1250652.5429 | 2683627.8255 | 1250652.7894 | 2683621.7637 | 1250645.8875
9 | 2683632.4191 | 1250652.5429 | 2683656.8359 | 1250659.3704
10 | 2683634.6199 | 1250571.0641 | 2683645.5017 | 1250575.0697 | 2683650.3297 | 1250584.4226 | 2683643.9453 | 1250601.8636
11 | 2683677.2085 | 1250658.0125 | 2683658.7046 | 1250653.2032 | 2683656.8359 | 1250659.3704
12 | 2683678.7221 | 1250651.8737 | 2683677.2085 | 1250658.0125
13 | 2683677.2085 | 1250658.0125 | 2683670.2252 | 1250685.8742
14 | 2683678.7221 | 1250651.8737 | 2683679.7607 | 1250652.0996 | 2683681.224 | 1250646.316 | 2683681.7878 | 1250644.3447
15 | 2683698.6115 | 1250586.4057 | 2683697.7057 | 1250589.6064 | 2683697.2261 | 1250591.4899 | 2683696.4655 | 1250594.0255
16 | 2683698.6115 | 1250586.4057 | 2683704.2967 | 1250587.932
17 | 2683696.4655 | 1250594.0255 | 2683694.2923 | 1250601.2841
18 | 2683704.2967 | 1250587.932 | 2683708.8853 | 1250589.1639 | 2683708.8853 | 1250589.1639
19 | 2683747.5322 | 1250865.6941 | 2683745.1416 | 1250861.2459 | 2683743.14 | 1250861.3176 | 2683741.5671 | 1250860.9729 | 2683740.097 | 1250860.2961 | 2683738.793 | 1250859.0879 | 2683737.0682 | 1250856.1391
20 | 2683747.5322 | 1250865.6941 | 2683772.8121 | 1250849.9941
21 | 2683720.3429 | 1250858.5379 | 2683725.9568 | 1250858.7285 | 2683729.9107 | 1250858.8622 | 2683733.3034 | 1250857.5759 | 2683737.0682 | 1250856.1391
22 | 2683737.0682 | 1250856.1391 | 2683734.3643 | 1250850.8859 | 2683734.0397 | 1250849.7924
23 | 2683784.0221 | 1250843.0322 | 2683772.8121 | 1250849.9941
24 | 2683743.8793 | 1250594.918 | 2683742.7723 | 1250598.9943
25 | 2683743.8793 | 1250594.918 | 2683736.0229 | 1250592.8087
26 | 2683742.7539 | 1250599.0681 | 2683742.7723 | 1250598.9943
27 | 2683742.7723 | 1250598.9943 | 2683749.1473 | 1250600.7034
28 | 2683731.2891 | 1250591.5377 | 2683736.0229 | 1250592.8087
29 | 2683720.3429 | 1250858.5379 | 2683720.4234 | 1250856.5821 | 2683719.5134 | 1250828.5594 | 2683719.5352 | 1250828.0356
30 | 2683720.3429 | 1250858.5379 | 2683720.2625 | 1250860.4827 | 2683719.2905 | 1250861.959 | 2683717.3779 | 1250863.2107 | 2683714.3675 | 1250863.0903
31 | 2683744.7398 | 1250790.8876 | 2683735.6818 | 1250796.1414 | 2683734.2017 | 1250797.7772 | 2683733.1904 | 1250799.8867 | 2683732.6833 | 1250802.1146 | 2683731.8195 | 1250810.353 | 2683731.3299 | 1250820.954 | 2683731.6841 | 1250834.3467 | 2683732.0746 | 1250840.3679 | 2683732.7502 | 1250845.4479 | 2683734.0397 | 1250849.7924
32 | 2683714.3675 | 1250863.0903 | 2683710.6541 | 1250861.4255 | 2683704.9521 | 1250856.7859 | 2683697.8785 | 1250850.3706
33 | 2683744.3737 | 1250787.4132 | 2683743.934 | 1250783.2705 | 2683741.0437 | 1250782.1289 | 2683739.0472 | 1250778.6314 | 2683739.661 | 1250773.6697 | 2683742.5283 | 1250763.7552
34 | 2683744.3737 | 1250787.4132 | 2683744.7398 | 1250790.8876
35 | 2683744.3737 | 1250787.4132 | 2683761.6885 | 1250778.0397 | 2683775.2474 | 1250770.6035
36 | 2683749.3843 | 1250740.0486 | 2683742.5283 | 1250763.7552
37 | 2683775.2474 | 1250770.6035 | 2683782.601 | 1250766.5705
38 | 2683595.9406 | 1250724.7044 | 2683616.3543 | 1250707.5796 | 2683611.7481 | 1250701.7957
39 | 2683595.9406 | 1250724.7044 | 2683598.6699 | 1250728.1677
40 | 2683595.9406 | 1250724.7044 | 2683586.6919 | 1250712.9857
41 | 2683588.9425 | 1250673.1594 | 2683611.7481 | 1250701.7957
42 | 2683598.6699 | 1250728.1677 | 2683620.7197 | 1250756.1107
43 | 2683598.6699 | 1250728.1677 | 2683617.7868 | 1250713.3709
44 | 2683620.7197 | 1250756.1107 | 2683640.6189 | 1250781.3239
45 | 2683620.7197 | 1250756.1107 | 2683632.7396 | 1250746.8156
46 | 2683617.7868 | 1250713.3709 | 2683633.4756 | 1250701.2275
47 | 2683640.6189 | 1250781.3239 | 2683651.1207 | 1250794.6301
48 | 2683653.9598 | 1250730.4057 | 2683632.7396 | 1250746.8156
49 | 2683729.3535 | 1250739.1427 | 2683715.9434 | 1250749.9947 | 2683711.5719 | 1250752.1568 | 2683706.0164 | 1250753.168
50 | 2683729.3535 | 1250739.1427 | 2683729.9314 | 1250748.4578 | 2683729.7041 | 1250756.5273 | 2683728.783 | 1250762.9413 | 2683727.0635 | 1250769.9998
51 | 2683698.2323 | 1250750.545 | 2683706.0164 | 1250753.168
52 | 2683727.0635 | 1250769.9998 | 2683723.8862 | 1250783.0427 | 2683721.1797 | 1250798.8052 | 2683720.8376 | 1250803.6234
53 | 2683718.5217 | 1250679.7454 | 2683698.1808 | 1250674.0539
54 | 2683718.5217 | 1250679.7454 | 2683710.1916 | 1250712.8874
55 | 2683700.5542 | 1250664.2356 | 2683698.1808 | 1250674.0539
56 | 2683698.1808 | 1250674.0539 | 2683696.4205 | 1250673.6065 | 2683688.7665 | 1250703.9448
57 | 2683720.1364 | 1250813.5665 | 2683719.5352 | 1250828.0356
58 | 2683690.0078 | 1250615.5948 | 2683694.2923 | 1250601.2841
59 | 2683709.8173 | 1250585.7189 | 2683708.8853 | 1250589.1639
60 | 2683803.814 | 1250832.215 | 2683788.4081 | 1250840.3083 | 2683784.0221 | 1250843.0322
61 | 2683873.8541 | 1250709.4524 | 2683884.0081 | 1250702.5243 | 2683885.0075 | 1250702.0996
62 | 2683873.8541 | 1250709.4524 | 2683873.1434 | 1250708.4638 | 2683856.8194 | 1250685.6825
63 | 2683776.1385 | 1250650.9713 | 2683780.8132 | 1250634.6759
64 | 2683795.8449 | 1250653.4851 | 2683776.1385 | 1250650.9713
65 | 2683726.8868 | 1250594.3003 | 2683730.301 | 1250595.2153 | 2683731.2891 | 1250591.5377 | 2683731.2891 | 1250591.5377
66 | 2683749.3843 | 1250740.0486 | 2683757.9093 | 1250742.0595 | 2683764.9309 | 1250740.413 | 2683770.992 | 1250736.7515 | 2683773.8648 | 1250731.0533
67 | 2683804.8728 | 1250754.3557 | 2683782.601 | 1250766.5705
68 | 2683879.8017 | 1250655.7075 | 2683896.3891 | 1250663.626 | 2683899.783 | 1250663.8398
69 | 2683879.8017 | 1250655.7075 | 2683877.6867 | 1250654.7213 | 2683872.2411 | 1250652.2313 | 2683869.3684 | 1250651.4345 | 2683866.7373 | 1250653.3098 | 2683864.6713 | 1250658.5479
70 | 2683879.8017 | 1250655.7075 | 2683880.6283 | 1250652.25 | 2683874.9145 | 1250649.0786
71 | 2683651.1207 | 1250794.6301 | 2683660.7647 | 1250806.8496
72 | 2683655.4716 | 1250729.2366 | 2683653.9598 | 1250730.4057
73 | 2683698.2323 | 1250750.545 | 2683694.9563 | 1250749.4424 | 2683689.0979 | 1250745.7124 | 2683686.8867 | 1250743.9125
74 | 2683720.8376 | 1250803.6234 | 2683720.1428 | 1250813.4125 | 2683720.1364 | 1250813.5665
75 | 2683726.1406 | 1250656.7944 | 2683726.2974 | 1250656.2599
76 | 2683726.2974 | 1250656.2599 | 2683727.2261 | 1250653.0484 | 2683717.6772 | 1250650.2892 | 2683716.5827 | 1250654.064
77 | 2683726.2974 | 1250656.2599 | 2683733.1036 | 1250658.2226
78 | 2683704.085 | 1250650.5086 | 2683702.6225 | 1250656.2366 | 2683700.5542 | 1250664.2356
79 | 2683678.4772 | 1250737.0672 | 2683682.1702 | 1250724.1541 | 2683683.8807 | 1250723.311 | 2683688.7665 | 1250703.9448
80 | 2683665.4644 | 1250720.8714 | 2683655.4716 | 1250729.2366
81 | 2683665.4644 | 1250720.8714 | 2683673.5699 | 1250730.6709 | 2683678.4772 | 1250737.0672
82 | 2683678.4772 | 1250737.0672 | 2683686.8867 | 1250743.9125
83 | 2683808.0474 | 1250752.6147 | 2683818.1961 | 1250747.0487 | 2683834.9217 | 1250736.628
84 | 2683808.0474 | 1250752.6147 | 2683804.8728 | 1250754.3557
85 | 2683856.8194 | 1250685.6825 | 2683858.2381 | 1250677.73 | 2683859.3958 | 1250672.5793
86 | 2683859.3958 | 1250672.5793 | 2683860.0992 | 1250669.4501 | 2683862.6647 | 1250663.1484 | 2683863.5972 | 1250661.2713 | 2683864.6713 | 1250658.5479
87 | 2683822.6761 | 1250684.4097 | 2683824.2131 | 1250678.0079
88 | 2683819.1526 | 1250690.1309 | 2683822.6761 | 1250684.4097
89 | 2683824.2131 | 1250678.0079 | 2683828.2575 | 1250661.1619
90 | 2683819.1526 | 1250690.1309 | 2683817.5214 | 1250701.9055 | 2683816.6244 | 1250708.2086 | 2683812.3398 | 1250709.5601 | 2683802.3612 | 1250711.1599
91 | 2683777.5425 | 1250720.91 | 2683776.0796 | 1250726.6603 | 2683773.8648 | 1250731.0533
92 | 2683704.085 | 1250650.5086 | 2683705.1247 | 1250646.9206 | 2683695.0195 | 1250643.9979 | 2683693.9007 | 1250647.8405
93 | 2683704.085 | 1250650.5086 | 2683710.6845 | 1250652.4186
94 | 2683688.1323 | 1250646.1757 | 2683693.9007 | 1250647.8405
95 | 2683710.6845 | 1250652.4186 | 2683716.5662 | 1250654.1209 | 2683716.5827 | 1250654.064
96 | 2683777.5425 | 1250720.91 | 2683779.082 | 1250712.9256
97 | 2683795.8449 | 1250653.4851 | 2683795.5345 | 1250655.6823 | 2683794.5846 | 1250661.4621 | 2683793.8931 | 1250666.0446 | 2683793.761 | 1250666.7679
98 | 2683781.4185 | 1250705.2086 | 2683780.2589 | 1250695.9186 | 2683785.9361 | 1250693.7862
99 | 2683785.9361 | 1250693.7862 | 2683788.5622 | 1250684.4986
100 | 2683791.5096 | 1250713.9245 | 2683786.1863 | 1250710.7913 | 2683781.4185 | 1250705.2086
101 | 2683781.4185 | 1250705.2086 | 2683779.6037 | 1250710.2201 | 2683779.082 | 1250712.9256
102 | 2683793.761 | 1250666.7679 | 2683792.0437 | 1250676.1705 | 2683789.6156 | 1250680.7729 | 2683788.5622 | 1250684.4986
103 | 2683791.5096 | 1250713.9245 | 2683800.7402 | 1250711.4197 | 2683802.3612 | 1250711.1599
104 | 2683681.7878 | 1250644.3447 | 2683683.0988 | 1250639.7264 | 2683685.7538 | 1250630.364
105 | 2683681.7878 | 1250644.3447 | 2683688.1323 | 1250646.1757
106 | 2683687.8978 | 1250622.8038 | 2683685.7538 | 1250630.364
107 | 2683837.7587 | 1250634.3635 | 2683836.7598 | 1250639.3308 | 2683836.0474 | 1250643.257 | 2683835.2729 | 1250646.7709 | 2683834.8406 | 1250648.5105 | 2683832.8945 | 1250649.9952 | 2683831.9555 | 1250650.7269 | 2683830.514 | 1250651.7629 | 2683828.2575 | 1250661.1619
108 | 2683822.3554 | 1250636.2533 | 2683826.3116 | 1250632.3667 | 2683828.7328 | 1250631.4559 | 2683831.9402 | 1250632.4891
109 | 2683837.7587 | 1250634.3635 | 2683831.9402 | 1250632.4891
110 | 2683837.7587 | 1250634.3635 | 2683851.1732 | 1250638.1672 | 2683854.3309 | 1250639.4841
111 | 2683854.3309 | 1250639.4841 | 2683867.5946 | 1250645.0157 | 2683874.9145 | 1250649.0786
112 | 2683734.7604 | 1250627.9583 | 2683741.1487 | 1250629.7579
113 | 2683734.7604 | 1250627.9583 | 2683734.7747 | 1250627.9076
114 | 2683719.0844 | 1250623.4335 | 2683724.4675 | 1250624.9551 | 2683724.4675 | 1250624.9551
115 | 2683712.4589 | 1250621.5608 | 2683719.0844 | 1250623.4335
116 | 2683734.7747 | 1250627.9076 | 2683735.7537 | 1250624.4475 | 2683725.4445 | 1250621.533 | 2683724.4675 | 1250624.9551
117 | 2683712.4589 | 1250621.5608 | 2683713.4995 | 1250617.9061 | 2683702.724 | 1250614.8627 | 2683701.6436 | 1250618.6649
118 | 2683710.4054 | 1250628.5036 | 2683711.1362 | 1250625.9454 | 2683712.4589 | 1250621.5608
119 | 2683696.312 | 1250617.3728 | 2683701.588 | 1250618.8608 | 2683701.6436 | 1250618.6649
120 | 2683690.0078 | 1250615.5948 | 2683696.312 | 1250617.3728
121 | 2683690.0078 | 1250615.5948 | 2683689.1761 | 1250618.3518 | 2683688.5017 | 1250620.6663 | 2683687.8978 | 1250622.8038
122 | 2683720.14 | 1250592.492 | 2683726.8868 | 1250594.3003
123 | 2683720.14 | 1250592.492 | 2683719.4615 | 1250595.0955 | 2683718.279 | 1250599.1707
124 | 2683720.14 | 1250592.492 | 2683721.144 | 1250588.759 | 2683717.03 | 1250587.6556 | 2683710.3137 | 1250585.8483 | 2683709.8173 | 1250585.7189
125 | 2683660.7647 | 1250806.8496 | 2683666.694 | 1250814.3622

## bus_geodata
| x | y | coords
0 | 2683675.8865 | 1250599.7145
1 | 2683683.8526 | 1250580.5723
2 | 2683669.2611 | 1250615.6353
3 | 2683655.4149 | 1250634.5208
4 | 2683652.0045 | 1250609.4436
5 | 2683639.4657 | 1250647.0204
6 | 2683647.0464 | 1250607.8938
7 | 2683632.4191 | 1250652.5429
8 | 2683643.9453 | 1250601.8636
9 | 2683621.7637 | 1250645.8875
10 | 2683656.8359 | 1250659.3704
11 | 2683677.2085 | 1250658.0125
12 | 2683678.7221 | 1250651.8737
13 | 2683670.2252 | 1250685.8742
14 | 2683634.6199 | 1250571.0641
15 | 2683698.6115 | 1250586.4057
16 | 2683696.4655 | 1250594.0255
17 | 2683704.2967 | 1250587.932
18 | 2683747.5322 | 1250865.6941
19 | 2683737.0682 | 1250856.1391
20 | 2683772.8121 | 1250849.9941
21 | 2683743.8793 | 1250594.918
22 | 2683742.7723 | 1250598.9943
23 | 2683736.0229 | 1250592.8087
24 | 2683720.3429 | 1250858.5379
25 | 2683734.0397 | 1250849.7924
26 | 2683714.3675 | 1250863.0903
27 | 2683697.8785 | 1250850.3706
28 | 2683744.3737 | 1250787.4132
29 | 2683742.5283 | 1250763.7552
30 | 2683744.7398 | 1250790.8876
31 | 2683775.2474 | 1250770.6035
32 | 2683595.9406 | 1250724.7044
33 | 2683611.7481 | 1250701.7957
34 | 2683598.6699 | 1250728.1677
35 | 2683586.6919 | 1250712.9857
36 | 2683620.7197 | 1250756.1107
37 | 2683617.7868 | 1250713.3709
38 | 2683640.6189 | 1250781.3239
39 | 2683632.7396 | 1250746.8156
40 | 2683729.3535 | 1250739.1427
41 | 2683706.0164 | 1250753.168
42 | 2683727.0635 | 1250769.9998
43 | 2683718.5217 | 1250679.7454
44 | 2683698.1808 | 1250674.0539
45 | 2683710.1916 | 1250712.8874
46 | 2683719.5352 | 1250828.0356
47 | 2683694.2923 | 1250601.2841
48 | 2683708.8853 | 1250589.1639
49 | 2683784.0221 | 1250843.0322
50 | 2683885.0075 | 1250702.0996
51 | 2683873.8541 | 1250709.4524
52 | 2683749.1473 | 1250600.7034
53 | 2683780.8132 | 1250634.6759
54 | 2683776.1385 | 1250650.9713
55 | 2683742.7539 | 1250599.0681
56 | 2683731.2891 | 1250591.5377
57 | 2683803.814 | 1250832.215
58 | 2683749.3843 | 1250740.0486
59 | 2683782.601 | 1250766.5705
60 | 2683899.783 | 1250663.8398
61 | 2683879.8017 | 1250655.7075
62 | 2683588.9425 | 1250673.1594
63 | 2683633.4756 | 1250701.2275
64 | 2683651.1207 | 1250794.6301
65 | 2683653.9598 | 1250730.4057
66 | 2683698.2323 | 1250750.545
67 | 2683720.8376 | 1250803.6234
68 | 2683726.1406 | 1250656.7944
69 | 2683726.2974 | 1250656.2599
70 | 2683700.5542 | 1250664.2356
71 | 2683688.7665 | 1250703.9448
72 | 2683733.1036 | 1250658.2226
73 | 2683720.1364 | 1250813.5665
74 | 2683655.4716 | 1250729.2366
75 | 2683665.4644 | 1250720.8714
76 | 2683678.4772 | 1250737.0672
77 | 2683686.8867 | 1250743.9125
78 | 2683834.9217 | 1250736.628
79 | 2683808.0474 | 1250752.6147
80 | 2683804.8728 | 1250754.3557
81 | 2683856.8194 | 1250685.6825
82 | 2683859.3958 | 1250672.5793
83 | 2683822.6761 | 1250684.4097
84 | 2683824.2131 | 1250678.0079
85 | 2683819.1526 | 1250690.1309
86 | 2683864.6713 | 1250658.5479
87 | 2683773.8648 | 1250731.0533
88 | 2683704.085 | 1250650.5086
89 | 2683693.9007 | 1250647.8405
90 | 2683710.6845 | 1250652.4186
91 | 2683777.5425 | 1250720.91
92 | 2683795.8449 | 1250653.4851
93 | 2683785.9361 | 1250693.7862
94 | 2683781.4185 | 1250705.2086
95 | 2683788.5622 | 1250684.4986
96 | 2683791.5096 | 1250713.9245
97 | 2683779.082 | 1250712.9256
98 | 2683793.761 | 1250666.7679
99 | 2683802.3612 | 1250711.1599
100 | 2683681.7878 | 1250644.3447
101 | 2683685.7538 | 1250630.364
102 | 2683688.1323 | 1250646.1757
103 | 2683716.5827 | 1250654.064
104 | 2683828.2575 | 1250661.1619
105 | 2683822.3554 | 1250636.2533
106 | 2683831.9402 | 1250632.4891
107 | 2683837.7587 | 1250634.3635
108 | 2683854.3309 | 1250639.4841
109 | 2683874.9145 | 1250649.0786
110 | 2683741.1487 | 1250629.7579
111 | 2683734.7604 | 1250627.9583
112 | 2683719.0844 | 1250623.4335
113 | 2683724.4675 | 1250624.9551
114 | 2683712.4589 | 1250621.5608
115 | 2683734.7747 | 1250627.9076
116 | 2683701.6436 | 1250618.6649
117 | 2683710.4054 | 1250628.5036
118 | 2683696.312 | 1250617.3728
119 | 2683690.0078 | 1250615.5948
120 | 2683726.8868 | 1250594.3003
121 | 2683720.14 | 1250592.492
122 | 2683718.279 | 1250599.1707
123 | 2683709.8173 | 1250585.7189
124 | 2683687.8978 | 1250622.8038
125 | 2683660.7647 | 1250806.8496
126 | 2683666.694 | 1250814.3622
127 | 2683718.5217 | 1250679.7454

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98436 | -0.30028 | 0.0053317 | 0.0013362
1 | 0.98424 | -0.30273 | 0.0065584 | 0.0016437
2 | 0.98455 | -0.29659 | 0 | 0
3 | 0.9852 | -0.28392 | 0.0045336 | 0.0011362
4 | 0.98427 | -0.30221 | 0.0021742 | 0.00054492
5 | 0.98583 | -0.27175 | 0.003691 | 0.00092505
6 | 0.98419 | -0.3036 | 0 | 0
7 | 0.98613 | -0.26579 | 0 | 0
8 | 0.98409 | -0.30555 | 0.00644 | 0.001614
9 | 0.98612 | -0.26605 | 0.0010532 | 0.00026396
10 | 0.98703 | -0.24845 | 0.0047116 | 0.0011809
11 | 0.98804 | -0.22884 | 0 | 0
12 | 0.98835 | -0.22268 | 0 | 0
13 | 0.98773 | -0.23483 | 0.011677 | 0.0029266
14 | 0.98378 | -0.31171 | 0.0084132 | 0.0021086
15 | 0.98703 | -0.2484 | 0 | 0
16 | 0.98717 | -0.24564 | 0 | 0
17 | 0.98693 | -0.25045 | 0.0046937 | 0.0011763
18 | 0.97938 | -0.39513 | 0 | 0
19 | 0.97956 | -0.39163 | 0 | 0
20 | 0.97904 | -0.40187 | 0.0041423 | 0.0010381
21 | 0.9865 | -0.25875 | 0 | 0
22 | 0.98649 | -0.25903 | 0 | 0
23 | 0.98653 | -0.25821 | 0.0010449 | 0.00026187
24 | 0.98029 | -0.37734 | 0 | 0
25 | 0.97928 | -0.39708 | 0.007508 | 0.0018817
26 | 0.98024 | -0.37836 | 0 | 0
27 | 0.98012 | -0.38074 | 0.0062572 | 0.0015682
28 | 0.97668 | -0.4479 | 0 | 0
29 | 0.97607 | -0.45986 | 0.0022204 | 0.00055649
30 | 0.97681 | -0.44546 | 0.009559 | 0.0023957
31 | 0.97488 | -0.48323 | 0.003591 | 0.00089999
32 | 0.98485 | -0.28985 | 0 | 0
33 | 0.98474 | -0.29198 | 0.0010163 | 0.00025471
34 | 0.98489 | -0.28904 | 0 | 0
35 | 0.98476 | -0.29168 | 0.0068332 | 0.0017126
36 | 0.98592 | -0.26909 | 0 | 0
37 | 0.98443 | -0.29814 | 0.019929 | 0.0049946
38 | 0.98545 | -0.27817 | 0.0043815 | 0.0010981
39 | 0.98658 | -0.25629 | 0.004815 | 0.0012068
40 | 0.9863 | -0.26091 | 0 | 0
41 | 0.98782 | -0.23165 | 0.0010212 | 0.00025595
42 | 0.9846 | -0.29384 | 0.0036487 | 0.00091444
43 | 0.99657 | -0.064734 | 0 | 0
44 | 0.99446 | -0.10486 | 0 | 0
45 | 1 | 0 | -0.44258 | -0.1135
46 | 0.98164 | -0.35123 | 0.0040949 | 0.0010263
47 | 0.98731 | -0.243 | 0.0025978 | 0.00065107
48 | 0.98686 | -0.25171 | 0.0010811 | 0.00027096
49 | 0.97894 | -0.40387 | 0.0041295 | 0.001035
50 | 0.97001 | -0.57937 | 0.0057938 | 0.0014521
51 | 0.97008 | -0.57793 | 0 | 0
52 | 0.98647 | -0.25935 | 0.002744 | 0.00068771
53 | 0.97368 | -0.50695 | 0.0044601 | 0.0011178
54 | 0.97375 | -0.50556 | 0 | 0
55 | 0.98649 | -0.25903 | 0.00094692 | 0.00023732
56 | 0.98655 | -0.2578 | 0.0010764 | 0.00026978
57 | 0.97885 | -0.40559 | 0.0041934 | 0.001051
58 | 0.97552 | -0.4707 | 0 | 0
59 | 0.97448 | -0.49113 | 0.0029854 | 0.00074822
60 | 0.97075 | -0.56472 | 0.00063022 | 0.00015795
61 | 0.97076 | -0.56447 | 0 | 0
62 | 0.98466 | -0.29359 | 0.0024541 | 0.00061506
63 | 0.98441 | -0.2985 | 0.0010205 | 0.00025576
64 | 0.98527 | -0.28163 | 0.0043352 | 0.0010865
65 | 0.98786 | -0.23142 | 0.0014768 | 0.00037013
66 | 0.98828 | -0.22298 | 0 | 0
67 | 0.98275 | -0.32961 | 0.032017 | 0.0080243
68 | 0.99151 | -0.16166 | 0.0010119 | 0.0002536
69 | 0.99151 | -0.16165 | 0 | 0
70 | 0.99335 | -0.12622 | 0 | 0
71 | 0.99205 | -0.15067 | 0.014501 | 0.0036342
72 | 0.99146 | -0.16264 | 0.0078859 | 0.0019764
73 | 0.98229 | -0.3386 | 0.0068525 | 0.0017174
74 | 0.98795 | -0.2296 | 0 | 0
75 | 0.98859 | -0.21722 | 0 | 0
76 | 0.98961 | -0.19751 | 0.0075344 | 0.0018883
77 | 0.98901 | -0.209 | 0.0014014 | 0.00035122
78 | 0.97274 | -0.52543 | 0.016843 | 0.0042212
79 | 0.97323 | -0.51573 | 0.013908 | 0.0034857
80 | 0.97334 | -0.51369 | 0.017573 | 0.0044043
81 | 0.97024 | -0.5748 | 0 | 0
82 | 0.97031 | -0.57337 | 0.0050186 | 0.0012578
83 | 0.97319 | -0.51645 | 0 | 0
84 | 0.97309 | -0.51849 | 0.0053196 | 0.0013332
85 | 0.9733 | -0.51437 | 0 | 0
86 | 0.97047 | -0.57036 | 0.0049754 | 0.001247
87 | 0.97486 | -0.48364 | 0.0026023 | 0.0006522
88 | 0.99179 | -0.15629 | 0.00099063 | 0.00024828
89 | 0.99001 | -0.19066 | 0.0012479 | 0.00031274
90 | 0.99171 | -0.15785 | 0.0029064 | 0.00072841
91 | 0.97462 | -0.48829 | 0 | 0
92 | 0.97383 | -0.50394 | 0 | 0
93 | 0.97412 | -0.49824 | 0 | 0
94 | 0.97428 | -0.49514 | 0 | 0
95 | 0.97402 | -0.50017 | 0.0031371 | 0.00078624
96 | 0.97402 | -0.50009 | 0 | 0
97 | 0.97445 | -0.49178 | 0.002635 | 0.0006604
98 | 0.97389 | -0.50284 | 0.0033193 | 0.00083191
99 | 0.97382 | -0.5042 | 0.012507 | 0.0031346
100 | 0.98881 | -0.21384 | 0.0022409 | 0.00056162
101 | 0.98821 | -0.22552 | 0.0028214 | 0.00070711
102 | 0.98943 | -0.20186 | 0.0029272 | 0.00073363
103 | 0.99165 | -0.15894 | 0.0010318 | 0.0002586
104 | 0.97284 | -0.52343 | 0.0052849 | 0.0013245
105 | 0.97183 | -0.54342 | 0.010437 | 0.0026158
106 | 0.97194 | -0.5412 | 0.010274 | 0.0025749
107 | 0.97206 | -0.53886 | 0 | 0
108 | 0.97148 | -0.5504 | 0.0098277 | 0.0024631
109 | 0.97092 | -0.5614 | 0.0097506 | 0.0024437
110 | 0.98695 | -0.24997 | 0.0053455 | 0.0013397
111 | 0.98698 | -0.24933 | 0 | 0
112 | 0.98713 | -0.24657 | 0.002781 | 0.00069698
113 | 0.98709 | -0.2473 | 0.00097707 | 0.00024488
114 | 0.98719 | -0.24533 | 0.00093192 | 0.00023356
115 | 0.98698 | -0.24933 | 0.00097471 | 0.00024428
116 | 0.98743 | -0.2407 | 0.0010761 | 0.00026971
117 | 0.98717 | -0.24568 | 0.0026605 | 0.00066679
118 | 0.9875 | -0.2392 | 0.0031046 | 0.00077809
119 | 0.98761 | -0.23711 | 0.0023107 | 0.00057912
120 | 0.98659 | -0.25703 | 0.0028142 | 0.0007053
121 | 0.98664 | -0.25595 | 0.00090374 | 0.0002265
122 | 0.98663 | -0.25627 | 0.0025521 | 0.00063961
123 | 0.98682 | -0.25258 | 0.0016077 | 0.00040294
124 | 0.9879 | -0.23145 | 0 | 0
125 | 0.98517 | -0.2836 | 0.0041116 | 0.0010305
126 | 0.98515 | -0.2841 | 0.0029277 | 0.00073376
127 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0065591 | 0.0016439 | -0.0065584 | -0.0016437 | 7.6438e-07 | 2.2566e-07 | 0.0099151 | 0.0099152 | 0.0099152 | 0.98436 | -0.30028 | 0.98424 | -0.30273 | 2.724
1 | -0.011891 | -0.0029802 | 0.011893 | 0.0029813 | 2.0893e-06 | 1.1179e-06 | 0.017975 | 0.017975 | 0.017975 | 0.98436 | -0.30028 | 0.98455 | -0.29659 | 4.9381
2 | -0.02893 | -0.0072539 | 0.028947 | 0.0072647 | 1.7487e-05 | 1.0881e-05 | 0.043725 | 0.043724 | 0.043725 | 0.98455 | -0.29659 | 0.9852 | -0.28392 | 12.0122
3 | 0.017037 | 0.0042726 | -0.017032 | -0.0042699 | 4.5613e-06 | 2.686e-06 | 0.02575 | 0.02575 | 0.02575 | 0.98455 | -0.29659 | 0.98427 | -0.30221 | 7.0742
4 | -0.033481 | -0.008401 | 0.0335 | 0.0084131 | 1.9434e-05 | 1.218e-05 | 0.050572 | 0.050572 | 0.050572 | 0.9852 | -0.28392 | 0.98583 | -0.27175 | 13.8933
5 | 0.014858 | 0.003725 | -0.014857 | -0.0037244 | 9.8293e-07 | 5.6306e-07 | 0.022463 | 0.022463 | 0.022463 | 0.98427 | -0.30221 | 0.98419 | -0.3036 | 6.1711
6 | -0.037191 | -0.0093382 | 0.037202 | 0.0093449 | 1.0582e-05 | 6.6585e-06 | 0.056143 | 0.056143 | 0.056143 | 0.98583 | -0.27175 | 0.98613 | -0.26579 | 15.4239
7 | 0.014857 | 0.0037244 | -0.014856 | -0.0037236 | 1.3789e-06 | 7.8989e-07 | 0.022463 | 0.022463 | 0.022463 | 0.98419 | -0.3036 | 0.98409 | -0.30555 | 6.1711
8 | 0.0010532 | 0.00026379 | -0.0010532 | -0.00026396 | 1.3057e-08 | -1.6752e-07 | 0.0015892 | 0.0015892 | 0.0015892 | 0.98613 | -0.26579 | 0.98612 | -0.26605 | 0.4366
9 | -0.038255 | -0.0096086 | 0.038287 | 0.0096286 | 3.1688e-05 | 1.9957e-05 | 0.057732 | 0.057732 | 0.057732 | 0.98613 | -0.26579 | 0.98703 | -0.24845 | 15.8605
10 | 0.0084157 | 0.0021096 | -0.0084132 | -0.0021086 | 2.4712e-06 | 1.0647e-06 | 0.012725 | 0.012725 | 0.012725 | 0.98409 | -0.30555 | 0.98378 | -0.31171 | 3.496
11 | -0.042998 | -0.010809 | 0.043039 | 0.010835 | 4.0296e-05 | 2.5462e-05 | 0.064835 | 0.064835 | 0.064835 | 0.98703 | -0.24845 | 0.98804 | -0.22884 | 17.8118
12 | -0.054719 | -0.013763 | 0.054735 | 0.013773 | 1.6107e-05 | 1.0228e-05 | 0.082427 | 0.082427 | 0.082427 | 0.98804 | -0.22884 | 0.98835 | -0.22268 | 22.6447
13 | 0.011681 | 0.0029284 | -0.011677 | -0.0029266 | 3.3334e-06 | 1.7656e-06 | 0.017592 | 0.017592 | 0.017592 | 0.98804 | -0.22884 | 0.98773 | -0.23483 | 4.8329
14 | -0.054735 | -0.013773 | 0.054758 | 0.013788 | 2.3124e-05 | 1.4683e-05 | 0.082427 | 0.082427 | 0.082427 | 0.98835 | -0.22268 | 0.98881 | -0.21384 | 22.6447
15 | -0.019471 | -0.0048814 | 0.019474 | 0.0048829 | 2.5582e-06 | 1.5361e-06 | 0.029354 | 0.029354 | 0.029354 | 0.98703 | -0.2484 | 0.98717 | -0.24564 | 8.0644
16 | 0.019471 | 0.0048814 | -0.019469 | -0.0048802 | 1.9021e-06 | 1.1421e-06 | 0.029354 | 0.029354 | 0.029354 | 0.98703 | -0.2484 | 0.98693 | -0.25045 | 8.0644
17 | -0.019474 | -0.0048829 | 0.019476 | 0.0048844 | 2.4483e-06 | 1.4701e-06 | 0.029354 | 0.029354 | 0.029354 | 0.98717 | -0.24564 | 0.98731 | -0.243 | 8.0644
18 | 0.014775 | 0.0037039 | -0.014775 | -0.0037034 | 8.8422e-07 | 5.052e-07 | 0.022278 | 0.022278 | 0.022278 | 0.98693 | -0.25045 | 0.98686 | -0.25171 | 6.1203
19 | -0.01247 | -0.0031265 | 0.012472 | 0.0031277 | 2.0803e-06 | 1.1369e-06 | 0.018947 | 0.018947 | 0.018947 | 0.97938 | -0.39513 | 0.97956 | -0.39163 | 5.2052
20 | 0.01247 | 0.0031265 | -0.012466 | -0.0031243 | 4.0062e-06 | 2.1896e-06 | 0.018947 | 0.018947 | 0.018947 | 0.97938 | -0.39513 | 0.97904 | -0.40187 | 5.2053
21 | -0.18366 | -0.046409 | 0.18378 | 0.046489 | 0.00012586 | 7.968e-05 | 0.27912 | 0.27912 | 0.27912 | 0.97956 | -0.39163 | 0.98029 | -0.37734 | 19.1704
22 | 0.17118 | 0.043281 | -0.17114 | -0.043253 | 4.4732e-05 | 2.8274e-05 | 0.26017 | 0.26017 | 0.26017 | 0.97956 | -0.39163 | 0.97928 | -0.39708 | 17.8691
23 | 0.008324 | 0.0020862 | -0.0083232 | -0.0020859 | 7.9205e-07 | 3.4099e-07 | 0.012651 | 0.012652 | 0.012652 | 0.97904 | -0.40187 | 0.97894 | -0.40387 | 3.4757
24 | 0.003691 | 0.00092495 | -0.003691 | -0.00092498 | 4.9098e-08 | -2.2506e-08 | 0.0055674 | 0.0055674 | 0.0055674 | 0.9865 | -0.25875 | 0.98649 | -0.25903 | 1.5295
25 | -0.003691 | -0.00092495 | 0.0036911 | 0.00092491 | 9.4553e-08 | -4.3348e-08 | 0.0055674 | 0.0055674 | 0.0055674 | 0.9865 | -0.25875 | 0.98653 | -0.25821 | 1.5295
26 | 0.00094692 | 0.00023732 | -0.00094692 | -0.00023732 | 5.7389e-11 | -9.3443e-10 | 0.0014283 | 0.0014283 | 0.0014283 | 0.98649 | -0.25903 | 0.98649 | -0.25903 | 0.3924
27 | 0.0027441 | 0.00068766 | -0.002744 | -0.00068771 | 4.2403e-08 | -5.7125e-08 | 0.0041391 | 0.0041391 | 0.0041391 | 0.98649 | -0.25903 | 0.98647 | -0.25935 | 1.1371
28 | -0.004736 | -0.0011868 | 0.0047361 | 0.0011868 | 9.3793e-08 | -2.5569e-09 | 0.0071434 | 0.0071434 | 0.0071434 | 0.98653 | -0.25821 | 0.98655 | -0.2578 | 1.9625
29 | -0.19004 | -0.048057 | 0.19028 | 0.048208 | 0.00023834 | 0.000151 | 0.28862 | 0.28862 | 0.28862 | 0.98029 | -0.37734 | 0.98164 | -0.35123 | 19.8228
30 | 0.0062582 | 0.0015685 | -0.0062579 | -0.0015684 | 3.045e-07 | 8.1444e-08 | 0.0094995 | 0.0094996 | 0.0094996 | 0.98029 | -0.37734 | 0.98024 | -0.37836 | 2.6098
31 | 0.16363 | 0.041371 | -0.16325 | -0.041132 | 0.00037877 | 0.00023913 | 0.24877 | 0.24877 | 0.24877 | 0.97928 | -0.39708 | 0.97681 | -0.44546 | 17.0856
32 | 0.0062579 | 0.0015684 | -0.0062572 | -0.0015682 | 7.0965e-07 | 1.8986e-07 | 0.0094996 | 0.0094997 | 0.0094997 | 0.98024 | -0.37836 | 0.98012 | -0.38074 | 2.6098
33 | 0.098598 | 0.024855 | -0.098542 | -0.02482 | 5.6357e-05 | 3.4737e-05 | 0.15027 | 0.15027 | 0.15027 | 0.97668 | -0.4479 | 0.97607 | -0.45986 | 10.3208
34 | -0.15367 | -0.038725 | 0.15369 | 0.038736 | 1.7966e-05 | 1.1323e-05 | 0.23421 | 0.23421 | 0.23421 | 0.97668 | -0.4479 | 0.97681 | -0.44546 | 16.0855
35 | 0.055076 | 0.01387 | -0.054983 | -0.013811 | 9.2871e-05 | 5.8998e-05 | 0.083935 | 0.083935 | 0.083935 | 0.97668 | -0.4479 | 0.97488 | -0.48323 | 23.059
36 | 0.096322 | 0.024264 | -0.096272 | -0.024233 | 4.9917e-05 | 3.0714e-05 | 0.14689 | 0.14689 | 0.14689 | 0.97607 | -0.45986 | 0.97552 | -0.4707 | 10.0884
37 | 0.051392 | 0.012911 | -0.051373 | -0.012899 | 1.9358e-05 | 1.2285e-05 | 0.078454 | 0.078454 | 0.078454 | 0.97488 | -0.48323 | 0.97448 | -0.49113 | 21.5532
38 | 0.003471 | 0.00086922 | -0.0034706 | -0.00086943 | 3.5104e-07 | -2.0843e-07 | 0.0052441 | 0.0052442 | 0.0052442 | 0.98485 | -0.28985 | 0.98474 | -0.29198 | 1.4407
39 | -0.010305 | -0.002582 | 0.010305 | 0.0025822 | 4.0042e-07 | 2.0021e-07 | 0.015569 | 0.015569 | 0.015569 | 0.98485 | -0.28985 | 0.98489 | -0.28904 | 4.2773
40 | 0.0068338 | 0.0017128 | -0.0068332 | -0.0017126 | 5.9684e-07 | 1.9203e-07 | 0.010325 | 0.010325 | 0.010325 | 0.98485 | -0.28985 | 0.98476 | -0.29168 | 2.8366
41 | 0.0024543 | 0.00061472 | -0.0024541 | -0.00061506 | 1.8881e-07 | -3.4485e-07 | 0.0037085 | 0.0037087 | 0.0037087 | 0.98474 | -0.29198 | 0.98466 | -0.29359 | 1.0189
42 | -0.031264 | -0.0078378 | 0.031293 | 0.0078564 | 2.9748e-05 | 1.8586e-05 | 0.047235 | 0.047235 | 0.047235 | 0.98489 | -0.28904 | 0.98592 | -0.26909 | 12.9767
43 | 0.020958 | 0.0052557 | -0.020949 | -0.0052501 | 9.0901e-06 | 5.5102e-06 | 0.031666 | 0.031666 | 0.031666 | 0.98489 | -0.28904 | 0.98443 | -0.29814 | 8.6994
44 | 0.015765 | 0.0039539 | -0.015759 | -0.00395 | 6.8201e-06 | 3.9554e-06 | 0.023795 | 0.023795 | 0.023795 | 0.98592 | -0.26909 | 0.98545 | -0.27817 | 6.5372
45 | -0.047059 | -0.01181 | 0.047088 | 0.011829 | 2.8748e-05 | 1.8205e-05 | 0.07103 | 0.07103 | 0.07103 | 0.98592 | -0.26909 | 0.98658 | -0.25629 | 19.5138
46 | 0.0010205 | 0.00025552 | -0.0010205 | -0.00025576 | 1.7702e-08 | -2.409e-07 | 0.0015425 | 0.0015426 | 0.0015426 | 0.98443 | -0.29814 | 0.98441 | -0.2985 | 0.42378
47 | 0.011377 | 0.0028519 | -0.011375 | -0.0028509 | 1.8761e-06 | 9.8477e-07 | 0.017179 | 0.01718 | 0.01718 | 0.98545 | -0.27817 | 0.98527 | -0.28163 | 4.7196
48 | -0.051903 | -0.013035 | 0.051964 | 0.013074 | 6.1661e-05 | 3.912e-05 | 0.078292 | 0.078292 | 0.078292 | 0.98658 | -0.25629 | 0.98786 | -0.23142 | 21.5089
49 | -0.23787 | -0.060515 | 0.23821 | 0.060729 | 0.00033596 | 0.0002136 | 0.3592 | 0.3592 | 0.3592 | 0.9863 | -0.26091 | 0.98782 | -0.23165 | 24.6702
50 | 0.23787 | 0.060515 | -0.2375 | -0.060276 | 0.00037679 | 0.00023956 | 0.3592 | 0.3592 | 0.3592 | 0.9863 | -0.26091 | 0.9846 | -0.29384 | 24.6702
51 | -0.23923 | -0.060985 | 0.23933 | 0.061049 | 0.00010021 | 6.3714e-05 | 0.36074 | 0.36074 | 0.36074 | 0.98782 | -0.23165 | 0.98828 | -0.22298 | 24.7758
52 | 0.23385 | 0.059361 | -0.23345 | -0.059106 | 0.00040164 | 0.00025531 | 0.35368 | 0.35369 | 0.35369 | 0.9846 | -0.29384 | 0.98275 | -0.32961 | 24.2916
53 | 0.43954 | 0.11261 | -0.43869 | -0.11207 | 0.00085284 | 0.00054472 | 0.65717 | 0.65717 | 0.65717 | 0.99657 | -0.064734 | 0.99446 | -0.10486 | 45.1353
54 | -0.43954 | -0.11261 | 0.44093 | 0.1135 | 0.0013836 | 0.00088371 | 0.65717 | 0.65717 | 0.65717 | 0.99657 | -0.064734 | 1 | 0 | 45.1353
55 | 0.12071 | 0.030572 | -0.12059 | -0.030493 | 0.00012373 | 7.9056e-05 | 0.18073 | 0.18073 | 0.18073 | 0.99446 | -0.10486 | 0.99335 | -0.12622 | 49.6521
56 | 0.31798 | 0.081495 | -0.31728 | -0.081046 | 0.0007045 | 0.00044917 | 0.47644 | 0.47644 | 0.47644 | 0.99446 | -0.10486 | 0.99205 | -0.15067 | 32.7224
57 | -0.19437 | -0.049234 | 0.19449 | 0.049309 | 0.00011801 | 7.4794e-05 | 0.29483 | 0.29483 | 0.29483 | 0.98164 | -0.35123 | 0.98229 | -0.3386 | 20.2491
58 | -0.022074 | -0.0055355 | 0.02208 | 0.0055392 | 6.2005e-06 | 3.7772e-06 | 0.03327 | 0.03327 | 0.03327 | 0.98731 | -0.243 | 0.98761 | -0.23711 | 9.14
59 | 0.013693 | 0.0034324 | -0.013693 | -0.0034321 | 5.7055e-07 | 3.1955e-07 | 0.020648 | 0.020648 | 0.020648 | 0.98686 | -0.25171 | 0.98682 | -0.25258 | 5.6724
60 | 0.0041937 | 0.0010509 | -0.0041934 | -0.001051 | 3.4386e-07 | -6.3606e-08 | 0.0063746 | 0.0063747 | 0.0063747 | 0.97894 | -0.40387 | 0.97885 | -0.40559 | 1.7513
61 | -0.0057938 | -0.0014521 | 0.0057942 | 0.0014521 | 3.9629e-07 | 8.8467e-08 | 0.0088877 | 0.0088877 | 0.0088877 | 0.97001 | -0.57937 | 0.97008 | -0.57793 | 2.4417
62 | -0.0057942 | -0.0014521 | 0.005795 | 0.0014523 | 8.6538e-07 | 1.9309e-07 | 0.0088877 | 0.0088875 | 0.0088877 | 0.97008 | -0.57793 | 0.97024 | -0.5748 | 2.4417
63 | -0.0044601 | -0.0011178 | 0.0044604 | 0.0011178 | 2.9535e-07 | -2.1844e-08 | 0.0068161 | 0.006816 | 0.0068161 | 0.97368 | -0.50695 | 0.97375 | -0.50556 | 1.8726
64 | -0.0044604 | -0.0011178 | 0.0044607 | 0.0011178 | 3.4509e-07 | -2.5567e-08 | 0.006816 | 0.0068159 | 0.006816 | 0.97375 | -0.50556 | 0.97383 | -0.50394 | 1.8725
65 | -0.0058125 | -0.0014566 | 0.0058127 | 0.0014566 | 2.1164e-07 | 4.1685e-08 | 0.008767 | 0.0087669 | 0.008767 | 0.98655 | -0.2578 | 0.98659 | -0.25703 | 2.4085
66 | 0.096272 | 0.024233 | -0.096212 | -0.024196 | 5.9536e-05 | 3.6634e-05 | 0.14689 | 0.14689 | 0.14689 | 0.97552 | -0.4707 | 0.97486 | -0.48364 | 10.0884
67 | 0.048387 | 0.012151 | -0.048335 | -0.012118 | 5.2014e-05 | 3.2973e-05 | 0.073895 | 0.073895 | 0.073895 | 0.97448 | -0.49113 | 0.97334 | -0.51369 | 20.3009
68 | -0.00063022 | -0.00015795 | 0.00063023 | 0.00015768 | 7.6218e-09 | -2.6441e-07 | 0.00096604 | 0.00096594 | 0.00096604 | 0.97075 | -0.56472 | 0.97076 | -0.56447 | 0.26539
69 | 0.015795 | 0.0039605 | -0.015791 | -0.0039579 | 4.4329e-06 | 2.5878e-06 | 0.024212 | 0.024212 | 0.024212 | 0.97076 | -0.56447 | 0.97047 | -0.57036 | 6.6517
70 | -0.016426 | -0.0041182 | 0.016428 | 0.0041196 | 2.3987e-06 | 1.4104e-06 | 0.025178 | 0.025178 | 0.025178 | 0.97076 | -0.56447 | 0.97092 | -0.5614 | 6.9171
71 | 0.0070401 | 0.0017644 | -0.0070394 | -0.0017642 | 6.5991e-07 | 2.2411e-07 | 0.010632 | 0.010632 | 0.010632 | 0.98527 | -0.28163 | 0.98517 | -0.2836 | 2.921
72 | -0.053441 | -0.013445 | 0.053446 | 0.013447 | 4.6462e-06 | 2.9491e-06 | 0.080517 | 0.080517 | 0.080517 | 0.98786 | -0.23142 | 0.98795 | -0.2296 | 22.12
73 | -0.23933 | -0.061049 | 0.23949 | 0.061151 | 0.00016168 | 0.0001028 | 0.36074 | 0.36074 | 0.36074 | 0.98828 | -0.22298 | 0.98901 | -0.209 | 24.7758
74 | 0.20143 | 0.051082 | -0.20134 | -0.051027 | 8.7049e-05 | 5.5206e-05 | 0.30521 | 0.30521 | 0.30521 | 0.98275 | -0.32961 | 0.98229 | -0.3386 | 20.962
75 | -0.0010119 | -0.0002536 | 0.0010119 | 0.00025359 | 4.8171e-10 | -6.8755e-09 | 0.0015186 | 0.0015186 | 0.0015186 | 0.99151 | -0.16166 | 0.99151 | -0.16165 | 0.41719
76 | -0.0088982 | -0.0022301 | 0.0088993 | 0.0022307 | 1.1511e-06 | 5.1465e-07 | 0.013354 | 0.013354 | 0.013354 | 0.99151 | -0.16165 | 0.99165 | -0.15894 | 3.6687
77 | 0.0078863 | 0.0019765 | -0.0078859 | -0.0019764 | 3.7209e-07 | 1.4678e-07 | 0.011835 | 0.011835 | 0.011835 | 0.99151 | -0.16165 | 0.99146 | -0.16264 | 3.2515
78 | 0.12059 | 0.030493 | -0.12041 | -0.030382 | 0.00017361 | 0.00011093 | 0.18073 | 0.18073 | 0.18073 | 0.99335 | -0.12622 | 0.99179 | -0.15629 | 49.6521
79 | 0.30278 | 0.077412 | -0.30209 | -0.076976 | 0.00068439 | 0.00043619 | 0.45469 | 0.45469 | 0.45469 | 0.99205 | -0.15067 | 0.98961 | -0.19751 | 31.2287
80 | -0.053446 | -0.013447 | 0.053477 | 0.013468 | 3.1629e-05 | 2.0076e-05 | 0.080517 | 0.080517 | 0.080517 | 0.98795 | -0.2296 | 0.98859 | -0.21722 | 22.12
81 | -0.053477 | -0.013468 | 0.053528 | 0.0135 | 5.0458e-05 | 3.2026e-05 | 0.080517 | 0.080517 | 0.080517 | 0.98859 | -0.21722 | 0.98961 | -0.19751 | 22.12
82 | 0.24103 | 0.061588 | -0.24089 | -0.061503 | 0.00013384 | 8.5098e-05 | 0.36284 | 0.36284 | 0.36284 | 0.98961 | -0.19751 | 0.98901 | -0.209 | 24.9206
83 | -0.016843 | -0.0042212 | 0.016851 | 0.0042258 | 7.7868e-06 | 4.5951e-06 | 0.025765 | 0.025765 | 0.025765 | 0.97274 | -0.52543 | 0.97323 | -0.51573 | 7.0782
84 | -0.030759 | -0.0077116 | 0.030762 | 0.0077134 | 3.003e-06 | 1.8769e-06 | 0.047029 | 0.047029 | 0.047029 | 0.97323 | -0.51573 | 0.97334 | -0.51369 | 12.9202
85 | -0.005795 | -0.0014523 | 0.0057954 | 0.0014524 | 3.9565e-07 | 8.8239e-08 | 0.0088875 | 0.0088875 | 0.0088875 | 0.97024 | -0.5748 | 0.97031 | -0.57337 | 2.4416
86 | -0.010814 | -0.0027102 | 0.010816 | 0.002711 | 1.5506e-06 | 8.0662e-07 | 0.016584 | 0.016584 | 0.016584 | 0.97031 | -0.57337 | 0.97047 | -0.57036 | 4.5559
87 | 0.067422 | 0.016936 | -0.067415 | -0.016932 | 6.5611e-06 | 3.8719e-06 | 0.1031 | 0.1031 | 0.1031 | 0.97319 | -0.51645 | 0.97309 | -0.51849 | 7.0812
88 | -0.067422 | -0.016936 | 0.067428 | 0.01694 | 6.6909e-06 | 3.9484e-06 | 0.1031 | 0.1031 | 0.1031 | 0.97319 | -0.51645 | 0.9733 | -0.51437 | 7.0812
89 | 0.062095 | 0.015599 | -0.062081 | -0.015591 | 1.4648e-05 | 8.5142e-06 | 0.094967 | 0.094968 | 0.094968 | 0.97309 | -0.51849 | 0.97284 | -0.52343 | 6.5225
90 | -0.067428 | -0.01694 | 0.067461 | 0.016959 | 3.2739e-05 | 1.9319e-05 | 0.1031 | 0.1031 | 0.1031 | 0.9733 | -0.51437 | 0.97382 | -0.5042 | 7.0811
91 | 0.09361 | 0.023544 | -0.093589 | -0.023531 | 2.0782e-05 | 1.2759e-05 | 0.14292 | 0.14292 | 0.14292 | 0.97486 | -0.48364 | 0.97462 | -0.48829 | 9.8156
92 | 0.10658 | 0.026915 | -0.10641 | -0.026803 | 0.00017523 | 0.00011192 | 0.15998 | 0.15998 | 0.15998 | 0.99179 | -0.15629 | 0.99001 | -0.19066 | 43.9518
93 | 0.012839 | 0.0032184 | -0.012838 | -0.0032179 | 9.56e-07 | 5.2319e-07 | 0.019263 | 0.019263 | 0.019263 | 0.99179 | -0.15629 | 0.99171 | -0.15785 | 5.2921
94 | 0.10516 | 0.026491 | -0.1051 | -0.026455 | 5.6283e-05 | 3.5944e-05 | 0.15811 | 0.15811 | 0.15811 | 0.99001 | -0.19066 | 0.98943 | -0.20186 | 43.4365
95 | 0.0099316 | 0.0024895 | -0.0099311 | -0.0024892 | 5.1485e-07 | 2.4974e-07 | 0.014902 | 0.014902 | 0.014902 | 0.99171 | -0.15785 | 0.99165 | -0.15894 | 4.094
96 | 0.093589 | 0.023531 | -0.093573 | -0.023522 | 1.557e-05 | 9.5598e-06 | 0.14292 | 0.14292 | 0.14292 | 0.97462 | -0.48829 | 0.97445 | -0.49178 | 9.8156
97 | -0.0044607 | -0.0011178 | 0.004461 | 0.0011177 | 2.3425e-07 | -1.7383e-08 | 0.0068159 | 0.0068159 | 0.0068159 | 0.97383 | -0.50394 | 0.97389 | -0.50284 | 1.8725
98 | -0.010919 | -0.0027368 | 0.010921 | 0.0027376 | 1.6095e-06 | 8.38e-07 | 0.01668 | 0.01668 | 0.01668 | 0.97412 | -0.49824 | 0.97428 | -0.49514 | 4.5824
99 | 0.010919 | 0.0027368 | -0.010918 | -0.0027363 | 1.007e-06 | 5.2434e-07 | 0.01668 | 0.01668 | 0.01668 | 0.97412 | -0.49824 | 0.97402 | -0.50017 | 4.5824
100 | 0.080003 | 0.020115 | -0.079984 | -0.020103 | 1.8896e-05 | 1.1421e-05 | 0.12221 | 0.12221 | 0.12221 | 0.97428 | -0.49514 | 0.97402 | -0.50009 | 8.3937
101 | -0.090924 | -0.022853 | 0.090938 | 0.022861 | 1.4622e-05 | 8.9555e-06 | 0.13889 | 0.13889 | 0.13889 | 0.97428 | -0.49514 | 0.97445 | -0.49178 | 9.5393
102 | 0.0077813 | 0.00195 | -0.0077803 | -0.0019496 | 9.8743e-07 | 4.0007e-07 | 0.011887 | 0.011888 | 0.011888 | 0.97402 | -0.50017 | 0.97389 | -0.50284 | 3.2658
103 | 0.079984 | 0.020103 | -0.079968 | -0.020094 | 1.5691e-05 | 9.4846e-06 | 0.12221 | 0.12221 | 0.12221 | 0.97402 | -0.50009 | 0.97382 | -0.5042 | 8.3937
104 | 0.04512 | 0.011334 | -0.045094 | -0.011318 | 2.5131e-05 | 1.5897e-05 | 0.067908 | 0.067908 | 0.067908 | 0.98881 | -0.21384 | 0.98821 | -0.22552 | 18.656
105 | -0.10212 | -0.025684 | 0.10218 | 0.025721 | 5.8503e-05 | 3.7357e-05 | 0.15371 | 0.15371 | 0.15371 | 0.98881 | -0.21384 | 0.98943 | -0.20186 | 42.2271
106 | 0.042273 | 0.010611 | -0.042261 | -0.010603 | 1.1942e-05 | 7.5425e-06 | 0.063659 | 0.06366 | 0.06366 | 0.98821 | -0.22552 | 0.9879 | -0.23145 | 17.4889
107 | 0.056796 | 0.014266 | -0.056754 | -0.01424 | 4.1793e-05 | 2.6015e-05 | 0.086884 | 0.086884 | 0.086884 | 0.97284 | -0.52343 | 0.97206 | -0.53886 | 11.9347
108 | -0.010437 | -0.0026158 | 0.010438 | 0.0026163 | 1.1016e-06 | 5.6245e-07 | 0.015981 | 0.015981 | 0.015981 | 0.97183 | -0.54342 | 0.97194 | -0.5412 | 4.3903
109 | -0.020712 | -0.0051912 | 0.020714 | 0.0051926 | 2.305e-06 | 1.3994e-06 | 0.03171 | 0.03171 | 0.03171 | 0.97194 | -0.5412 | 0.97206 | -0.53886 | 8.7114
110 | 0.03604 | 0.0090474 | -0.03602 | -0.0090349 | 1.9824e-05 | 1.2472e-05 | 0.055175 | 0.055175 | 0.055175 | 0.97206 | -0.53886 | 0.97148 | -0.5504 | 15.1579
111 | 0.026192 | 0.0065719 | -0.026179 | -0.0065634 | 1.3729e-05 | 8.505e-06 | 0.040122 | 0.040122 | 0.040122 | 0.97148 | -0.5504 | 0.97092 | -0.5614 | 11.0225
112 | -0.0053455 | -0.0013397 | 0.0053457 | 0.0013397 | 1.6166e-07 | 1.8644e-08 | 0.0080594 | 0.0080593 | 0.0080594 | 0.98695 | -0.24997 | 0.98698 | -0.24933 | 2.2141
113 | -0.0053457 | -0.0013397 | 0.0053457 | 0.0013397 | 1.2799e-09 | 1.4955e-10 | 0.0080593 | 0.0080593 | 0.0080593 | 0.98698 | -0.24933 | 0.98698 | -0.24933 | 2.2141
114 | 0.0072983 | 0.0018291 | -0.007298 | -0.001829 | 2.5391e-07 | 9.099e-08 | 0.011002 | 0.011002 | 0.011002 | 0.98713 | -0.24657 | 0.98709 | -0.2473 | 3.0224
115 | -0.010079 | -0.0025261 | 0.01008 | 0.0025264 | 5.9603e-07 | 2.9344e-07 | 0.015194 | 0.015194 | 0.015194 | 0.98713 | -0.24657 | 0.98719 | -0.24533 | 4.1741
116 | 0.006321 | 0.0015842 | -0.0063204 | -0.001584 | 6.0839e-07 | 1.6099e-07 | 0.0095288 | 0.0095288 | 0.0095288 | 0.98709 | -0.2473 | 0.98698 | -0.24933 | 2.6178
117 | -0.013672 | -0.0034267 | 0.013675 | 0.0034284 | 3.0181e-06 | 1.6893e-06 | 0.020609 | 0.020609 | 0.020609 | 0.98719 | -0.24533 | 0.98743 | -0.2407 | 5.6617
118 | 0.0026606 | 0.00066672 | -0.0026605 | -0.00066679 | 4.3658e-08 | -6.461e-08 | 0.0040103 | 0.0040103 | 0.0040103 | 0.98719 | -0.24533 | 0.98717 | -0.24568 | 1.1017
119 | -0.014752 | -0.0036981 | 0.014753 | 0.0036987 | 1.0536e-06 | 6.0158e-07 | 0.02223 | 0.02223 | 0.02223 | 0.98743 | -0.2407 | 0.9875 | -0.2392 | 6.1072
120 | -0.017857 | -0.0044768 | 0.017859 | 0.0044778 | 1.7785e-06 | 1.0544e-06 | 0.026908 | 0.026908 | 0.026908 | 0.9875 | -0.2392 | 0.98761 | -0.23711 | 7.3924
121 | -0.04225 | -0.010596 | 0.042261 | 0.010603 | 1.1413e-05 | 7.2082e-06 | 0.06366 | 0.06366 | 0.06366 | 0.98761 | -0.23711 | 0.9879 | -0.23145 | 17.4889
122 | -0.0086269 | -0.0021619 | 0.0086274 | 0.0021621 | 4.4345e-07 | 1.9461e-07 | 0.013011 | 0.013011 | 0.013011 | 0.98659 | -0.25703 | 0.98664 | -0.25595 | 3.5746
123 | 0.0025521 | 0.00063955 | -0.0025521 | -0.00063961 | 3.8517e-08 | -6.389e-08 | 0.003849 | 0.003849 | 0.003849 | 0.98664 | -0.25595 | 0.98663 | -0.25627 | 1.0574
124 | -0.012083 | -0.0030281 | 0.012085 | 0.0030292 | 1.9419e-06 | 1.0436e-06 | 0.018223 | 0.018223 | 0.018223 | 0.98664 | -0.25595 | 0.98682 | -0.25258 | 5.0064
125 | 0.0029278 | 0.00073368 | -0.0029277 | -0.00073376 | 7.0185e-08 | -7.6943e-08 | 0.0044222 | 0.0044222 | 0.0044222 | 0.98517 | -0.2836 | 0.98515 | -0.2841 | 1.2149

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.45408 | 0.11638

## res_load
| p_mw | q_mvar
0 | 0.0053317 | 0.0013362
1 | 0.0065584 | 0.0016437
2 | 0.0045336 | 0.0011362
3 | 0.0021742 | 0.00054492
4 | 0.003691 | 0.00092505
5 | 0.00644 | 0.001614
6 | 0.0010532 | 0.00026396
7 | 0.0047116 | 0.0011809
8 | 0.011677 | 0.0029266
9 | 0.0084132 | 0.0021086
10 | 0.0046937 | 0.0011763
11 | 0.0041423 | 0.0010381
12 | 0.0010449 | 0.00026187
13 | 0.007508 | 0.0018817
14 | 0.0062572 | 0.0015682
15 | 0.0022204 | 0.00055649
16 | 0.009559 | 0.0023957
17 | 0.003591 | 0.00089999
18 | 0.0010163 | 0.00025471
19 | 0.0068332 | 0.0017126
20 | 0.019929 | 0.0049946
21 | 0.0043815 | 0.0010981
22 | 0.004815 | 0.0012068
23 | 0.0010212 | 0.00025595
24 | 0.0036487 | 0.00091444
25 | 0.011502 | 0.0028827
26 | 0.0040949 | 0.0010263
27 | 0.0025978 | 0.00065107
28 | 0.0010811 | 0.00027096
29 | 0.0041295 | 0.001035
30 | 0.0057938 | 0.0014521
31 | 0.002744 | 0.00068771
32 | 0.0044601 | 0.0011178
33 | 0.00094692 | 0.00023732
34 | 0.0010764 | 0.00026978
35 | 0.0041934 | 0.001051
36 | 0.0029854 | 0.00074822
37 | 0.00063022 | 0.00015795
38 | 0.0024541 | 0.00061506
39 | 0.0010205 | 0.00025576
40 | 0.0043352 | 0.0010865
41 | 0.0014768 | 0.00037013
42 | 0.032017 | 0.0080243
43 | 0.0010119 | 0.0002536
44 | 0.014501 | 0.0036342
45 | 0.0078859 | 0.0019764
46 | 0.0068525 | 0.0017174
47 | 0.0075344 | 0.0018883
48 | 0.0014014 | 0.00035122
49 | 0.016843 | 0.0042212
50 | 0.013908 | 0.0034857
51 | 0.017573 | 0.0044043
52 | 0.0050186 | 0.0012578
53 | 0.0053196 | 0.0013332
54 | 0.0049754 | 0.001247
55 | 0.0026023 | 0.0006522
56 | 0.00099063 | 0.00024828
57 | 0.0012479 | 0.00031274
58 | 0.0029064 | 0.00072841
59 | 0.0031371 | 0.00078624
60 | 0.002635 | 0.0006604
61 | 0.0033193 | 0.00083191
62 | 0.012507 | 0.0031346
63 | 0.0022409 | 0.00056162
64 | 0.0028214 | 0.00070711
65 | 0.0029272 | 0.00073363
66 | 0.0010318 | 0.0002586
67 | 0.0052849 | 0.0013245
68 | 0.010437 | 0.0026158
69 | 0.010274 | 0.0025749
70 | 0.0098277 | 0.0024631
71 | 0.0097506 | 0.0024437
72 | 0.0053455 | 0.0013397
73 | 0.002781 | 0.00069698
74 | 0.00097707 | 0.00024488
75 | 0.00093192 | 0.00023356
76 | 0.00097471 | 0.00024428
77 | 0.0010761 | 0.00026971
78 | 0.0026605 | 0.00066679
79 | 0.0031046 | 0.00077809
80 | 0.0023107 | 0.00057912
81 | 0.0028142 | 0.0007053
82 | 0.00090374 | 0.0002265
83 | 0.0025521 | 0.00063961
84 | 0.0016077 | 0.00040294
85 | 0.0041116 | 0.0010305
86 | 0.0029277 | 0.00073376

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1