## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-504_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-504_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-504_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-504_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-504_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_261-504_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_261-504_0_4_node_53 | 0.4 | n |  | TRUE
7 | bus_LV_261-504_0_4_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_261-504_0_4_node_54 | 0.4 | n |  | TRUE
9 | bus_LV_261-504_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_261-504_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_261-504_0_4_node_127 | 0.4 | n |  | TRUE
12 | bus_LV_261-504_0_4_node_134 | 0.4 | n |  | TRUE
13 | bus_LV_261-504_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_261-504_0_4_node_132 | 0.4 | n |  | TRUE
15 | bus_LV_261-504_0_4_node_131 | 0.4 | n |  | TRUE
16 | bus_LV_261-504_0_4_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_261-504_0_4_node_135 | 0.4 | n |  | TRUE
18 | bus_LV_261-504_0_4_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_261-504_0_4_node_30 | 0.4 | n |  | TRUE
20 | bus_LV_261-504_0_4_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_261-504_0_4_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_261-504_0_4_node_106 | 0.4 | n |  | TRUE
23 | bus_LV_261-504_0_4_node_51 | 0.4 | n |  | TRUE
24 | bus_LV_261-504_0_4_node_35 | 0.4 | n |  | TRUE
25 | bus_LV_261-504_0_4_node_77 | 0.4 | n |  | TRUE
26 | bus_LV_261-504_0_4_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_261-504_0_4_node_65 | 0.4 | n |  | TRUE
28 | bus_LV_261-504_0_4_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_261-504_0_4_node_62 | 0.4 | n |  | TRUE
30 | bus_LV_261-504_0_4_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_261-504_0_4_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_261-504_0_4_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_261-504_0_4_node_89 | 0.4 | n |  | TRUE
34 | bus_LV_261-504_0_4_node_67 | 0.4 | n |  | TRUE
35 | bus_LV_261-504_0_4_node_66 | 0.4 | n |  | TRUE
36 | bus_LV_261-504_0_4_node_107 | 0.4 | n |  | TRUE
37 | bus_LV_261-504_0_4_node_21 | 0.4 | n |  | TRUE
38 | bus_LV_261-504_0_4_node_68 | 0.4 | n |  | TRUE
39 | bus_LV_261-504_0_4_node_69 | 0.4 | n |  | TRUE
40 | bus_LV_261-504_0_4_node_85 | 0.4 | n |  | TRUE
41 | bus_LV_261-504_0_4_node_84 | 0.4 | n |  | TRUE
42 | bus_LV_261-504_0_4_node_82 | 0.4 | n |  | TRUE
43 | bus_LV_261-504_0_4_node_28 | 0.4 | n |  | TRUE
44 | bus_LV_261-504_0_4_node_87 | 0.4 | n |  | TRUE
45 | bus_LV_261-504_0_4_node_94 | 0.4 | n |  | TRUE
46 | bus_LV_261-504_0_4_node_130 | 0.4 | n |  | TRUE
47 | bus_LV_261-504_0_4_node_33 | 0.4 | n |  | TRUE
48 | bus_LV_261-504_0_4_node_52 | 0.4 | n |  | TRUE
49 | bus_LV_261-504_0_4_node_55 | 0.4 | n |  | TRUE
50 | bus_LV_261-504_0_4_node_124 | 0.4 | n |  | TRUE
51 | bus_LV_261-504_0_4_node_36 | 0.4 | n |  | TRUE
52 | bus_LV_261-504_0_4_node_126 | 0.4 | n |  | TRUE
53 | bus_LV_261-504_0_4_node_37 | 0.4 | n |  | TRUE
54 | bus_LV_261-504_0_4_node_125 | 0.4 | n |  | TRUE
55 | bus_LV_261-504_0_4_node_38 | 0.4 | n |  | TRUE
56 | bus_LV_261-504_0_4_node_40 | 0.4 | n |  | TRUE
57 | bus_LV_261-504_0_4_node_42 | 0.4 | n |  | TRUE
58 | bus_LV_261-504_0_4_node_141 | 0.4 | n |  | TRUE
59 | bus_LV_261-504_0_4_node_39 | 0.4 | n |  | TRUE
60 | bus_LV_261-504_0_4_node_78 | 0.4 | n |  | TRUE
61 | bus_LV_261-504_0_4_node_47 | 0.4 | n |  | TRUE
62 | bus_LV_261-504_0_4_node_75 | 0.4 | n |  | TRUE
63 | bus_LV_261-504_0_4_node_50 | 0.4 | n |  | TRUE
64 | bus_LV_261-504_0_4_node_98 | 0.4 | n |  | TRUE
65 | bus_LV_261-504_0_4_node_41 | 0.4 | n |  | TRUE
66 | bus_LV_261-504_0_4_node_86 | 0.4 | n |  | TRUE
67 | bus_LV_261-504_0_4_node_99 | 0.4 | n |  | TRUE
68 | bus_LV_261-504_0_4_node_44 | 0.4 | n |  | TRUE
69 | bus_LV_261-504_0_4_node_58 | 0.4 | n |  | TRUE
70 | bus_LV_261-504_0_4_node_46 | 0.4 | n |  | TRUE
71 | bus_LV_261-504_0_4_node_48 | 0.4 | n |  | TRUE
72 | bus_LV_261-504_0_4_node_49 | 0.4 | n |  | TRUE
73 | bus_LV_261-504_0_4_node_123 | 0.4 | n |  | TRUE
74 | bus_LV_261-504_0_4_node_129 | 0.4 | n |  | TRUE
75 | bus_LV_261-504_0_4_node_128 | 0.4 | n |  | TRUE
76 | bus_LV_261-504_0_4_node_118 | 0.4 | n |  | TRUE
77 | bus_LV_261-504_0_4_node_142 | 0.4 | n |  | TRUE
78 | bus_LV_261-504_0_4_node_72 | 0.4 | n |  | TRUE
79 | bus_LV_261-504_0_4_node_74 | 0.4 | n |  | TRUE
80 | bus_LV_261-504_0_4_node_70 | 0.4 | n |  | TRUE
81 | bus_LV_261-504_0_4_node_136 | 0.4 | n |  | TRUE
82 | bus_LV_261-504_0_4_node_133 | 0.4 | n |  | TRUE
83 | bus_LV_261-504_0_4_node_137 | 0.4 | n |  | TRUE
84 | bus_LV_261-504_0_4_node_138 | 0.4 | n |  | TRUE
85 | bus_LV_261-504_0_4_node_105 | 0.4 | n |  | TRUE
86 | bus_LV_261-504_0_4_node_104 | 0.4 | n |  | TRUE
87 | bus_LV_261-504_0_4_node_76 | 0.4 | n |  | TRUE
88 | bus_LV_261-504_0_4_node_95 | 0.4 | n |  | TRUE
89 | bus_LV_261-504_0_4_node_90 | 0.4 | n |  | TRUE
90 | bus_LV_261-504_0_4_node_93 | 0.4 | n |  | TRUE
91 | bus_LV_261-504_0_4_node_92 | 0.4 | n |  | TRUE
92 | bus_LV_261-504_0_4_node_91 | 0.4 | n |  | TRUE
93 | bus_LV_261-504_0_4_node_83 | 0.4 | n |  | TRUE
94 | bus_LV_261-504_0_4_node_102 | 0.4 | n |  | TRUE
95 | bus_LV_261-504_0_4_node_103 | 0.4 | n |  | TRUE
96 | bus_LV_261-504_0_4_node_101 | 0.4 | n |  | TRUE
97 | bus_LV_261-504_0_4_node_110 | 0.4 | n |  | TRUE
98 | bus_LV_261-504_0_4_node_111 | 0.4 | n |  | TRUE
99 | bus_LV_261-504_0_4_node_116 | 0.4 | n |  | TRUE
100 | bus_LV_261-504_0_4_node_114 | 0.4 | n |  | TRUE
101 | bus_LV_261-504_0_4_node_115 | 0.4 | n |  | TRUE
102 | bus_LV_261-504_0_4_node_64 | 0.4 | n |  | TRUE
103 | bus_LV_261-504_0_4_node_100 | 0.4 | n |  | TRUE
104 | bus_LV_261-504_0_4_node_56 | 0.4 | n |  | TRUE
105 | bus_LV_261-504_0_4_node_108 | 0.4 | n |  | TRUE
106 | bus_LV_261-504_0_4_node_60 | 0.4 | n |  | TRUE
107 | bus_LV_261-504_0_4_node_57 | 0.4 | n |  | TRUE
108 | bus_LV_261-504_0_4_node_88 | 0.4 | n |  | TRUE
109 | bus_LV_261-504_0_4_node_140 | 0.4 | n |  | TRUE
110 | bus_LV_261-504_0_4_node_119 | 0.4 | n |  | TRUE
111 | bus_LV_261-504_0_4_node_59 | 0.4 | n |  | TRUE
112 | bus_LV_261-504_0_4_node_61 | 0.4 | n |  | TRUE
113 | bus_LV_261-504_0_4_node_96 | 0.4 | n |  | TRUE
114 | bus_LV_261-504_0_4_node_63 | 0.4 | n |  | TRUE
115 | bus_LV_261-504_0_4_node_97 | 0.4 | n |  | TRUE
116 | bus_LV_261-504_0_4_node_71 | 0.4 | n |  | TRUE
117 | bus_LV_261-504_0_4_node_73 | 0.4 | n |  | TRUE
118 | bus_LV_261-504_0_4_node_79 | 0.4 | n |  | TRUE
119 | bus_LV_261-504_0_4_node_80 | 0.4 | n |  | TRUE
120 | bus_LV_261-504_0_4_node_81 | 0.4 | n |  | TRUE
121 | bus_LV_261-504_0_4_node_120 | 0.4 | n |  | TRUE
122 | bus_LV_261-504_0_4_node_113 | 0.4 | n |  | TRUE
123 | bus_LV_261-504_0_4_node_112 | 0.4 | n |  | TRUE
124 | bus_LV_261-504_0_4_node_121 | 0.4 | n |  | TRUE
125 | bus_LV_261-504_0_4_node_109 | 0.4 | n |  | TRUE
126 | bus_LV_261-504_0_4_node_117 | 0.4 | n |  | TRUE
127 | bus_LV_261-504_0_4_node_122 | 0.4 | n |  | TRUE
128 | bus_LV_261-504_0_4_node_139 | 0.4 | n |  | TRUE
129 | bus_MV_530_0_node_181 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-504_0_4_load_0 | 0 | 0.0029814 | 0.0007472 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-504_0_4_load_1 | 1 | 0.0038093 | 0.00095469 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-504_0_4_load_3 | 3 | 0.0047409 | 0.0011882 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-504_0_4_load_4 | 4 | 0.01148 | 0.0028772 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-504_0_4_load_53 | 6 | 0.0036515 | 0.00091514 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-504_0_4_load_54 | 8 | 0.0036139 | 0.00090572 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-504_0_4_load_127 | 11 | 0.011977 | 0.0030016 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-504_0_4_load_134 | 12 | 0.0077264 | 0.0019364 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-504_0_4_load_132 | 14 | 0.008441 | 0.0021155 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-504_0_4_load_135 | 17 | 0.0069984 | 0.001754 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-504_0_4_load_106 | 22 | 0.013181 | 0.0033034 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-504_0_4_load_51 | 23 | 0.0029823 | 0.00074743 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-504_0_4_load_77 | 25 | 0.0080943 | 0.0020286 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-504_0_4_load_62 | 29 | 0.0065838 | 0.00165 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-504_0_4_load_89 | 33 | 0.0048069 | 0.0012047 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-504_0_4_load_67 | 34 | 0.011311 | 0.0028349 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-504_0_4_load_66 | 35 | 0.0064154 | 0.0016078 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-504_0_4_load_107 | 36 | 0.0048921 | 0.0012261 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-504_0_4_load_69 | 39 | 0.010285 | 0.0025776 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-504_0_4_load_85 | 40 | 0.0059274 | 0.0014856 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-504_0_4_load_84 | 41 | 0.013175 | 0.0033019 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-504_0_4_load_82 | 42 | 0.0016388 | 0.00041072 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-504_0_4_load_94 | 45 | 0.0041763 | 0.0010467 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-504_0_4_load_130 | 46 | 0.0077163 | 0.0019339 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-504_0_4_load_52 | 48 | 0.0031538 | 0.00079043 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-504_0_4_load_124 | 50 | 0.0047202 | 0.001183 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-504_0_4_load_126 | 52 | 0.0052091 | 0.0013055 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-504_0_4_load_125 | 54 | 0.0036431 | 0.00091304 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-504_0_4_load_141 | 58 | 0.0037499 | 0.00093982 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-504_0_4_load_78 | 60 | 0.0075648 | 0.0018959 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-504_0_4_load_75 | 62 | 0.0059161 | 0.0014827 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-504_0_4_load_98 | 64 | 0.0083125 | 0.0020833 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-504_0_4_load_86 | 66 | 0.0082868 | 0.0020769 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-504_0_4_load_99 | 67 | 0.0060329 | 0.001512 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-504_0_4_load_58 | 69 | 0.0060296 | 0.0015112 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-504_0_4_load_123 | 73 | 0.0047315 | 0.0011858 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-504_0_4_load_128 | 75 | 0.0075759 | 0.0018987 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-504_0_4_load_118 | 76 | 0.005923 | 0.0014845 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-504_0_4_load_142 | 77 | 0.0037493 | 0.00093968 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-504_0_4_load_70 | 80 | 0.0047751 | 0.0011968 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-504_0_4_load_136 | 81 | 0.0087634 | 0.0021963 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-504_0_4_load_137 | 83 | 0.0075696 | 0.0018971 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-504_0_4_load_105 | 85 | 0.0083882 | 0.0021023 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-504_0_4_load_104 | 86 | 0.0084613 | 0.0021206 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-504_0_4_load_76 | 87 | 0.005917 | 0.0014829 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-504_0_4_load_95 | 88 | 0.0065879 | 0.0016511 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-504_0_4_load_93 | 90 | 0.0037928 | 0.00095057 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-504_0_4_load_92 | 91 | 0.004531 | 0.0011356 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-504_0_4_load_91 | 92 | 0.0061675 | 0.0015457 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-504_0_4_load_103 | 95 | 0.0058674 | 0.0014705 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-504_0_4_load_101 | 96 | 0.006455 | 0.0016178 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-504_0_4_load_110 | 97 | 0.0051364 | 0.0012873 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-504_0_4_load_111 | 98 | 0.0047743 | 0.0011966 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-504_0_4_load_116 | 99 | 0.004685 | 0.0011742 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-504_0_4_load_114 | 100 | 0.0046309 | 0.0011606 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-504_0_4_load_64 | 102 | 0.0097656 | 0.0024475 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-504_0_4_load_100 | 103 | 0.0037507 | 0.00094 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-504_0_4_load_56 | 104 | 0.0031289 | 0.00078418 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-504_0_4_load_57 | 107 | 0.0058998 | 0.0014786 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-504_0_4_load_88 | 108 | 0.0083204 | 0.0020853 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-504_0_4_load_140 | 109 | 0.0079356 | 0.0019888 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-504_0_4_load_119 | 110 | 0.0057371 | 0.0014379 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-504_0_4_load_61 | 112 | 0.0060325 | 0.0015119 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-504_0_4_load_96 | 113 | 0.0069998 | 0.0017543 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-504_0_4_load_63 | 114 | 0.010886 | 0.0027282 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-504_0_4_load_97 | 115 | 0.0097546 | 0.0024447 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-504_0_4_load_71 | 116 | 0.0058665 | 0.0014703 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-504_0_4_load_79 | 118 | 0.0056911 | 0.0014263 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-504_0_4_load_81 | 120 | 0.0049214 | 0.0012334 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-504_0_4_load_120 | 121 | 0.0047783 | 0.0011976 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-504_0_4_load_112 | 123 | 0.0047779 | 0.0011975 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-504_0_4_load_121 | 124 | 0.0049234 | 0.0012339 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-504_0_4_load_109 | 125 | 0.0047754 | 0.0011968 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-504_0_4_load_117 | 126 | 0.0047059 | 0.0011794 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-504_0_4_load_122 | 127 | 0.0048513 | 0.0012159 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-504_0_4_load_139 | 128 | 0.0083346 | 0.0020888 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 128 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-504_0_4_line_0 |  | 0 | 1 | 0.018827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_261-504_0_4_line_1 |  | 0 | 2 | 0.019449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_261-504_0_4_line_2 |  | 1 | 3 | 0.0090238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_261-504_0_4_line_3 |  | 2 | 4 | 0.00938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_261-504_0_4_line_4 |  | 2 | 5 | 0.035008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_261-504_0_4_line_5 |  | 5 | 6 | 0.021608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_261-504_0_4_line_6 |  | 5 | 7 | 0.059937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_261-504_0_4_line_7 |  | 5 | 8 | 0.010735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_261-504_0_4_line_8 |  | 6 | 20 | 0.0098316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_261-504_0_4_line_9 |  | 7 | 17 | 0.003347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_261-504_0_4_line_10 |  | 7 | 9 | 0.05032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_261-504_0_4_line_11 |  | 8 | 49 | 0.011419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-504_0_4_line_12 |  | 9 | 10 | 0.046573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_261-504_0_4_line_13 |  | 9 | 11 | 0.006305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-504_0_4_line_14 |  | 10 | 12 | 0.004511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-504_0_4_line_15 |  | 11 | 51 | 0.003825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_261-504_0_4_line_16 |  | 13 | 14 | 0.013092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-504_0_4_line_17 |  | 13 | 15 | 0.031709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_261-504_0_4_line_18 |  | 13 | 16 | 0.035085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_261-504_0_4_line_19 |  | 15 | 81 | 0.009753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_261-504_0_4_line_20 |  | 15 | 19 | 0.031668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_261-504_0_4_line_21 |  | 16 | 24 | 0.016901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_261-504_0_4_line_22 |  | 16 | 25 | 0.022164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_261-504_0_4_line_23 |  | 18 | 19 | 0.02226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_261-504_0_4_line_24 |  | 18 | 20 | 0.040507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_261-504_0_4_line_25 |  | 18 | 21 | 0.038834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_261-504_0_4_line_26 |  | 18 | 22 | 0.022972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-504_0_4_line_27 |  | 19 | 46 | 0.024907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-504_0_4_line_28 |  | 20 | 23 | 0.032254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-504_0_4_line_29 |  | 21 | 34 | 0.0081137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-504_0_4_line_30 |  | 21 | 35 | 0.032805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_261-504_0_4_line_31 |  | 24 | 50 | 0.020814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-504_0_4_line_32 |  | 25 | 87 | 0.033464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_261-504_0_4_line_33 |  | 26 | 27 | 0.00644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-504_0_4_line_34 |  | 26 | 28 | 0.021184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-504_0_4_line_35 |  | 26 | 29 | 0.024493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-504_0_4_line_36 |  | 27 | 88 | 0.0045141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-504_0_4_line_37 |  | 28 | 40 | 0.0073181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-504_0_4_line_38 |  | 30 | 31 | 0.082101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-504_0_4_line_39 |  | 30 | 32 | 0.02292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_261-504_0_4_line_40 |  | 30 | 33 | 0.0043643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-504_0_4_line_41 |  | 31 | 36 | 0.023022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-504_0_4_line_42 |  | 32 | 41 | 0.022284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_261-504_0_4_line_43 |  | 32 | 42 | 0.0032584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_261-504_0_4_line_44 |  | 33 | 89 | 0.021407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-504_0_4_line_45 |  | 34 | 86 | 0.029894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_261-504_0_4_line_46 |  | 35 | 37 | 0.011044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_261-504_0_4_line_47 |  | 37 | 38 | 0.020421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_261-504_0_4_line_48 |  | 37 | 39 | 0.018368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_261-504_0_4_line_49 |  | 38 | 90 | 0.01515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_261-504_0_4_line_50 |  | 38 | 91 | 0.0090977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-504_0_4_line_51 |  | 39 | 92 | 0.033979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
52 | LV_261-504_0_4_line_52 |  | 40 | 93 | 0.020055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_261-504_0_4_line_53 |  | 42 | 93 | 0.0023186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_261-504_0_4_line_54 |  | 43 | 44 | 0.019815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-504_0_4_line_55 |  | 43 | 45 | 0.03939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-504_0_4_line_56 |  | 44 | 65 | 0.046739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-504_0_4_line_57 |  | 46 | 102 | 0.020578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-504_0_4_line_58 |  | 47 | 48 | 0.010722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-504_0_4_line_59 |  | 47 | 49 | 0.013315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_261-504_0_4_line_60 |  | 49 | 104 | 0.031237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-504_0_4_line_61 |  | 50 | 53 | 0.013575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_261-504_0_4_line_62 |  | 51 | 52 | 0.0064381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_261-504_0_4_line_63 |  | 53 | 54 | 0.0043304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-504_0_4_line_64 |  | 54 | 99 | 0.018111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_261-504_0_4_line_65 |  | 55 | 56 | 0.020752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_261-504_0_4_line_66 |  | 55 | 57 | 0.023631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-504_0_4_line_67 |  | 55 | 58 | 0.012041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_261-504_0_4_line_68 |  | 56 | 63 | 0.067139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-504_0_4_line_69 |  | 56 | 64 | 0.017598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-504_0_4_line_70 |  | 57 | 67 | 0.010854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-504_0_4_line_71 |  | 59 | 60 | 0.022082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_261-504_0_4_line_72 |  | 59 | 61 | 0.035949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_261-504_0_4_line_73 |  | 59 | 62 | 0.021213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_261-504_0_4_line_74 |  | 60 | 105 | 0.02624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
75 | LV_261-504_0_4_line_75 |  | 61 | 74 | 0.01815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_261-504_0_4_line_76 |  | 61 | 71 | 0.019168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-504_0_4_line_77 |  | 61 | 75 | 0.027022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-504_0_4_line_78 |  | 61 | 68 | 0.031997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_261-504_0_4_line_79 |  | 62 | 87 | 0.021637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_261-504_0_4_line_80 |  | 63 | 77 | 0.011299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_261-504_0_4_line_81 |  | 64 | 71 | 0.010133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-504_0_4_line_82 |  | 65 | 66 | 0.017712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_261-504_0_4_line_83 |  | 66 | 106 | 0.002748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_261-504_0_4_line_84 |  | 68 | 69 | 0.028426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_261-504_0_4_line_85 |  | 69 | 107 | 0.0010821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_261-504_0_4_line_86 |  | 70 | 71 | 0.078018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_261-504_0_4_line_87 |  | 70 | 72 | 0.00221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_261-504_0_4_line_88 |  | 70 | 73 | 0.010689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_261-504_0_4_line_89 |  | 72 | 76 | 0.0048689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_261-504_0_4_line_90 |  | 74 | 109 | 0.007593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_261-504_0_4_line_91 |  | 74 | 84 | 0.021002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_261-504_0_4_line_92 |  | 76 | 110 | 0.016087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_261-504_0_4_line_93 |  | 78 | 79 | 0.022834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_261-504_0_4_line_94 |  | 78 | 80 | 0.022315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_261-504_0_4_line_95 |  | 79 | 105 | 0.014329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_261-504_0_4_line_96 |  | 79 | 121 | 0.032149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_261-504_0_4_line_97 |  | 80 | 116 | 0.021812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_261-504_0_4_line_98 |  | 82 | 83 | 0.006635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_261-504_0_4_line_99 |  | 82 | 84 | 0.030427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_261-504_0_4_line_100 |  | 84 | 128 | 0.010253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_261-504_0_4_line_101 |  | 85 | 86 | 0.020059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_261-504_0_4_line_102 |  | 88 | 115 | 0.014286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_261-504_0_4_line_103 |  | 89 | 92 | 0.014666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
104 | LV_261-504_0_4_line_104 |  | 94 | 95 | 0.017802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_261-504_0_4_line_105 |  | 94 | 96 | 0.044184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_261-504_0_4_line_106 |  | 95 | 118 | 0.029368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_261-504_0_4_line_107 |  | 97 | 98 | 0.010988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_261-504_0_4_line_108 |  | 98 | 123 | 0.016908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_261-504_0_4_line_109 |  | 100 | 101 | 0.0031847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-504_0_4_line_110 |  | 101 | 126 | 0.016746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_261-504_0_4_line_111 |  | 101 | 122 | 0.029373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_261-504_0_4_line_112 |  | 102 | 114 | 0.020997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_261-504_0_4_line_113 |  | 103 | 104 | 0.0094622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_261-504_0_4_line_114 |  | 106 | 108 | 0.034616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_261-504_0_4_line_115 |  | 106 | 111 | 0.017817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_261-504_0_4_line_116 |  | 107 | 111 | 0.028152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_261-504_0_4_line_117 |  | 111 | 112 | 0.01203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_261-504_0_4_line_118 |  | 112 | 113 | 0.028485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_261-504_0_4_line_119 |  | 117 | 118 | 0.02402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_261-504_0_4_line_120 |  | 117 | 119 | 0.025747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_261-504_0_4_line_121 |  | 117 | 120 | 0.012967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_261-504_0_4_line_122 |  | 119 | 122 | 0.007463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_261-504_0_4_line_123 |  | 119 | 123 | 0.024074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_261-504_0_4_line_124 |  | 120 | 121 | 0.018702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_261-504_0_4_line_125 |  | 122 | 124 | 0.015208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_261-504_0_4_line_126 |  | 124 | 125 | 0.017598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_261-504_0_4_line_127 |  | 126 | 127 | 0.015549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-504_0_4_trafo_139 | 0.63 MVA 20/0.4 kV | 129 | 128 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2682528.2215 | 1250267.614 | 2682509.8175 | 1250263.6445
1 | 2682547.2338 | 1250271.7147 | 2682528.2215 | 1250267.614
2 | 2682500.9966 | 1250261.742 | 2682509.8175 | 1250263.6445
3 | 2682547.2338 | 1250271.7147 | 2682545.1961 | 1250280.8709
4 | 2682547.2338 | 1250271.7147 | 2682548.3468 | 1250268.2387 | 2682544.289 | 1250266.859 | 2682557.4148 | 1250266.5749 | 2682565.5797 | 1250266.3328 | 2682563.1005 | 1250261.1167
5 | 2682563.1005 | 1250261.1167 | 2682565.1317 | 1250258.9322 | 2682566.7433 | 1250254.8961 | 2682566.903 | 1250251.0177 | 2682566.2439 | 1250244.6816 | 2682565.2506 | 1250240.7792
6 | 2682563.1005 | 1250261.1167 | 2682565.5797 | 1250266.3328 | 2682567.2046 | 1250270.0026 | 2682569.5042 | 1250274.5603 | 2682576.2706 | 1250274.9882 | 2682583.5799 | 1250275.457 | 2682585.5638 | 1250275.5848 | 2682589.1618 | 1250275.824 | 2682590.4546 | 1250276.776 | 2682600.6077 | 1250279.5974 | 2682603.9869 | 1250266.835
7 | 2682563.1005 | 1250261.1167 | 2682560.8852 | 1250261.8864 | 2682558.7745 | 1250262.1905 | 2682554.2771 | 1250261.4829 | 2682552.601 | 1250261.1704
8 | 2682560.6725 | 1250232.1836 | 2682563.0153 | 1250235.2741 | 2682564.9912 | 1250239.7605 | 2682565.2506 | 1250240.7792
9 | 2682607.2288 | 1250267.703 | 2682603.9869 | 1250266.835
10 | 2682603.9869 | 1250266.835 | 2682600.6077 | 1250279.5974 | 2682604.337 | 1250280.7057 | 2682612.9684 | 1250283.2835 | 2682615.9268 | 1250280.1223 | 2682621.4778 | 1250281.6119 | 2682623.773 | 1250282.1554 | 2682625.8875 | 1250282.6631 | 2682630.3567 | 1250283.7706 | 2682632.8773 | 1250284.384 | 2682635.2173 | 1250284.9615
11 | 2682541.3938 | 1250258.9906 | 2682543.0643 | 1250259.3919 | 2682552.601 | 1250261.1704
12 | 2682635.2173 | 1250284.9615 | 2682637.4069 | 1250285.4924 | 2682640.4994 | 1250286.2472 | 2682644.9087 | 1250287.3206 | 2682646.406 | 1250287.6862 | 2682651.1538 | 1250288.8532 | 2682654.2251 | 1250290.0414 | 2682648.4326 | 1250311.2653 | 2682647.1665 | 1250315.9733
13 | 2682635.2173 | 1250284.9615 | 2682636.7974 | 1250278.8567
14 | 2682651.5527 | 1250317.0797 | 2682647.1665 | 1250315.9733
15 | 2682640.4979 | 1250279.8646 | 2682636.7974 | 1250278.8567
16 | 2682644.0373 | 1250218.2794 | 2682639.0268 | 1250206.1783
17 | 2682613.675 | 1250216.9218 | 2682617.3901 | 1250218.5081 | 2682631.1609 | 1250221.7913 | 2682635.7165 | 1250221.5769 | 2682640.7634 | 1250220.2463 | 2682644.0373 | 1250218.2794
18 | 2682644.0373 | 1250218.2794 | 2682647.3001 | 1250221.9831 | 2682651.8263 | 1250227.1279 | 2682655.5891 | 1250229.6266 | 2682661.0201 | 1250233.2272 | 2682668.0003 | 1250230.7783 | 2682672.5906 | 1250229.1634
19 | 2682613.675 | 1250216.9218 | 2682614.965 | 1250207.2548
20 | 2682613.675 | 1250216.9218 | 2682610.9507 | 1250215.7496 | 2682596.7347 | 1250210.2808 | 2682594.1654 | 1250208.8217 | 2682592.0035 | 1250206.8457 | 2682589.9177 | 1250203.7365 | 2682588.83 | 1250199.9852
21 | 2682672.5906 | 1250229.1634 | 2682675.3139 | 1250232.5705 | 2682678.5566 | 1250235.0065 | 2682685.9727 | 1250239.1908
22 | 2682672.5906 | 1250229.1634 | 2682671.0805 | 1250225.3839 | 2682670.2002 | 1250221.3798 | 2682670.1579 | 1250215.7528 | 2682671.9121 | 1250207.5721
23 | 2682567.5572 | 1250195.4188 | 2682575.8572 | 1250199.5709 | 2682588.83 | 1250199.9852
24 | 2682560.6725 | 1250232.1836 | 2682564.8379 | 1250227.4714 | 2682567.6225 | 1250224.319 | 2682570.1609 | 1250221.4967 | 2682569.3138 | 1250209.6872 | 2682568.4997 | 1250203.0932 | 2682567.5572 | 1250195.4188
25 | 2682567.5572 | 1250195.4188 | 2682568.1573 | 1250179.4487 | 2682568.3248 | 1250156.6007
26 | 2682567.5572 | 1250195.4188 | 2682546.0935 | 1250187.232
27 | 2682588.83 | 1250199.9852 | 2682587.4263 | 1250191.8152 | 2682584.6552 | 1250177.2102 | 2682584.4906 | 1250175.4658
28 | 2682560.6725 | 1250232.1836 | 2682558.3848 | 1250229.4831 | 2682554.3612 | 1250226.1912 | 2682548.5412 | 1250222.8633 | 2682533.1262 | 1250216.1536
29 | 2682568.3248 | 1250156.6007 | 2682567.3575 | 1250156.6651 | 2682560.2217 | 1250157.0141
30 | 2682568.3248 | 1250156.6007 | 2682567.2269 | 1250139.495 | 2682565.6285 | 1250123.9125
31 | 2682685.9727 | 1250239.1908 | 2682698.8081 | 1250243.4841 | 2682705.8759 | 1250245.2286
32 | 2682671.9121 | 1250207.5721 | 2682673.6143 | 1250199.6335 | 2682676.6687 | 1250187.4337 | 2682678.5959 | 1250175.3961 | 2682678.7242 | 1250174.833
33 | 2682575.8533 | 1250064.4483 | 2682569.5235 | 1250065.7278
34 | 2682569.5235 | 1250065.7278 | 2682567.7078 | 1250056.7847 | 2682566.1536 | 1250053.9943 | 2682564.7882 | 1250045.2355
35 | 2682569.5235 | 1250065.7278 | 2682574.3917 | 1250089.7323
36 | 2682575.8533 | 1250064.4483 | 2682580.2494 | 1250063.4229
37 | 2682564.7882 | 1250045.2355 | 2682563.6597 | 1250038.0049
38 | 2682511.0922 | 1250056.5296 | 2682512.4808 | 1250054.9477 | 2682516.6815 | 1250048.7905 | 2682521.0604 | 1250037.9657 | 2682526.3575 | 1250014.889 | 2682527.7579 | 1250005.9574 | 2682536.2038 | 1250006.7089 | 2682540.8231 | 1250008.4411 | 2682542.251 | 1250010.5403 | 2682544.4097 | 1250014.3844 | 2682546.0326 | 1250022.0015
39 | 2682546.0326 | 1250022.0015 | 2682544.4097 | 1250014.3844 | 2682552.2286 | 1250013.5259 | 2682559.4503 | 1250012.7259
40 | 2682546.0326 | 1250022.0015 | 2682546.9512 | 1250026.268
41 | 2682511.0922 | 1250056.5296 | 2682514.3562 | 1250059.0769 | 2682512.1431 | 1250061.8481 | 2682514.9675 | 1250065.6014 | 2682516.4646 | 1250069.7809 | 2682522.6609 | 1250069.9561
42 | 2682559.4503 | 1250012.7259 | 2682558.8021 | 1250006.1453 | 2682560.2007 | 1249993.5555 | 2682561.1871 | 1249990.7173
43 | 2682559.4503 | 1250012.7259 | 2682560.1028 | 1250015.9183
44 | 2682551.4574 | 1250047.1957 | 2682546.9512 | 1250026.268
45 | 2682560.2217 | 1250157.0141 | 2682530.3636 | 1250158.4746
46 | 2682564.5016 | 1250112.9262 | 2682565.6285 | 1250123.9125
47 | 2682544.3802 | 1250116.7377 | 2682564.5016 | 1250112.9262
48 | 2682564.5016 | 1250112.9262 | 2682560.8477 | 1250094.9251
49 | 2682529.4519 | 1250119.5653 | 2682544.3802 | 1250116.7377
50 | 2682544.3802 | 1250116.7377 | 2682546.2918 | 1250125.6323
51 | 2682554.2466 | 1250061.5938 | 2682557.6909 | 1250079.3731 | 2682560.8477 | 1250094.9251
52 | 2682560.5671 | 1250018.19 | 2682563.6597 | 1250038.0049
53 | 2682560.5671 | 1250018.19 | 2682560.1028 | 1250015.9183
54 | 2682612.1181 | 1249993.9902 | 2682595.2689 | 1249983.4809
55 | 2682595.2689 | 1249983.4809 | 2682593.0863 | 1249987.3089 | 2682588.446 | 1249984.9203 | 2682582.1713 | 1249996.8639 | 2682583.1667 | 1249997.4894 | 2682581.9473 | 1249999.9298 | 2682581.1985 | 1250003.2774 | 2682581.3755 | 1250006.8269 | 2682582.5499 | 1250009.7788 | 2682583.8095 | 1250011.5926
56 | 2682612.1181 | 1249993.9902 | 2682654.2242 | 1250004.4071 | 2682657.6177 | 1250005.2439
57 | 2682582.6475 | 1250154.9712 | 2682583.1422 | 1250161.1772 | 2682584.4906 | 1250175.4658
58 | 2682544.1499 | 1250245.9637 | 2682542.5517 | 1250242.5389 | 2682542.3407 | 1250239.2558 | 2682542.8442 | 1250235.6379
59 | 2682544.1499 | 1250245.9637 | 2682541.3938 | 1250258.9906
60 | 2682541.3938 | 1250258.9906 | 2682531.9576 | 1250256.7353 | 2682517.6375 | 1250253.3223 | 2682514.4244 | 1250252.5548 | 2682512.2497 | 1250252.0352 | 2682511.0056 | 1250251.7578
61 | 2682719.0554 | 1250248.4815 | 2682705.8759 | 1250245.2286
62 | 2682640.4979 | 1250279.8646 | 2682645.3377 | 1250284.1102
63 | 2682719.0554 | 1250248.4815 | 2682723.3267 | 1250249.1942
64 | 2682723.3267 | 1250249.1942 | 2682738.1802 | 1250251.673 | 2682741.2269 | 1250251.8496
65 | 2682706.1402 | 1250082.2667 | 2682689.4076 | 1250069.9241
66 | 2682680.8409 | 1250054.5821 | 2682687.6785 | 1250059.1142 | 2682683.1674 | 1250065.3226 | 2682689.4076 | 1250069.9241
67 | 2682696.8934 | 1250060.4771 | 2682689.4076 | 1250069.9241
68 | 2682706.1402 | 1250082.2667 | 2682709.6417 | 1250078.6129 | 2682737.0606 | 1250049.6629 | 2682720.5748 | 1250034.7884
69 | 2682706.1402 | 1250082.2667 | 2682702.44 | 1250087.1743 | 2682696.4832 | 1250096.9549
70 | 2682680.8409 | 1250054.5821 | 2682675.1042 | 1250050.1433 | 2682674.5347 | 1250046.5883
71 | 2682692.8026 | 1250134.475 | 2682714.0427 | 1250140.5147
72 | 2682678.5896 | 1250117.9645 | 2682681.178 | 1250113.7307 | 2682682.669 | 1250115.097 | 2682690.756 | 1250122.0705 | 2682688.9934 | 1250125.5596 | 2682685.9594 | 1250131.9665 | 2682692.8026 | 1250134.475
73 | 2682692.8026 | 1250134.475 | 2682689.473 | 1250141.5004 | 2682684.913 | 1250154.1413
74 | 2682739.0128 | 1250138.0113 | 2682735.9073 | 1250140.3474 | 2682731.0593 | 1250142.0255 | 2682726.358 | 1250142.3935 | 2682718.0932 | 1250141.6665 | 2682714.0427 | 1250140.5147
75 | 2682676.7447 | 1250134.3842 | 2682680.6105 | 1250125.7206 | 2682681.2004 | 1250123.4827 | 2682680.9933 | 1250121.5562 | 2682680.1319 | 1250119.4426 | 2682678.5896 | 1250117.9645
76 | 2682691.2123 | 1250105.6091 | 2682688.487 | 1250109.3739 | 2682683.3986 | 1250109.8811 | 2682681.178 | 1250113.7307 | 2682678.5896 | 1250117.9645
77 | 2682678.5896 | 1250117.9645 | 2682677.2561 | 1250116.6782 | 2682658.8927 | 1250099.4649
78 | 2682661.2207 | 1250095.4944 | 2682681.178 | 1250113.7307 | 2682678.5896 | 1250117.9645
79 | 2682678.7242 | 1250174.833 | 2682680.9122 | 1250165.2319 | 2682684.913 | 1250154.1413
80 | 2682712.6475 | 1250042.8616 | 2682720.5748 | 1250034.7884
81 | 2682691.2123 | 1250105.6091 | 2682696.4832 | 1250096.9549
82 | 2682657.6177 | 1250005.2439 | 2682653.2669 | 1250022.4136
83 | 2682652.5919 | 1250025.0774 | 2682653.2669 | 1250022.4136
84 | 2682661.2207 | 1250095.4944 | 2682656.558 | 1250090.3923 | 2682651.8897 | 1250083.5221 | 2682650.5488 | 1250081.135 | 2682648.9803 | 1250077.2102 | 2682647.2565 | 1250071.209
85 | 2682646.9821 | 1250070.163 | 2682647.0434 | 1250070.4671 | 2682647.2565 | 1250071.209
86 | 2682691.2123 | 1250105.6091 | 2682696.4643 | 1250109.0627 | 2682697.6684 | 1250109.8801 | 2682698.8188 | 1250110.7635 | 2682703.8778 | 1250113.9809 | 2682708.6556 | 1250105.975 | 2682723.4565 | 1250085.7887 | 2682728.7857 | 1250079.9254 | 2682743.6808 | 1250094.0883
87 | 2682743.6808 | 1250094.0883 | 2682745.4208 | 1250095.458
88 | 2682743.6808 | 1250094.0883 | 2682751.0737 | 1250086.3684
89 | 2682745.4208 | 1250095.458 | 2682741.9489 | 1250098.8714
90 | 2682669.9677 | 1250130.9205 | 2682676.7447 | 1250134.3842
91 | 2682676.7447 | 1250134.3842 | 2682674.1104 | 1250140.2852 | 2682669.1855 | 1250153.9711
92 | 2682730.4777 | 1250110.1492 | 2682741.9489 | 1250098.8714
93 | 2682750.6961 | 1250129.6682 | 2682769.2081 | 1250116.2277
94 | 2682769.2081 | 1250116.2277 | 2682784.3282 | 1250132.6399
95 | 2682750.6961 | 1250129.6682 | 2682739.0128 | 1250138.0113
96 | 2682750.6961 | 1250129.6682 | 2682753.466 | 1250132.9871 | 2682752.4388 | 1250136.2529 | 2682751.3834 | 1250138.8401 | 2682749.5835 | 1250142.8402 | 2682749.7245 | 1250146.2558 | 2682751.2686 | 1250149.224 | 2682753.7332 | 1250151.6936 | 2682759.7019 | 1250155.2911
97 | 2682800.705 | 1250146.6457 | 2682789.3496 | 1250139.0815 | 2682784.3282 | 1250132.6399
98 | 2682658.1141 | 1250182.3156 | 2682651.8171 | 1250180.1706
99 | 2682658.1141 | 1250182.3156 | 2682661.5728 | 1250173.6018 | 2682666.1456 | 1250162.4239 | 2682669.1855 | 1250153.9711
100 | 2682659.5094 | 1250150.5003 | 2682669.1855 | 1250153.9711
101 | 2682510.3283 | 1250159.4546 | 2682530.3636 | 1250158.4746
102 | 2682594.1617 | 1250060.178 | 2682580.2494 | 1250063.4229
103 | 2682551.4574 | 1250047.1957 | 2682554.2466 | 1250061.5938
104 | 2682829.8853 | 1250213.6587 | 2682828.8176 | 1250210.1078 | 2682828.8781 | 1250204.1598 | 2682829.8972 | 1250198.7701 | 2682827.6213 | 1250197.3928
105 | 2682829.8853 | 1250213.6587 | 2682865.7443 | 1250187.8454
106 | 2682827.6213 | 1250197.3928 | 2682827.6213 | 1250197.3928 | 2682822.7128 | 1250198.0024 | 2682810.7576 | 1250191.2304 | 2682807.4831 | 1250187.8266 | 2682806.7158 | 1250182.7676 | 2682806.0813 | 1250182.2146
107 | 2682799.9936 | 1250218.0666 | 2682794.3567 | 1250218.3881 | 2682789.0167 | 1250218.547
108 | 2682782.7465 | 1250203.6817 | 2682784.5105 | 1250214.1364 | 2682789.0167 | 1250218.547
109 | 2682747.4967 | 1250220.3353 | 2682748.4199 | 1250223.3832
110 | 2682747.4967 | 1250220.3353 | 2682741.2204 | 1250216.1779 | 2682732.4447 | 1250213.357
111 | 2682747.4967 | 1250220.3353 | 2682747.2952 | 1250215.3065 | 2682748.2716 | 1250209.7271 | 2682751.7583 | 1250202.2591 | 2682756.6965 | 1250196.824 | 2682759.0949 | 1250194.8449
112 | 2682580.6898 | 1250134.0673 | 2682581.8634 | 1250145.1364 | 2682582.6475 | 1250154.9712
113 | 2682511.0056 | 1250251.7578 | 2682502.7285 | 1250249.9122 | 2682501.7701 | 1250249.6989
114 | 2682652.5919 | 1250025.0774 | 2682670.1305 | 1250029.9923 | 2682673.4282 | 1250030.1161 | 2682676.8053 | 1250025.6377 | 2682680.1078 | 1250018.9121
115 | 2682648.1306 | 1250042.328 | 2682652.5919 | 1250025.0774
116 | 2682648.1306 | 1250042.328 | 2682646.5152 | 1250050.4226 | 2682645.6924 | 1250057.9834 | 2682645.8853 | 1250064.7244 | 2682646.9821 | 1250070.163
117 | 2682648.1306 | 1250042.328 | 2682636.4689 | 1250039.3744
118 | 2682609.9211 | 1250031.5371 | 2682620.1084 | 1250034.4427 | 2682636.6762 | 1250038.5878 | 2682636.4689 | 1250039.3744 | 2682636.4689 | 1250039.3744
119 | 2682784.461 | 1250173.3832 | 2682788.3224 | 1250173.148 | 2682796.5652 | 1250176.5212 | 2682802.1135 | 1250178.7559 | 2682806.0813 | 1250182.2146
120 | 2682764.4453 | 1250189.6269 | 2682766.1676 | 1250187.9385 | 2682775.7848 | 1250180.4895 | 2682784.461 | 1250173.3832
121 | 2682784.461 | 1250173.3832 | 2682782.9141 | 1250171.1599 | 2682776.5562 | 1250163.1096 | 2682776.5562 | 1250163.1096
122 | 2682764.4453 | 1250189.6269 | 2682759.0949 | 1250194.8449
123 | 2682764.4453 | 1250189.6269 | 2682779.135 | 1250203.8648 | 2682782.7465 | 1250203.6817
124 | 2682759.7019 | 1250155.2911 | 2682760.0223 | 1250155.4842 | 2682761.2566 | 1250156.302 | 2682772.3596 | 1250160.3156 | 2682776.5562 | 1250163.1096
125 | 2682759.0949 | 1250194.8449 | 2682753.3927 | 1250186.8705 | 2682748.8741 | 1250183.9045
126 | 2682733.0932 | 1250176.154 | 2682738.4927 | 1250178.4896 | 2682747.8714 | 1250183.2463 | 2682748.8741 | 1250183.9045
127 | 2682717.6418 | 1250208.5988 | 2682732.4447 | 1250213.357

## bus_geodata
| x | y | coords
0 | 2682528.2215 | 1250267.614
1 | 2682509.8175 | 1250263.6445
2 | 2682547.2338 | 1250271.7147
3 | 2682500.9966 | 1250261.742
4 | 2682545.1961 | 1250280.8709
5 | 2682563.1005 | 1250261.1167
6 | 2682565.2506 | 1250240.7792
7 | 2682603.9869 | 1250266.835
8 | 2682552.601 | 1250261.1704
9 | 2682635.2173 | 1250284.9615
10 | 2682647.1665 | 1250315.9733
11 | 2682636.7974 | 1250278.8567
12 | 2682651.5527 | 1250317.0797
13 | 2682644.0373 | 1250218.2794
14 | 2682639.0268 | 1250206.1783
15 | 2682613.675 | 1250216.9218
16 | 2682672.5906 | 1250229.1634
17 | 2682607.2288 | 1250267.703
18 | 2682567.5572 | 1250195.4188
19 | 2682588.83 | 1250199.9852
20 | 2682560.6725 | 1250232.1836
21 | 2682568.3248 | 1250156.6007
22 | 2682546.0935 | 1250187.232
23 | 2682533.1262 | 1250216.1536
24 | 2682685.9727 | 1250239.1908
25 | 2682671.9121 | 1250207.5721
26 | 2682569.5235 | 1250065.7278
27 | 2682575.8533 | 1250064.4483
28 | 2682564.7882 | 1250045.2355
29 | 2682574.3917 | 1250089.7323
30 | 2682546.0326 | 1250022.0015
31 | 2682511.0922 | 1250056.5296
32 | 2682559.4503 | 1250012.7259
33 | 2682546.9512 | 1250026.268
34 | 2682560.2217 | 1250157.0141
35 | 2682565.6285 | 1250123.9125
36 | 2682522.6609 | 1250069.9561
37 | 2682564.5016 | 1250112.9262
38 | 2682544.3802 | 1250116.7377
39 | 2682560.8477 | 1250094.9251
40 | 2682563.6597 | 1250038.0049
41 | 2682561.1871 | 1249990.7173
42 | 2682560.1028 | 1250015.9183
43 | 2682595.2689 | 1249983.4809
44 | 2682612.1181 | 1249993.9902
45 | 2682583.8095 | 1250011.5926
46 | 2682584.4906 | 1250175.4658
47 | 2682544.1499 | 1250245.9637
48 | 2682542.8442 | 1250235.6379
49 | 2682541.3938 | 1250258.9906
50 | 2682705.8759 | 1250245.2286
51 | 2682640.4979 | 1250279.8646
52 | 2682645.3377 | 1250284.1102
53 | 2682719.0554 | 1250248.4815
54 | 2682723.3267 | 1250249.1942
55 | 2682689.4076 | 1250069.9241
56 | 2682706.1402 | 1250082.2667
57 | 2682680.8409 | 1250054.5821
58 | 2682696.8934 | 1250060.4771
59 | 2682692.8026 | 1250134.475
60 | 2682714.0427 | 1250140.5147
61 | 2682678.5896 | 1250117.9645
62 | 2682684.913 | 1250154.1413
63 | 2682720.5748 | 1250034.7884
64 | 2682696.4832 | 1250096.9549
65 | 2682657.6177 | 1250005.2439
66 | 2682653.2669 | 1250022.4136
67 | 2682674.5347 | 1250046.5883
68 | 2682661.2207 | 1250095.4944
69 | 2682647.2565 | 1250071.209
70 | 2682743.6808 | 1250094.0883
71 | 2682691.2123 | 1250105.6091
72 | 2682745.4208 | 1250095.458
73 | 2682751.0737 | 1250086.3684
74 | 2682676.7447 | 1250134.3842
75 | 2682658.8927 | 1250099.4649
76 | 2682741.9489 | 1250098.8714
77 | 2682712.6475 | 1250042.8616
78 | 2682769.2081 | 1250116.2277
79 | 2682750.6961 | 1250129.6682
80 | 2682784.3282 | 1250132.6399
81 | 2682614.965 | 1250207.2548
82 | 2682658.1141 | 1250182.3156
83 | 2682651.8171 | 1250180.1706
84 | 2682669.1855 | 1250153.9711
85 | 2682510.3283 | 1250159.4546
86 | 2682530.3636 | 1250158.4746
87 | 2682678.7242 | 1250174.833
88 | 2682580.2494 | 1250063.4229
89 | 2682551.4574 | 1250047.1957
90 | 2682529.4519 | 1250119.5653
91 | 2682546.2918 | 1250125.6323
92 | 2682554.2466 | 1250061.5938
93 | 2682560.5671 | 1250018.19
94 | 2682829.8853 | 1250213.6587
95 | 2682827.6213 | 1250197.3928
96 | 2682865.7443 | 1250187.8454
97 | 2682799.9936 | 1250218.0666
98 | 2682789.0167 | 1250218.547
99 | 2682741.2269 | 1250251.8496
100 | 2682748.4199 | 1250223.3832
101 | 2682747.4967 | 1250220.3353
102 | 2682582.6475 | 1250154.9712
103 | 2682501.7701 | 1250249.6989
104 | 2682511.0056 | 1250251.7578
105 | 2682739.0128 | 1250138.0113
106 | 2682652.5919 | 1250025.0774
107 | 2682646.9821 | 1250070.163
108 | 2682680.1078 | 1250018.9121
109 | 2682669.9677 | 1250130.9205
110 | 2682730.4777 | 1250110.1492
111 | 2682648.1306 | 1250042.328
112 | 2682636.4689 | 1250039.3744
113 | 2682609.9211 | 1250031.5371
114 | 2682580.6898 | 1250134.0673
115 | 2682594.1617 | 1250060.178
116 | 2682800.705 | 1250146.6457
117 | 2682784.461 | 1250173.3832
118 | 2682806.0813 | 1250182.2146
119 | 2682764.4453 | 1250189.6269
120 | 2682776.5562 | 1250163.1096
121 | 2682759.7019 | 1250155.2911
122 | 2682759.0949 | 1250194.8449
123 | 2682782.7465 | 1250203.6817
124 | 2682748.8741 | 1250183.9045
125 | 2682733.0932 | 1250176.154
126 | 2682732.4447 | 1250213.357
127 | 2682717.6418 | 1250208.5988
128 | 2682659.5094 | 1250150.5003
129 | 2682669.1855 | 1250153.9711

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9746 | -0.48938 | 0.0029814 | 0.0007472
1 | 0.97445 | -0.49233 | 0.0038093 | 0.00095469
2 | 0.97481 | -0.48526 | 0 | 0
3 | 0.97441 | -0.49312 | 0.0047409 | 0.0011882
4 | 0.97471 | -0.48724 | 0.01148 | 0.0028772
5 | 0.97555 | -0.4705 | 0 | 0
6 | 0.97693 | -0.4434 | 0.0036515 | 0.00091514
7 | 0.97377 | -0.5056 | 0 | 0
8 | 0.97542 | -0.47318 | 0.0036139 | 0.00090572
9 | 0.9726 | -0.52867 | 0 | 0
10 | 0.97227 | -0.5353 | 0 | 0
11 | 0.9725 | -0.53066 | 0.011977 | 0.0030016
12 | 0.97224 | -0.53594 | 0.0077264 | 0.0019364
13 | 0.9835 | -0.31534 | 0 | 0
14 | 0.9834 | -0.31734 | 0.008441 | 0.0021155
15 | 0.98174 | -0.34944 | 0 | 0
16 | 0.98551 | -0.27643 | 0 | 0
17 | 0.97375 | -0.50603 | 0.0069984 | 0.001754
18 | 0.97901 | -0.40269 | 0 | 0
19 | 0.98005 | -0.38236 | 0 | 0
20 | 0.9776 | -0.43044 | 0 | 0
21 | 0.978 | -0.42262 | 0 | 0
22 | 0.97873 | -0.4082 | 0.013181 | 0.0033034
23 | 0.97751 | -0.43219 | 0.0029823 | 0.00074743
24 | 0.98544 | -0.27775 | 0 | 0
25 | 0.98685 | -0.25063 | 0.0080943 | 0.0020286
26 | 0.97194 | -0.54169 | 0 | 0
27 | 0.97184 | -0.54364 | 0 | 0
28 | 0.9724 | -0.53274 | 0 | 0
29 | 0.97179 | -0.54467 | 0.0065838 | 0.00165
30 | 0.97418 | -0.49752 | 0 | 0
31 | 0.97381 | -0.50491 | 0 | 0
32 | 0.97325 | -0.51593 | 0 | 0
33 | 0.97438 | -0.49363 | 0.0048069 | 0.0012047
34 | 0.97778 | -0.42678 | 0.011311 | 0.0028349
35 | 0.97735 | -0.43527 | 0.0064154 | 0.0016078
36 | 0.9737 | -0.50698 | 0.0048921 | 0.0012261
37 | 0.97715 | -0.43921 | 0 | 0
38 | 0.97699 | -0.44231 | 0 | 0
39 | 0.97675 | -0.44701 | 0.010285 | 0.0025776
40 | 0.97255 | -0.52964 | 0.0059274 | 0.0014856
41 | 0.97297 | -0.52133 | 0.013175 | 0.0033019
42 | 0.97315 | -0.51775 | 0.0016388 | 0.00041072
43 | 0.99059 | -0.17997 | 0 | 0
44 | 0.99066 | -0.1785 | 0 | 0
45 | 0.99044 | -0.18289 | 0.0041763 | 0.0010467
46 | 0.9794 | -0.39519 | 0.0077163 | 0.0019339
47 | 0.97527 | -0.47605 | 0 | 0
48 | 0.97524 | -0.47667 | 0.0031538 | 0.00079043
49 | 0.97531 | -0.47528 | 0 | 0
50 | 0.98519 | -0.28262 | 0.0047202 | 0.001183
51 | 0.97248 | -0.53103 | 0 | 0
52 | 0.97245 | -0.53165 | 0.0052091 | 0.0013055
53 | 0.98509 | -0.28465 | 0 | 0
54 | 0.98506 | -0.2853 | 0.0036431 | 0.00091304
55 | 0.99345 | -0.12469 | 0 | 0
56 | 0.99363 | -0.12111 | 0 | 0
57 | 0.99332 | -0.12721 | 0 | 0
58 | 0.99341 | -0.12549 | 0.0037499 | 0.00093982
59 | 0.99169 | -0.15792 | 0 | 0
60 | 0.99126 | -0.16619 | 0.0075648 | 0.0018959
61 | 0.99472 | -0.10008 | 0 | 0
62 | 0.99031 | -0.18425 | 0.0059161 | 0.0014827
63 | 0.9934 | -0.12556 | 0 | 0
64 | 0.99385 | -0.1169 | 0.0083125 | 0.0020833
65 | 0.99084 | -0.17503 | 0 | 0
66 | 0.99091 | -0.17371 | 0.0082868 | 0.0020769
67 | 0.99326 | -0.12837 | 0.0060329 | 0.001512
68 | 0.99338 | -0.1259 | 0 | 0
69 | 0.99219 | -0.1489 | 0.0060296 | 0.0015112
70 | 0.99288 | -0.13559 | 0 | 0
71 | 0.99405 | -0.113 | 0 | 0
72 | 0.99286 | -0.13604 | 0 | 0
73 | 0.99284 | -0.13648 | 0.0047315 | 0.0011858
74 | 0.99663 | -0.063713 | 0 | 0
75 | 0.99453 | -0.10368 | 0.0075759 | 0.0018987
76 | 0.99281 | -0.13704 | 0.005923 | 0.0014845
77 | 0.99336 | -0.1263 | 0.0037493 | 0.00093968
78 | 0.9894 | -0.20206 | 0 | 0
79 | 0.98962 | -0.19774 | 0 | 0
80 | 0.98918 | -0.20629 | 0.0047751 | 0.0011968
81 | 0.98167 | -0.35099 | 0.0087634 | 0.0021963
82 | 0.99867 | -0.025106 | 0 | 0
83 | 0.99863 | -0.025983 | 0.0075696 | 0.0018971
84 | 0.99888 | -0.021081 | 0 | 0
85 | 0.97716 | -0.43904 | 0.0083882 | 0.0021023
86 | 0.97732 | -0.43597 | 0.0084613 | 0.0021206
87 | 0.98893 | -0.2106 | 0.005917 | 0.0014829
88 | 0.97178 | -0.545 | 0.0065879 | 0.0016511
89 | 0.97544 | -0.47268 | 0 | 0
90 | 0.97694 | -0.44336 | 0.0037928 | 0.00095057
91 | 0.97695 | -0.44306 | 0.004531 | 0.0011356
92 | 0.97581 | -0.46551 | 0.0061675 | 0.0015457
93 | 0.97309 | -0.51899 | 0 | 0
94 | 0.98509 | -0.2858 | 0 | 0
95 | 0.9852 | -0.28374 | 0.0058674 | 0.0014705
96 | 0.98483 | -0.29093 | 0.006455 | 0.0016178
97 | 0.98448 | -0.29769 | 0.0051364 | 0.0012873
98 | 0.98453 | -0.29667 | 0.0047743 | 0.0011966
99 | 0.98498 | -0.28683 | 0.004685 | 0.0011742
100 | 0.98445 | -0.29827 | 0.0046309 | 0.0011606
101 | 0.98446 | -0.298 | 0 | 0
102 | 0.97901 | -0.40292 | 0.0097656 | 0.0024475
103 | 0.97508 | -0.47987 | 0.0037507 | 0.00094
104 | 0.97511 | -0.47922 | 0.0031289 | 0.00078418
105 | 0.99064 | -0.17814 | 0 | 0
106 | 0.99094 | -0.17311 | 0 | 0
107 | 0.99215 | -0.14966 | 0.0058998 | 0.0014786
108 | 0.99068 | -0.17822 | 0.0083204 | 0.0020853
109 | 0.99658 | -0.06477 | 0.0079356 | 0.0019888
110 | 0.99272 | -0.13868 | 0.0057371 | 0.0014379
111 | 0.99128 | -0.16653 | 0 | 0
112 | 0.99114 | -0.16932 | 0.0060325 | 0.0015119
113 | 0.99096 | -0.17285 | 0.0069998 | 0.0017543
114 | 0.9788 | -0.40707 | 0.010886 | 0.0027282
115 | 0.97165 | -0.54757 | 0.0097546 | 0.0024447
116 | 0.98907 | -0.20857 | 0.0058665 | 0.0014703
117 | 0.98593 | -0.26948 | 0 | 0
118 | 0.98553 | -0.27724 | 0.0056911 | 0.0014263
119 | 0.98501 | -0.2873 | 0 | 0
120 | 0.9866 | -0.25633 | 0.0049214 | 0.0012334
121 | 0.98766 | -0.23575 | 0.0047783 | 0.0011976
122 | 0.98485 | -0.29051 | 0 | 0
123 | 0.98469 | -0.29366 | 0.0047779 | 0.0011975
124 | 0.98471 | -0.29316 | 0.0049234 | 0.0012339
125 | 0.98463 | -0.29467 | 0.0047754 | 0.0011968
126 | 0.98432 | -0.30088 | 0.0047059 | 0.0011794
127 | 0.98425 | -0.30224 | 0.0048513 | 0.0012159
128 | 1 | 0 | -0.4806 | -0.123
129 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0085515 | 0.0021434 | -0.0085503 | -0.0021429 | 1.2036e-06 | 5.3572e-07 | 0.013057 | 0.013057 | 0.013057 | 0.9746 | -0.48938 | 0.97445 | -0.49233 | 3.587
1 | -0.011533 | -0.0028906 | 0.011535 | 0.0028918 | 2.2614e-06 | 1.2049e-06 | 0.017609 | 0.017608 | 0.017609 | 0.9746 | -0.48938 | 0.97481 | -0.48526 | 4.8375
2 | 0.0047411 | 0.0011882 | -0.0047409 | -0.0011882 | 1.7737e-07 | 1.1064e-09 | 0.0072398 | 0.0072398 | 0.0072398 | 0.97445 | -0.49233 | 0.97441 | -0.49312 | 1.989
3 | 0.011481 | 0.0028778 | -0.01148 | -0.0028772 | 1.0804e-06 | 5.7454e-07 | 0.017526 | 0.017526 | 0.017526 | 0.97481 | -0.48526 | 0.97471 | -0.48724 | 4.8148
4 | -0.023016 | -0.0057696 | 0.023033 | 0.0057795 | 1.6206e-05 | 9.9348e-06 | 0.035134 | 0.035134 | 0.035134 | 0.97481 | -0.48526 | 0.97555 | -0.4705 | 9.6523
5 | -0.06868 | -0.017252 | 0.068769 | 0.017308 | 8.8947e-05 | 5.6656e-05 | 0.10477 | 0.10477 | 0.10477 | 0.97555 | -0.4705 | 0.97693 | -0.4434 | 28.7836
6 | 0.031996 | 0.0080501 | -0.031943 | -0.0080166 | 5.356e-05 | 3.3532e-05 | 0.048815 | 0.048816 | 0.048816 | 0.97555 | -0.4705 | 0.97377 | -0.5056 | 13.4109
7 | 0.013652 | 0.003422 | -0.01365 | -0.0034211 | 1.7456e-06 | 9.8317e-07 | 0.020823 | 0.020823 | 0.020823 | 0.97555 | -0.4705 | 0.97542 | -0.47318 | 5.7207
8 | -0.072421 | -0.018223 | 0.072466 | 0.018252 | 4.4882e-05 | 2.8601e-05 | 0.11033 | 0.11033 | 0.11033 | 0.97693 | -0.4434 | 0.9776 | -0.43044 | 30.3116
9 | 0.0069986 | 0.001754 | -0.0069984 | -0.001754 | 1.4355e-07 | 5.0237e-08 | 0.010695 | 0.010695 | 0.010695 | 0.97377 | -0.5056 | 0.97375 | -0.50603 | 2.9381
10 | 0.024944 | 0.0062626 | -0.024917 | -0.0062457 | 2.7422e-05 | 1.6925e-05 | 0.038121 | 0.038121 | 0.038121 | 0.97377 | -0.5056 | 0.9726 | -0.52867 | 10.4729
11 | 0.010036 | 0.0025153 | -0.010035 | -0.0025148 | 1.0037e-06 | 4.9988e-07 | 0.01531 | 0.01531 | 0.01531 | 0.97542 | -0.47318 | 0.97531 | -0.47528 | 4.2061
12 | 0.0077291 | 0.0019375 | -0.0077267 | -0.0019365 | 2.4422e-06 | 9.8525e-07 | 0.011825 | 0.011825 | 0.011825 | 0.9726 | -0.52867 | 0.97227 | -0.5353 | 3.2487
13 | 0.017188 | 0.0043082 | -0.017186 | -0.0043072 | 1.6349e-06 | 9.6812e-07 | 0.026296 | 0.026296 | 0.026296 | 0.9726 | -0.52867 | 0.9725 | -0.53066 | 7.2242
14 | 0.0077267 | 0.0019365 | -0.0077264 | -0.0019364 | 2.3656e-07 | 9.5453e-08 | 0.011825 | 0.011825 | 0.011825 | 0.97227 | -0.5353 | 0.97224 | -0.53594 | 3.2487
15 | 0.0052093 | 0.0013056 | -0.0052092 | -0.0013055 | 9.113e-08 | 1.0865e-08 | 0.0079708 | 0.0079708 | 0.0079708 | 0.9725 | -0.53066 | 0.97248 | -0.53103 | 2.1898
16 | 0.0084418 | 0.0021159 | -0.008441 | -0.0021155 | 8.009e-07 | 3.4646e-07 | 0.012772 | 0.012772 | 0.012772 | 0.9835 | -0.31534 | 0.9834 | -0.31734 | 3.5089
17 | 0.23999 | 0.06081 | -0.2396 | -0.060561 | 0.00039245 | 0.00024956 | 0.36334 | 0.36334 | 0.36334 | 0.9835 | -0.31534 | 0.98174 | -0.34944 | 24.9549
18 | -0.24844 | -0.062926 | 0.2489 | 0.063222 | 0.0004653 | 0.00029601 | 0.37611 | 0.37611 | 0.37611 | 0.9835 | -0.31534 | 0.98551 | -0.27643 | 25.8321
19 | 0.008764 | 0.0021966 | -0.0087634 | -0.0021963 | 6.4536e-07 | 2.8972e-07 | 0.013284 | 0.013284 | 0.013284 | 0.98174 | -0.34944 | 0.98167 | -0.35099 | 3.6493
20 | 0.23084 | 0.058364 | -0.23047 | -0.058133 | 0.00036381 | 0.00023124 | 0.35006 | 0.35006 | 0.35006 | 0.98174 | -0.34944 | 0.98005 | -0.38236 | 24.0426
21 | 0.013053 | 0.0032722 | -0.013053 | -0.0032723 | 8.2069e-07 | -1.2077e-07 | 0.01971 | 0.01971 | 0.01971 | 0.98551 | -0.27643 | 0.98544 | -0.27775 | 1.8049
22 | -0.26195 | -0.066495 | 0.26228 | 0.066702 | 0.00032555 | 0.00020722 | 0.39582 | 0.39582 | 0.39582 | 0.98551 | -0.27643 | 0.98685 | -0.25063 | 27.1857
23 | -0.20188 | -0.050882 | 0.20208 | 0.051007 | 0.00019662 | 0.00012471 | 0.30695 | 0.30694 | 0.30695 | 0.97901 | -0.40269 | 0.98005 | -0.38236 | 21.0814
24 | 0.075549 | 0.019062 | -0.075448 | -0.018999 | 0.00010022 | 6.3126e-05 | 0.11487 | 0.11487 | 0.11487 | 0.97901 | -0.40269 | 0.9776 | -0.43044 | 15.7794
25 | 0.11315 | 0.028514 | -0.11304 | -0.028447 | 0.00010775 | 6.7007e-05 | 0.17203 | 0.17203 | 0.17203 | 0.97901 | -0.40269 | 0.978 | -0.42262 | 11.8155
26 | 0.013184 | 0.0033053 | -0.013181 | -0.0033034 | 3.4594e-06 | 1.9252e-06 | 0.020039 | 0.020039 | 0.020039 | 0.97901 | -0.40269 | 0.97873 | -0.4082 | 5.5053
27 | 0.028395 | 0.0071262 | -0.028378 | -0.0071154 | 1.7363e-05 | 1.0799e-05 | 0.043115 | 0.043115 | 0.043115 | 0.98005 | -0.38236 | 0.9794 | -0.39519 | 11.8449
28 | 0.0029825 | 0.00074719 | -0.0029823 | -0.00074743 | 2.4927e-07 | -2.4483e-07 | 0.0045397 | 0.0045398 | 0.0045398 | 0.9776 | -0.43044 | 0.97751 | -0.43219 | 1.2472
29 | 0.028175 | 0.0070661 | -0.028169 | -0.0070626 | 5.5918e-06 | 3.477e-06 | 0.04287 | 0.04287 | 0.04287 | 0.978 | -0.42262 | 0.97778 | -0.42678 | 11.7774
30 | 0.084866 | 0.021381 | -0.084815 | -0.02135 | 5.1309e-05 | 3.1192e-05 | 0.12916 | 0.12916 | 0.12916 | 0.978 | -0.42262 | 0.97735 | -0.43527 | 8.8712
31 | 0.013053 | 0.0032723 | -0.01305 | -0.0032706 | 3.0322e-06 | 1.6755e-06 | 0.01971 | 0.01971 | 0.01971 | 0.98544 | -0.27775 | 0.98519 | -0.28262 | 5.4148
32 | -0.27037 | -0.06873 | 0.2709 | 0.069063 | 0.00052231 | 0.00033256 | 0.40803 | 0.40803 | 0.40803 | 0.98685 | -0.25063 | 0.98893 | -0.2106 | 28.0239
33 | 0.016346 | 0.0040979 | -0.016345 | -0.004097 | 1.5125e-06 | 8.8821e-07 | 0.025026 | 0.025026 | 0.025026 | 0.97194 | -0.54169 | 0.97184 | -0.54364 | 6.8753
34 | -0.022931 | -0.0057483 | 0.022941 | 0.0057543 | 9.7911e-06 | 6.0036e-06 | 0.035107 | 0.035107 | 0.035107 | 0.97194 | -0.54169 | 0.9724 | -0.53274 | 9.6448
35 | 0.0065847 | 0.0016503 | -0.0065838 | -0.00165 | 9.3344e-07 | 2.939e-07 | 0.010081 | 0.010081 | 0.010081 | 0.97194 | -0.54169 | 0.97179 | -0.54467 | 2.7695
36 | 0.016345 | 0.004097 | -0.016344 | -0.0040964 | 1.0602e-06 | 6.226e-07 | 0.025026 | 0.025026 | 0.025026 | 0.97184 | -0.54364 | 0.97178 | -0.545 | 6.8753
37 | -0.022941 | -0.0057543 | 0.022944 | 0.0057563 | 3.3823e-06 | 2.0739e-06 | 0.035107 | 0.035107 | 0.035107 | 0.9724 | -0.53274 | 0.97255 | -0.52964 | 9.6448
38 | 0.0048943 | 0.0012262 | -0.0048926 | -0.0012261 | 1.7207e-06 | 7.9422e-08 | 0.0074757 | 0.007476 | 0.007476 | 0.97418 | -0.49752 | 0.97381 | -0.50491 | 2.0539
39 | 0.043746 | 0.010993 | -0.043708 | -0.010968 | 3.8388e-05 | 2.4283e-05 | 0.06683 | 0.06683 | 0.06683 | 0.97418 | -0.49752 | 0.97325 | -0.51593 | 18.36
40 | -0.04864 | -0.012219 | 0.048649 | 0.012224 | 9.0363e-06 | 5.7289e-06 | 0.074306 | 0.074306 | 0.074306 | 0.97418 | -0.49752 | 0.97438 | -0.49363 | 20.4137
41 | 0.0048926 | 0.0012261 | -0.0048921 | -0.0012261 | 4.8253e-07 | 2.2431e-08 | 0.007476 | 0.0074761 | 0.0074761 | 0.97381 | -0.50491 | 0.9737 | -0.50698 | 2.0539
42 | 0.013178 | 0.0033038 | -0.013175 | -0.0033019 | 3.3926e-06 | 1.8944e-06 | 0.020149 | 0.020149 | 0.020149 | 0.97325 | -0.51593 | 0.97297 | -0.52133 | 5.5354
43 | 0.030529 | 0.0076645 | -0.030527 | -0.0076628 | 2.6627e-06 | 1.6637e-06 | 0.046682 | 0.046682 | 0.046682 | 0.97325 | -0.51593 | 0.97315 | -0.51775 | 12.8246
44 | -0.053456 | -0.013429 | 0.05351 | 0.013463 | 5.3515e-05 | 3.3982e-05 | 0.081647 | 0.081647 | 0.081647 | 0.97438 | -0.49363 | 0.97544 | -0.47268 | 22.4305
45 | 0.016858 | 0.0042278 | -0.016851 | -0.0042234 | 7.379e-06 | 4.3478e-06 | 0.025656 | 0.025656 | 0.025656 | 0.97778 | -0.42678 | 0.97732 | -0.43597 | 7.0484
46 | 0.078399 | 0.019742 | -0.078385 | -0.019733 | 1.476e-05 | 8.8928e-06 | 0.1194 | 0.1194 | 0.1194 | 0.97735 | -0.43527 | 0.97715 | -0.43921 | 8.2003
47 | 0.0083254 | 0.0020866 | -0.0083242 | -0.0020861 | 1.2309e-06 | 5.3201e-07 | 0.012678 | 0.012678 | 0.012678 | 0.97715 | -0.43921 | 0.97699 | -0.44231 | 3.483
48 | 0.070059 | 0.017647 | -0.070033 | -0.017631 | 2.6149e-05 | 1.6045e-05 | 0.10672 | 0.10672 | 0.10672 | 0.97715 | -0.43921 | 0.97675 | -0.44701 | 9.7728
49 | 0.003793 | 0.0009505 | -0.0037928 | -0.00095057 | 1.896e-07 | -6.836e-08 | 0.0057769 | 0.005777 | 0.005777 | 0.97699 | -0.44231 | 0.97694 | -0.44336 | 1.5871
50 | 0.0045312 | 0.0011356 | -0.004531 | -0.0011356 | 1.6249e-07 | -9.9293e-09 | 0.0069013 | 0.0069013 | 0.0069013 | 0.97699 | -0.44231 | 0.97695 | -0.44306 | 1.896
51 | 0.059748 | 0.015053 | -0.059696 | -0.01502 | 5.2818e-05 | 3.2954e-05 | 0.091051 | 0.091051 | 0.091051 | 0.97675 | -0.44701 | 0.97581 | -0.46551 | 12.5071
52 | -0.028872 | -0.0072419 | 0.028886 | 0.007251 | 1.4676e-05 | 9.1439e-06 | 0.044176 | 0.044176 | 0.044176 | 0.97255 | -0.52964 | 0.97309 | -0.51899 | 12.1363
53 | 0.028888 | 0.0072521 | -0.028886 | -0.007251 | 1.6968e-06 | 1.0571e-06 | 0.044176 | 0.044176 | 0.044176 | 0.97315 | -0.51775 | 0.97309 | -0.51899 | 12.1362
54 | -0.0041768 | -0.0010465 | 0.0041771 | 0.0010465 | 2.925e-07 | -6.7908e-08 | 0.0062741 | 0.006274 | 0.0062741 | 0.99059 | -0.17997 | 0.99066 | -0.1785 | 1.7237
55 | 0.0041768 | 0.0010465 | -0.0041763 | -0.0010467 | 5.8149e-07 | -1.3486e-07 | 0.0062741 | 0.0062743 | 0.0062743 | 0.99059 | -0.17997 | 0.99044 | -0.18289 | 1.7237
56 | -0.0041771 | -0.0010465 | 0.0041778 | 0.0010463 | 6.8991e-07 | -1.6035e-07 | 0.006274 | 0.0062738 | 0.006274 | 0.99066 | -0.1785 | 0.99084 | -0.17503 | 1.7236
57 | 0.020661 | 0.0051815 | -0.020654 | -0.0051768 | 7.6044e-06 | 4.608e-06 | 0.031392 | 0.031392 | 0.031392 | 0.9794 | -0.39519 | 0.97901 | -0.40292 | 8.6242
58 | 0.0031539 | 0.00079035 | -0.0031538 | -0.00079043 | 9.3105e-08 | -7.4203e-08 | 0.0048121 | 0.0048121 | 0.0048121 | 0.97527 | -0.47605 | 0.97524 | -0.47667 | 1.322
59 | -0.0031539 | -0.00079035 | 0.0031541 | 0.00079026 | 1.1562e-07 | -9.2162e-08 | 0.0048121 | 0.004812 | 0.0048121 | 0.97527 | -0.47605 | 0.97531 | -0.47528 | 1.322
60 | 0.006881 | 0.0017246 | -0.0068797 | -0.0017241 | 1.291e-06 | 4.3652e-07 | 0.010498 | 0.010498 | 0.010498 | 0.97531 | -0.47528 | 0.97511 | -0.47922 | 2.8842
61 | 0.0083294 | 0.0020876 | -0.0083286 | -0.0020873 | 8.0571e-07 | 3.4281e-07 | 0.012581 | 0.012581 | 0.012581 | 0.98519 | -0.28262 | 0.98509 | -0.28465 | 3.4562
62 | 0.0052092 | 0.0013055 | -0.0052091 | -0.0013055 | 1.5339e-07 | 1.8292e-08 | 0.0079708 | 0.0079708 | 0.0079708 | 0.97248 | -0.53103 | 0.97245 | -0.53165 | 2.1898
63 | 0.0083286 | 0.0020873 | -0.0083284 | -0.0020872 | 2.5702e-07 | 1.0936e-07 | 0.012581 | 0.012581 | 0.012581 | 0.98509 | -0.28465 | 0.98506 | -0.2853 | 3.4562
64 | 0.0046853 | 0.0011741 | -0.004685 | -0.0011742 | 3.402e-07 | -1.2805e-08 | 0.0070775 | 0.0070776 | 0.0070776 | 0.98506 | -0.2853 | 0.98498 | -0.28683 | 1.9444
65 | -0.009784 | -0.002452 | 0.0097857 | 0.0024528 | 1.6713e-06 | 8.0086e-07 | 0.014655 | 0.014655 | 0.014655 | 0.99345 | -0.12469 | 0.99363 | -0.12111 | 4.026
66 | 0.0060339 | 0.0015122 | -0.0060332 | -0.0015121 | 7.2384e-07 | 1.5733e-07 | 0.0090378 | 0.0090379 | 0.0090379 | 0.99345 | -0.12469 | 0.99332 | -0.12721 | 2.4829
67 | 0.0037501 | 0.00093975 | -0.0037499 | -0.00093982 | 1.4246e-07 | -6.4725e-08 | 0.0056169 | 0.005617 | 0.005617 | 0.99345 | -0.12469 | 0.99341 | -0.12549 | 1.5431
68 | 0.0037503 | 0.00093925 | -0.0037495 | -0.00093961 | 7.9411e-07 | -3.612e-07 | 0.005616 | 0.0056163 | 0.0056163 | 0.99363 | -0.12111 | 0.9934 | -0.12556 | 1.5429
69 | -0.013536 | -0.003392 | 0.013539 | 0.0033935 | 2.7116e-06 | 1.5074e-06 | 0.020271 | 0.020271 | 0.020271 | 0.99363 | -0.12111 | 0.99385 | -0.1169 | 5.5689
70 | 0.0060332 | 0.0015121 | -0.0060329 | -0.001512 | 3.3247e-07 | 7.2292e-08 | 0.0090379 | 0.009038 | 0.009038 | 0.99332 | -0.12721 | 0.99326 | -0.12837 | 2.483
71 | 0.084931 | 0.021448 | -0.084898 | -0.021427 | 3.3652e-05 | 2.0398e-05 | 0.1275 | 0.1275 | 0.1275 | 0.99169 | -0.15792 | 0.99126 | -0.16619 | 8.7566
72 | -0.36837 | -0.093931 | 0.36941 | 0.094589 | 0.0010318 | 0.00065851 | 0.55331 | 0.55331 | 0.55331 | 0.99169 | -0.15792 | 0.99472 | -0.10008 | 38.0024
73 | 0.28344 | 0.072483 | -0.28308 | -0.072253 | 0.00036059 | 0.00022969 | 0.42582 | 0.42582 | 0.42582 | 0.99169 | -0.15792 | 0.99031 | -0.18425 | 29.2458
74 | 0.077333 | 0.019531 | -0.077289 | -0.019504 | 4.4243e-05 | 2.7301e-05 | 0.11614 | 0.11614 | 0.11614 | 0.99126 | -0.16619 | 0.99064 | -0.17814 | 10.6356
75 | -0.46117 | -0.11766 | 0.46198 | 0.11818 | 0.00081153 | 0.00051844 | 0.6906 | 0.6906 | 0.6906 | 0.99472 | -0.10008 | 0.99663 | -0.063713 | 47.4316
76 | 0.03829 | 0.0096131 | -0.038266 | -0.0095982 | 2.3587e-05 | 1.4847e-05 | 0.057284 | 0.057284 | 0.057284 | 0.99472 | -0.10008 | 0.99405 | -0.113 | 15.7373
77 | 0.0075772 | 0.0018992 | -0.0075759 | -0.0018987 | 1.3019e-06 | 4.8253e-07 | 0.011335 | 0.011335 | 0.011335 | 0.99472 | -0.10008 | 0.99453 | -0.10368 | 3.114
78 | 0.045894 | 0.011556 | -0.045838 | -0.01152 | 5.6586e-05 | 3.58e-05 | 0.068673 | 0.068673 | 0.068673 | 0.99472 | -0.10008 | 0.99338 | -0.1259 | 18.8663
79 | 0.27717 | 0.07077 | -0.27681 | -0.070546 | 0.00035262 | 0.00022456 | 0.41693 | 0.41693 | 0.41693 | 0.99031 | -0.18425 | 0.98893 | -0.2106 | 28.6353
80 | 0.0037495 | 0.00093961 | -0.0037493 | -0.00093968 | 1.3365e-07 | -6.0742e-08 | 0.0056163 | 0.0056164 | 0.0056164 | 0.9934 | -0.12556 | 0.99336 | -0.1263 | 1.543
81 | -0.021851 | -0.0054768 | 0.021855 | 0.0054793 | 4.0672e-06 | 2.4717e-06 | 0.032716 | 0.032716 | 0.032716 | 0.99385 | -0.1169 | 0.99405 | -0.113 | 8.988
82 | -0.0041778 | -0.0010463 | 0.0041781 | 0.0010462 | 2.6144e-07 | -6.0833e-08 | 0.0062738 | 0.0062738 | 0.0062738 | 0.99084 | -0.17503 | 0.99091 | -0.17371 | 1.7236
83 | -0.012465 | -0.0031231 | 0.012465 | 0.0031233 | 3.6104e-07 | 1.9566e-07 | 0.018718 | 0.018718 | 0.018718 | 0.99091 | -0.17371 | 0.99094 | -0.17311 | 5.1422
84 | 0.045838 | 0.01152 | -0.045787 | -0.011489 | 5.0272e-05 | 3.1807e-05 | 0.068673 | 0.068673 | 0.068673 | 0.99338 | -0.1259 | 0.99219 | -0.1489 | 18.8663
85 | 0.039758 | 0.0099775 | -0.039756 | -0.0099766 | 1.4429e-06 | 9.0945e-07 | 0.059631 | 0.059631 | 0.059631 | 0.99219 | -0.1489 | 0.99215 | -0.14966 | 16.382
86 | -0.016393 | -0.0041086 | 0.016411 | 0.0041189 | 1.7659e-05 | 1.0291e-05 | 0.024568 | 0.024568 | 0.024568 | 0.99288 | -0.13559 | 0.99405 | -0.113 | 6.7495
87 | 0.011661 | 0.0029228 | -0.011661 | -0.0029227 | 2.5313e-07 | 1.3342e-07 | 0.017477 | 0.017477 | 0.017477 | 0.99288 | -0.13559 | 0.99286 | -0.13604 | 4.8013
88 | 0.0047317 | 0.0011858 | -0.0047315 | -0.0011858 | 2.0156e-07 | -9.2343e-09 | 0.0070913 | 0.0070913 | 0.0070913 | 0.99288 | -0.13559 | 0.99284 | -0.13648 | 1.9482
89 | 0.011661 | 0.0029227 | -0.011661 | -0.0029224 | 5.5768e-07 | 2.9395e-07 | 0.017477 | 0.017477 | 0.017477 | 0.99286 | -0.13604 | 0.99281 | -0.13704 | 4.8013
90 | 0.007936 | 0.001989 | -0.0079356 | -0.0019888 | 3.9976e-07 | 1.569e-07 | 0.011849 | 0.011849 | 0.011849 | 0.99663 | -0.063713 | 0.99658 | -0.06477 | 3.2552
91 | -0.46991 | -0.12017 | 0.47089 | 0.12079 | 0.00097155 | 0.0006207 | 0.70245 | 0.70245 | 0.70245 | 0.99663 | -0.063713 | 0.99888 | -0.021081 | 48.2454
92 | 0.0057376 | 0.0014379 | -0.0057371 | -0.0014379 | 4.4611e-07 | 7.7507e-08 | 0.0085995 | 0.0085995 | 0.0085995 | 0.99281 | -0.13704 | 0.99272 | -0.13868 | 2.3625
93 | -0.010644 | -0.0026683 | 0.010647 | 0.0026694 | 2.1945e-06 | 1.1112e-06 | 0.016009 | 0.016009 | 0.016009 | 0.9894 | -0.20206 | 0.98962 | -0.19774 | 4.3981
94 | 0.010644 | 0.0026683 | -0.010642 | -0.0026672 | 2.1447e-06 | 1.0861e-06 | 0.016009 | 0.016009 | 0.016009 | 0.9894 | -0.20206 | 0.98918 | -0.20629 | 4.3981
95 | -0.077216 | -0.019458 | 0.077289 | 0.019504 | 7.248e-05 | 4.6203e-05 | 0.11614 | 0.11614 | 0.11614 | 0.98962 | -0.19774 | 0.99064 | -0.17814 | 31.9069
96 | 0.066569 | 0.016789 | -0.066449 | -0.016712 | 0.00012088 | 7.6951e-05 | 0.10013 | 0.10013 | 0.10013 | 0.98962 | -0.19774 | 0.98766 | -0.23575 | 27.5089
97 | 0.0058672 | 0.0014704 | -0.0058665 | -0.0014703 | 6.3715e-07 | 1.2781e-07 | 0.0088259 | 0.008826 | 0.008826 | 0.98918 | -0.20629 | 0.98907 | -0.20857 | 2.4247
98 | 0.00757 | 0.0018972 | -0.0075696 | -0.0018971 | 3.1654e-07 | 1.1577e-07 | 0.011279 | 0.011279 | 0.011279 | 0.99867 | -0.025106 | 0.99863 | -0.025983 | 3.0987
99 | -0.00757 | -0.0018972 | 0.0075714 | 0.0018978 | 1.4516e-06 | 5.308e-07 | 0.011279 | 0.011279 | 0.011279 | 0.99867 | -0.025106 | 0.99888 | -0.021081 | 3.0987
100 | -0.47846 | -0.12268 | 0.47895 | 0.123 | 0.00048966 | 0.00031284 | 0.71373 | 0.71373 | 0.71373 | 0.99888 | -0.021081 | 1 | 0 | 49.02
101 | -0.0083882 | -0.0021023 | 0.0083894 | 0.0021028 | 1.2273e-06 | 5.3418e-07 | 0.012774 | 0.012773 | 0.012774 | 0.97716 | -0.43904 | 0.97732 | -0.43597 | 3.5092
102 | 0.0097558 | 0.0024453 | -0.0097546 | -0.0024447 | 1.1955e-06 | 5.8815e-07 | 0.014938 | 0.014939 | 0.014939 | 0.97178 | -0.545 | 0.97165 | -0.54757 | 4.104
103 | -0.05351 | -0.013463 | 0.053528 | 0.013475 | 1.8331e-05 | 1.1365e-05 | 0.081647 | 0.081647 | 0.081647 | 0.97544 | -0.47268 | 0.97581 | -0.46551 | 11.2152
104 | -0.0064566 | -0.0016182 | 0.0064572 | 0.0016184 | 6.3498e-07 | 1.7973e-07 | 0.009753 | 0.0097529 | 0.009753 | 0.98509 | -0.2858 | 0.9852 | -0.28374 | 2.6794
105 | 0.0064566 | 0.0016182 | -0.006455 | -0.0016178 | 1.5761e-06 | 4.4633e-07 | 0.009753 | 0.0097532 | 0.0097532 | 0.98509 | -0.2858 | 0.98483 | -0.29093 | 2.6794
106 | -0.012325 | -0.0030889 | 0.012328 | 0.003091 | 3.8161e-06 | 2.0682e-06 | 0.018615 | 0.018615 | 0.018615 | 0.9852 | -0.28374 | 0.98553 | -0.27724 | 5.114
107 | -0.0051364 | -0.0012873 | 0.0051367 | 0.0012873 | 2.4837e-07 | 1.9226e-08 | 0.0077636 | 0.0077636 | 0.0077636 | 0.98448 | -0.29769 | 0.98453 | -0.29667 | 2.1329
108 | -0.009911 | -0.0024839 | 0.0099124 | 0.0024846 | 1.4227e-06 | 6.9547e-07 | 0.014979 | 0.014979 | 0.014979 | 0.98453 | -0.29667 | 0.98469 | -0.29366 | 4.1152
109 | -0.0046309 | -0.0011606 | 0.0046309 | 0.0011606 | 5.8513e-08 | -3.0441e-09 | 0.0069996 | 0.0069996 | 0.0069996 | 0.98445 | -0.29827 | 0.98446 | -0.298 | 1.923
110 | 0.0095588 | 0.0023959 | -0.0095575 | -0.0023953 | 1.3109e-06 | 6.261e-07 | 0.014448 | 0.014448 | 0.014448 | 0.98446 | -0.298 | 0.98432 | -0.30088 | 3.9693
111 | -0.01419 | -0.0035565 | 0.014195 | 0.0035594 | 5.0669e-06 | 2.8692e-06 | 0.021448 | 0.021448 | 0.021448 | 0.98446 | -0.298 | 0.98485 | -0.29051 | 5.8923
112 | 0.010888 | 0.0027293 | -0.010886 | -0.0027282 | 2.1564e-06 | 1.1162e-06 | 0.016549 | 0.016549 | 0.016549 | 0.97901 | -0.40292 | 0.9788 | -0.40707 | 4.5465
113 | -0.0037507 | -0.00094 | 0.0037508 | 0.00093996 | 1.1624e-07 | -4.3635e-08 | 0.0057237 | 0.0057236 | 0.0057237 | 0.97508 | -0.47987 | 0.97511 | -0.47922 | 1.5724
114 | 0.0083224 | 0.0020861 | -0.0083204 | -0.0020853 | 2.0274e-06 | 8.5171e-07 | 0.012497 | 0.012497 | 0.012497 | 0.99094 | -0.17311 | 0.99068 | -0.17822 | 3.4333
115 | -0.020788 | -0.0052094 | 0.020794 | 0.0052134 | 6.5101e-06 | 3.9369e-06 | 0.031215 | 0.031215 | 0.031215 | 0.99094 | -0.17311 | 0.99128 | -0.16653 | 8.5755
116 | 0.033857 | 0.008498 | -0.033829 | -0.0084809 | 2.7224e-05 | 1.706e-05 | 0.050782 | 0.050782 | 0.050782 | 0.99215 | -0.14966 | 0.99128 | -0.16653 | 13.9512
117 | 0.013035 | 0.0032675 | -0.013034 | -0.0032666 | 1.7273e-06 | 9.504e-07 | 0.019567 | 0.019568 | 0.019568 | 0.99128 | -0.16653 | 0.99114 | -0.16932 | 5.3757
118 | 0.007001 | 0.0017547 | -0.0069998 | -0.0017543 | 1.1801e-06 | 3.8824e-07 | 0.010511 | 0.010511 | 0.010511 | 0.99114 | -0.16932 | 0.99096 | -0.17285 | 2.8876
119 | 0.018026 | 0.0045213 | -0.01802 | -0.0045173 | 6.6678e-06 | 3.9612e-06 | 0.027207 | 0.027208 | 0.027208 | 0.98593 | -0.26948 | 0.98553 | -0.27724 | 7.4746
120 | 0.038626 | 0.0096982 | -0.038594 | -0.0096775 | 3.2821e-05 | 2.0677e-05 | 0.058303 | 0.058304 | 0.058304 | 0.98593 | -0.26948 | 0.98501 | -0.2873 | 16.0175
121 | -0.056653 | -0.014219 | 0.056688 | 0.014242 | 3.5555e-05 | 2.259e-05 | 0.085511 | 0.085511 | 0.085511 | 0.98593 | -0.26948 | 0.9866 | -0.25633 | 23.492
122 | 0.023899 | 0.0059929 | -0.023895 | -0.0059907 | 3.648e-06 | 2.2398e-06 | 0.036104 | 0.036104 | 0.036104 | 0.98501 | -0.2873 | 0.98485 | -0.29051 | 9.9187
123 | 0.014695 | 0.0036846 | -0.01469 | -0.003682 | 4.4489e-06 | 2.541e-06 | 0.022199 | 0.0222 | 0.0222 | 0.98501 | -0.2873 | 0.98469 | -0.29366 | 6.0988
124 | -0.06161 | -0.015475 | 0.06167 | 0.015514 | 6.0572e-05 | 3.8527e-05 | 0.092933 | 0.092933 | 0.092933 | 0.9866 | -0.25633 | 0.98766 | -0.23575 | 25.5312
125 | 0.0097004 | 0.0024313 | -0.0096991 | -0.0024307 | 1.2251e-06 | 5.9058e-07 | 0.014656 | 0.014657 | 0.014657 | 0.98485 | -0.29051 | 0.98471 | -0.29316 | 4.0265
126 | 0.0047757 | 0.0011968 | -0.0047754 | -0.0011968 | 3.437e-07 | -3.8869e-09 | 0.0072167 | 0.0072167 | 0.0072167 | 0.98471 | -0.29316 | 0.98463 | -0.29467 | 1.9826
127 | 0.0048516 | 0.0012159 | -0.0048513 | -0.0012159 | 3.1366e-07 | 3.112e-09 | 0.0073343 | 0.0073344 | 0.0073344 | 0.98432 | -0.30088 | 0.98425 | -0.30224 | 2.0149

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.48893 | 0.12509

## res_load
| p_mw | q_mvar
0 | 0.0029814 | 0.0007472
1 | 0.0038093 | 0.00095469
2 | 0.0047409 | 0.0011882
3 | 0.01148 | 0.0028772
4 | 0.0036515 | 0.00091514
5 | 0.0036139 | 0.00090572
6 | 0.011977 | 0.0030016
7 | 0.0077264 | 0.0019364
8 | 0.008441 | 0.0021155
9 | 0.0069984 | 0.001754
10 | 0.013181 | 0.0033034
11 | 0.0029823 | 0.00074743
12 | 0.0080943 | 0.0020286
13 | 0.0065838 | 0.00165
14 | 0.0048069 | 0.0012047
15 | 0.011311 | 0.0028349
16 | 0.0064154 | 0.0016078
17 | 0.0048921 | 0.0012261
18 | 0.010285 | 0.0025776
19 | 0.0059274 | 0.0014856
20 | 0.013175 | 0.0033019
21 | 0.0016388 | 0.00041072
22 | 0.0041763 | 0.0010467
23 | 0.0077163 | 0.0019339
24 | 0.0031538 | 0.00079043
25 | 0.0047202 | 0.001183
26 | 0.0052091 | 0.0013055
27 | 0.0036431 | 0.00091304
28 | 0.0037499 | 0.00093982
29 | 0.0075648 | 0.0018959
30 | 0.0059161 | 0.0014827
31 | 0.0083125 | 0.0020833
32 | 0.0082868 | 0.0020769
33 | 0.0060329 | 0.001512
34 | 0.0060296 | 0.0015112
35 | 0.0047315 | 0.0011858
36 | 0.0075759 | 0.0018987
37 | 0.005923 | 0.0014845
38 | 0.0037493 | 0.00093968
39 | 0.0047751 | 0.0011968
40 | 0.0087634 | 0.0021963
41 | 0.0075696 | 0.0018971
42 | 0.0083882 | 0.0021023
43 | 0.0084613 | 0.0021206
44 | 0.005917 | 0.0014829
45 | 0.0065879 | 0.0016511
46 | 0.0037928 | 0.00095057
47 | 0.004531 | 0.0011356
48 | 0.0061675 | 0.0015457
49 | 0.0058674 | 0.0014705
50 | 0.006455 | 0.0016178
51 | 0.0051364 | 0.0012873
52 | 0.0047743 | 0.0011966
53 | 0.004685 | 0.0011742
54 | 0.0046309 | 0.0011606
55 | 0.0097656 | 0.0024475
56 | 0.0037507 | 0.00094
57 | 0.0031289 | 0.00078418
58 | 0.0058998 | 0.0014786
59 | 0.0083204 | 0.0020853
60 | 0.0079356 | 0.0019888
61 | 0.0057371 | 0.0014379
62 | 0.0060325 | 0.0015119
63 | 0.0069998 | 0.0017543
64 | 0.010886 | 0.0027282
65 | 0.0097546 | 0.0024447
66 | 0.0058665 | 0.0014703
67 | 0.0056911 | 0.0014263
68 | 0.0049214 | 0.0012334
69 | 0.0047783 | 0.0011976
70 | 0.0047779 | 0.0011975
71 | 0.0049234 | 0.0012339
72 | 0.0047754 | 0.0011968
73 | 0.0047059 | 0.0011794
74 | 0.0048513 | 0.0012159
75 | 0.0083346 | 0.0020888

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1